## Sheet1
Party | BD | DQI breach | Cause | Mitigation | Corrective Action | Corrective action live since
CREOS | 2022-07-02 | 1 to 24 | Due to some Warnings/Errors in IGM in the CGMES format different tests have been performed with the parameter setting of the SCADA system .Here in this case , unfortunately the dedicated setting skipped the transformers in the UCTE files thus creating IGM with no transformer definition | Reset of default setting in the SCADA System (SCADA: Supervisory Control and Data Acquisition) | Better coordination of internal tests and settings of the SCADA | 2022-07-08
CREOS | 2022-07-24 | 1 to 24 | Cyberattack 22/23/07/22 ; A wrong format of the IGMs of CREOS | The DPO team has taken all necessary measures to protect our data. Among other things, thus for instance files couldn't be sent to the "external world". | All necessary steps from Creos IT and other involved departments have been applied | end of august 22
CREOS | 2022-07-27 | 1 to 24 | Cyberattack 22/23/07/22 ; missing files of BD 27/07/2022, Problems 25/7 & 26/6 | The DPO team has taken all necessary measures to protect our data. Among other things , thus for instance files couldn't be sent to the "external world". | All necessary steps from Creos IT and other involved departments have been applied | end of august 22
CREOS | 2022-07-28 | 1 to 24 | Cyberattack 22/23/07/22 ; missing files of BD 28/07/2022; Problems 25/7 & 26/7 | The DPO team has taken all necessary measures to protect our data.Among other things, thus for instance files couldn't be sent to the "external world". | All necessary steps from Creos IT and other involved departments have been applied | end of august 22
RTE | 2022-07-05 | 17.30 to 23.30 | The issue was not properly an IGM replacement, but a handling of x-node inconsistency by the Merging Entity. This is only a Core internal process issue and has no consequence on the results, thus decision has been taken to exclude this from the DQI reports in the future. Still, RTE is working on reducing this type of issue. | N/A | N/A | N/A
RTE | 2022-07-07 | 0.30 to 23.30 | The issue was not properly an IGM replacement, but a handling of x-node inconsistency by the Merging Entity. This is only a Core internal process issue and has no consequence on the results, thus decision has been taken to exclude this from the DQI reports in the future. Still, RTE is working on reducing this type of issue. | N/A | N/A | N/A
SEPS | 2022-07-04 | 1 to 24 | There was an issue with the voltage regulation in node QLEME that increased voltage above the predefined limits | Correction of the voltage regulation in node QLEME that was causing the troubles with convergence | Update of the IGM creation | 2022-07-09
SEPS | 2022-07-05 | 1 to 24 | There was an issue with the voltage regulation in node QLEME that increased voltage above the predefined limits | Correction of the voltage regulation in node QLEME that was causing the troubles with convergence | Update of the IGM creation | 2022-07-09
SEPS | 2022-07-20 | 1 to 24 | The IGM did not contain Pmin/Pmax limit for node that is included in the GLSK file and that led to the issue with merging | Data quality checks introduced in order to check whether all nodes from GLSK have Pmin/Pmax limits defined in the IGM | New data quality checks introduced | 2022-07-26
TENNET NL | 2022-07-17 | N/A | X-node inconsistencies are wrongly translated to IGM replacement. So on this BD no real IGM replacement occurred, only X-node inconsistency cause a technical replacement at Coreso side. | none | manual correction in IGM creation | 2022-07-17
TENNET NL | 2022-07-20 | only MTU 24 | Wrong IGM format for one MTU. Single occurence. | None |  | 2022-07-20
TSCNET | 2022-09-12 | 1 to 14 and 19 to 24 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
TSCNET | 2022-09-17 | 1 to 9 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
TSCNET | 2022-09-21 | 1 to 24 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
TSCNET | 2022-09-22 | 1 to 24 | Ambiguity in the starting procedure of specific NRAO service application components on the vendor side, which lead to application component shutdowns. | Vendor implemented application component restart scripts. This measure was unsuccesful. | Restart scripts were shut down and removed on the 22.09.22. The correct application component starting procedure was redefined, documented, and shared with all support levels via workshops. Implemented a 24/7 application components monitoring and notiffication system to ensure all componentes are running. | 22.09.2022
ELES | 2022-10-17 | 23 and 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-18 | 1 to 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-19 | 1 to 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-20 | 7, 8 and 17 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-21 | 10 to 16 and 22 to 24 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022
ELES | 2022-10-22 | 9 to 12 and 17 | The ICGM merging failed due to issue during the PST Divaca and Pardiciano special procedure. This happened due to the fact that there was no active generation in Eles IGM. | CORESO to fix merging tool to avoid process fail is such cases | Merging tool fixed. | 1.12.2022