## Lines
|  |  | Substation_1 | Substation_2 |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
220 kV Konjsko - Bilice 271/1 | 31T-0000-A-0023V | HOPS | Konjsko | Bilice | 220 | - | - | - | - | - | - | 780 | - | - | 4.3 | 22.09 | 143.9 | 53.13
220 kV Konjsko - Bilice 271/2 | 31T-0000-A-0024T | HOPS | Konjsko | Bilice | 220 | - | - | - | - | - | - | 780 | - | - | 4.3 | 22.09 | 143.9 | 53.13
220 kV Zakucac - Bilice 257 | 31T-0000-A-0022X | HOPS | Zakucac | Bilice | 220 | - | - | - | - | - | - | 780 | - | - | 6.22 | 30.75 | 202.5 | 75.2
220 kV Mraclin -Brinje 208 | 31T-0000-A-0007T | HOPS | Mraclin | Brinje | 220 | - | - | - | - | - | - | 1210 | - | - | 7.07 | 37.7 | 414.66 | 117.8
220 kV Senj - Brinje 235 | 31T-0000-A-0013Y | HOPS | Senj | Brinje | 220 | - | - | - | - | - | - | 815 | - | - | 1.24 | 6.66 | 41.62 | 15.53
220 kV Brinje - VE Padene | 31T-0000-A-00200 | HOPS | Brinje | VE Padene | 220 | - | - | - | - | - | - | 780 | - | - | 11.59 | 60.82 | 392.46 | 144.82
400 kV Zerjavinec - Ernestinovo 408 | 31T-0000-A-00022 | HOPS | Zerjavinec | Ernestinovo | 400 | - | - | - | - | - | - | 1920 | - | - | 7.17 | 76.29 | 816.28 | 231.2
400 kV Konjsko - Velebit 419 | 31T-0000-A-0008R | HOPS | Konjsko | Velebit | 400 | - | - | - | - | - | - | 1600 | - | - | 3.22 | 33.6 | 354.46 | 100.827
220 kV Konjsko - VE Padene | 31T-0000-A-0021Z | HOPS | Konjsko | VE Padene | 220 | - | - | - | - | - | - | 780 | - | - | 5.26 | 27.62 | 178.21 | 65.76
220 kV Zakucac - Konjsko 274 | 31T-0000-A-00111 | HOPS | Zakucac | Konjsko | 220 | - | - | - | - | - | - | 1200 | - | - | 1.57 | 5.24 | 67.54 | 24.92
220 kV TE Sisak - Meduric 246 | 31T-0000-A-0006V | HOPS | TE Sisak | Meduric | 220 | - | - | - | - | - | - | 815 | - | - | 3.64 | 18.45 | 122.85 | 45
400 kV Tumbri - Melina 456 | 31T-0000-A-00014 | HOPS | Tumbri | Melina | 400 | - | - | - | - | - | - | 1920 | - | - | 3.83 | 42.08 | 448.75 | 127.56
400 kV Melina - Velebit 434 | 31T-0000-A-0009P | HOPS | Melina | Velebit | 400 | - | - | - | - | - | - | 1920 | - | - | 5.88 | 61.08 | 629.38 | 178.8
220 kV Melina - Pehlin1 285 | 31T-0000-A-0016S | HOPS | Melina | Pehlin | 220 | - | - | - | - | - | - | 815 | - | - | 1.18 | 5.95 | 38.05 | 13.69
220 kV Melina - Pehlin2 286/2 | 31T-0000-A-0017Q | HOPS | Melina | Pehlin | 220 | - | - | - | - | - | - | 960 | - | - | 1.1 | 7.2 | 49.88 | 17.94
220 kV Melina - Senj 241 | 31T-0000-A-0018O | HOPS | Melina | Senj | 220 | - | - | - | - | - | - | 815 | - | - | 4.42 | 23.69 | 147.49 | 55.24
220 kV Melina - Plomin 287 | 31T-0000-A-0015U | HOPS | Melina | Plomin | 220 | - | - | - | - | - | - | 950 | - | - | 3.72 | 25.6 | 178.37 | 64.16
220 kV Mraclin - TE Sisak 249 | 31T-0000-A-0005X | HOPS | Mraclin | TE Sisak | 220 | - | - | - | - | - | - | 780 | - | - | 3.56 | 18.44 | 120.12 | 44
220 kV Mraclin - TE Sisak2 222 | 31T-0000-A-0019M | HOPS | Mraclin | TE Sisak | 220 | - | - | - | - | - | - | 780 | - | - | 4.69 | 24.75 | 178.66 | 58.637
220 kV Zerjavinec - Mraclin 247 | 31T-0000-A-0004Z | HOPS | Zerjavinec | Mraclin | 220 | - | - | - | - | - | - | 780 | - | - | 2.11 | 10.82 | 73.39 | 26.4
220 kV Pehlin - Plomin 284 | 31T-0000-A-0014W | HOPS | Pehlin | Plomin | 220 | - | - | - | - | - | - | 950 | - | - | 2.73 | 19.04 | 129.41 | 46.22
400 kV Zerjavinec - Tumbri 477 | 31T-0000-A-00030 | HOPS | Zerjavinec | Tumbri | 400 | - | - | - | - | - | - | 1900 | - | - | 1.83 | 19.03 | 211.06 | 61

## Tielines
|  |  | Substation_1 | Substation_2 |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters |  |  | TSO Share until border
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Pecs - Ernestinovo1 491A | 10T-HR-HU-000033 | HOPS | Pecs | Ernestinovo | 400 | - | - | - | - | - | - | 2001 | - | - | 1.28 | 13.47 | 161.48 | 43.7 | Tie-line to HU (MAVIR)
Pecs - Ernestinovo2 491B | 10T-HR-HU-000041 | HOPS | Pecs | Ernestinovo | 400 | - | - | - | - | - | - | 2001 | - | - | 1.28 | 13.47 | 161.48 | 43.7 | Tie-line to HU (MAVIR)
Ernestinovo-S. Mitrovica | 10T-RS-HR-00001B | HOPS | Ernestinovo | S. Mitrovica | 400 | - | - | - | - | - | - | 1920 | - | - | 1.46 | 15.17 | 164.29 | 51.53 | Tie-line to RS (EMS)
Gradacac - Dakovo | 10T-BA-HR-00001V | HOPS | Gradacac | Dakovo | 220 | - | - | - | - | - | - | 815 | - | - | 1.77 | 9.17 | 60.34 | 27.3 | Tie-line to BA (NOSBiH)
Melina - Divaca | 10T-HR-SI-000014 | HOPS | Melina | Divaca | 400 | - | - | - | - | - | - | 1920 | - | - | 1.02 | 10.86 | 117.73 | 25.736 | Tie-line to SI (ELES)
Mostar - Konjsko | 10T-BA-HR-00002T | HOPS | Mostar | Konjsko | 400 | - | - | - | - | - | - | 1920 | - | - | 1.75 | 17.71 | 196.06 | 68.556 | Tie-line to BA (NOSBiH)
Mostar - Zakucac | 10T-BA-HR-00003R | HOPS | Mostar | Zakucac | 220 | - | - | - | - | - | - | 780 | - | - | 3.79 | 19.79 | 129.7 | 49.463 | Tie-line to BA (NOSBiH)
Pehlin - Divaca | 10T-HR-SI-000022 | HOPS | Pehlin | Divaca | 220 | - | - | - | - | - | - | 960 | - | - | 1.58 | 11.03 | 74.11 | 24.61 | Tie-line to SI (ELES)
Prijedor - Meduric | 10T-BA-HR-00004P | HOPS | Prijedor | Meduric | 220 | - | - | - | - | - | - | 780 | - | - | 2.27 | 11.48 | 75.88 | 32.4 | Tie-line to BA (NOSBiH)
Prijedor - Sisak | 10T1001C--00027Y | HOPS | Prijedor | Sisak | 220 | - | - | - | - | - | - | 780 | - | - | 3.23 | 16.85 | 114.17 | 60.8 | Tie-line to BA (NOSBiH)
Trebinje - Plat 1 | 10T-BA-HR-00019C | HOPS | Trebinje | Plat | 220 | - | - | - | - | - | - | 675 | - | - | 0.43 | 2.28 | 14.79 | 1.324 | Tie-line to BA (NOSBiH)
Tuzla - Dakovo | 10T-BA-HR-00005N | HOPS | Tuzla | Dakovo | 220 | - | - | - | - | - | - | 815 | - | - | 3.69 | 18.95 | 124.7 | 26.3 | Tie-line to BA (NOSBiH)
Tumbri - Krsko 1 | 10T-HR-SI-00004Z | HOPS | Tumbri | Krsko | 400 | - | - | - | - | - | - | 1920 | - | - | 0.72 | 7.57 | 87.94 | 16 | Tie-line to SI (ELES)
Tumbri - Krsko 2 | 10T-HR-SI-00005X | HOPS | Tumbri | Krsko | 400 | - | - | - | - | - | - | 1920 | - | - | 0.72 | 7.57 | 87.94 | 16 | Tie-line to SI (ELES)
Ugljevik - Ernestinovo | 10T-BA-HR-00006L | HOPS | Ugljevik | Ernestinovo | 400 | - | - | - | - | - | - | 1920 | - | - | 1.57 | 17.01 | 181.46 | 52.6 | Tie-line to BA (NOSBiH)
Zerjavinec - Podlog | 10T1001C--001029 | HOPS | Zerjavinec | Podlog | 220 | - | - | - | - | - | - | 780 | - | - | 4.3 | 25.01 | 167.29 | 37.5 | Tie-line to SI (ELES)
Zerjavinec-Heviz 1 | 10T-HR-HU-000017 | HOPS | Zerjavinec | Heviz | 400 | - | - | - | - | - | - | 1920 | - | - | 2.7 | 30.03 | 320.32 | 97.67 | Tie-line to HU (MAVIR)
Zerjavinec-Heviz 2 | 10T-HR-HU-000025 | HOPS | Zerjavinec | Heviz | 400 | - | - | - | - | - | - | 1920 | - | - | 2.56 | 26.58 | 294.79 | 97.67 | Tie-line to HU (MAVIR)

## Transformers
Location |  |  | Maximum Current Imax (A) primary |  |  | Voltage_level(kV) |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | EIC_Code | TSO | Min | Max | Fixed | Primary | Secondary | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B (µS) | Conductance_G (µS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
TR 1 400/220 Konjsko | 31T-0000-B-0004S | HOPS | 1000 | 1000 |  | 400 | 231 | 0.194 | 15.6 | -8.66 | 2.4 |  | 0 | Asymmetrical | 5 | 0
TR 2 400/220 Konjsko | 31T-0000-B-0005Q | HOPS | 1000 | 1000 |  | 400 | 231 | 0.195 | 15.6 | -7.9 | 2.4 |  | 0 | Asymmetrical | 5 | 0
TR1 400/220 kV Melina | 31T-0000-B-0002W | HOPS | 1000 | 1000 |  | 400 | 231 | 0.196 | 15.5 | -9.42 | 2.5 |  | 0 | Asymmetrical | 5 | 0
TR2 400/220 kV Melina | 31T-0000-B-0003U | HOPS | 1000 | 1000 |  | 400 | 231 | 0.207 | 15.9 | -5.49 | 2.4 |  | 0 | Asymmetrical | 5 | 0
TR4 400/220 kV Zerjavinec | 31T-0000-B-0001Y | HOPS | 1000 | 1000 |  | 400 | 231 | 0.195 | 16.3 | -32.21 | 1.2 | -12;12 | 0 | Symmetrical/Asymmetrical | 0/1,5 | 0,9/0 | usually works in asymmetrical mode

## Remedial Actions
Location
Name of RA | TSO | Description