## Lines
|  |  | Substation_1 | Substation_2 |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Arad - Nadab | 30TARAD400NADB-P | TEL | Arad | Nadab | 400 | - | - | - |  |  |  | 1920 |  |  | 1.086 | 9.76 | 131 | 33.6
Bacau Sud - Gutinas | 30TBACS400GUTI-C | TEL | Bacau Sud | Gutinas | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2 | 18.52 | 184 | 55
Bacau Sud - Roman Nord | 30TBACS400ROMN-Q | TEL | Bacau Sud | Roman Nord | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.06 | 19.44 | 193.001 | 58
Bradu - Brasov | 30TBRAD400BRAS-Y | TEL | Bradu | Brasov | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 5.4 | 50.6 | 500 | 151
Bradu - Tantareni | 30TBRAD400TINT-R | TEL | Bradu | Tantareni | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 7 | 66.5 | 661.001 | 199
Brasov - Darste | 30TBRAS400DIRS-Y | TEL | Brasov | Darste | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 0.46 | 4.39 | 44.001 | 13
Brasov - Sibiu Sud | 30TBRAS400SIBI-1 | TEL | Brasov | Sibiu Sud | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.5 | 42.3 | 420.999 | 126
Brazi Vest - Darste | 30TBRAZ400DIRS-1 | TEL | Brazi Vest | Darste | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.05 | 38.24 | 380.001 | 114
Bucuresti Sud - Domnesti | 30TBUCU400DOMN-Z | TEL | Bucuresti Sud | Domnesti | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 1.21 | 11.4 | 113.399 | 44
Bucuresti Sud - Gura Ialomitei | 30TBUCU400GIAL-R | TEL | Bucuresti Sud | Gura Ialomitei | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.99 | 47.1 | 468.201 | 140
Bucuresti Sud - Pelicanu | 30TBUCU400PELI-W | TEL | Bucuresti Sud | Pelicanu | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 3.83 | 36.25 | 446.301 | 119
Cernavoda - Constanta Nord | 30TCERN400CONS-W | TEL | Cernavoda | Constanta Nord | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.38 | 22.38 | 251.899 | 73
Cernavoda - Gura Ialomitei c1 | 30TCERN400GIAL1X | TEL | Cernavoda | Gura Ialomitei | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.26 | 20.8 | 246.1 | 60
Cernavoda - Gura Ialomitei c2 | 30TCERN400GIAL2V | TEL | Cernavoda | Gura Ialomitei | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.14 | 20.06 | 227.301 | 67
Cernavoda - Pelicanu | 30TCERN400PELI-5 | TEL | Cernavoda | Pelicanu | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 3.23 | 30.2 | 344.9 | 95
Domnesti - Brazi Vest | 30TBRAZ400DOMN-6 | TEL | Domnesti | Brazi Vest | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.27 | 21.46 | 213 | 64
Domnesti - Urechesti | 30TDOMN400UREC-Q | TEL | Domnesti | Urechesti | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 9.35 | 88.25 | 877.199 | 263
Gadalin - Cluj Est | 30TCLES400GADA-X | TEL | Gadalin | Cluj Est | 400 | - | - | - |  |  |  | 960 |  |  | 0.69 | 6.5 | 65 | 19
Gura Ialomitei - Lacu Sarat | 30TGIAL400LACS-E | TEL | Gura Ialomitei | Lacu Sarat | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.38 | 23.7 | 232.999 | 71
Gutinas - Brasov | 30TBRAS400GUTI-F | TEL | Gutinas | Brasov | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.4 | 41.3 | 410 | 123
Gutinas - Smardan | 30TGUTI400SMIR-C | TEL | Gutinas | Smardan | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.77 | 45.04 | 448.001 | 134
Iernut - Gadalin | 30TGADA400IERN-T | TEL | Iernut | Gadalin | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 1.8 | 16.95 | 168 | 51
Iernut - Sibiu Sud | 30TIERN400SIBI-3 | TEL | Iernut | Sibiu Sud | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.98 | 28.14 | 280.001 | 84
Isaccea - Lacu Sarat | 30TISAC400LACS-W | TEL | Isaccea | Lacu Sarat | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.38 | 22.49 | 223.499 | 67
Isaccea - Rahman | 30TISAC400RAHM-V | TEL | Isaccea | Rahman | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 1.66 | 16.89 | 230 | 55.3
Isaccea - Smardan c1 | 30TISAC400SMIR1G | TEL | Isaccea | Smardan | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2 | 18.1 | 197 | 57.1
Isaccea - Smardan c2 | 30TISAC400SMIR2E | TEL | Isaccea | Smardan | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2 | 18.1 | 197 | 56.9
Isaccea - Stupina | 30TISAC400STPA-8 | TEL | Isaccea | Stupina | 400 | - | - | - |  |  |  | 2000 |  |  | 1.6 | 23.4 | 333 | 82.9
Isaccea - Tulcea Vest | 30TISAC400TULC-7 | TEL | Isaccea | Tulcea Vest | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 1 | 9.57 | 94.999 | 29
Medgidia Sud - Cernavoda | 30TCERN400MEDG-O | TEL | Medgidia Sud | Cernavoda | 400 | - | - | - |  |  |  | 960 |  |  | 0.71 | 6.23 | 80.5 | 21
Mintia - Arad | 30TARAD400MINT-8 | TEL | Mintia | Arad | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.89 | 46.1 | 458.201 | 138
Oradea Sud - Rosiori | 30TORAD400ROSI-1 | TEL | Oradea Sud | Rosiori | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.71 | 44.24 | 442 | 133
Portile de Fier - Urechesti | 30TPDFE400UREC-L | TEL | Portile de Fier | Urechesti | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 3.03 | 28.4 | 281.999 | 85
Roman Nord - Suceava | 30TROMN400SUCE-S | TEL | Roman Nord | Suceava | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 3.53 | 33.34 | 331.001 | 99.5
Rosiori - Gadalin | 30TGADA400ROSI-A | TEL | Rosiori | Gadalin | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.2 | 39.7 | 394.999 | 119
Sibiu Sud - Mintia | 30TMINT400SIBI-Z | TEL | Sibiu Sud | Mintia | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 4.62 | 43.58 | 432.999 | 130
Sibiu Sud - Tantareni | 30TSIBI400TINT-1 | TEL | Sibiu Sud | Tantareni | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 9.23 | 87.1 | 865.999 | 264
Slatina - Bucuresti Sud | 30TBUCU400SLAT-R | TEL | Slatina | Bucuresti Sud | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 6.14 | 58 | 575.998 | 172
Slatina - Draganesti Olt | 30TDRGO400SLAT-G | TEL | Slatina | Draganesti Olt | 400 | - | - | - |  |  |  | 960 |  |  | 1.11 | 11.45 | 114.498 | 34
Slatina - Portile de Fier | 30TPDFE400SLAT-S | TEL | Slatina | Portile de Fier | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 5.6 | 52.8 | 526 | 158
Slatina - Tantareni | 30TSLAT400TINTC | TEL | Slatina | Tantareni | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.98 | 28.14 | 280.001 | 84
Smardan - Lacu Sarat | 30TLACS400SMIR-F | TEL | Smardan | Lacu Sarat | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 1.2 | 11.36 | 113 | 34
Tantareni - Urechesti | 30TTINT400UREC-4 | TEL | Tantareni | Urechesti | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 2.5 | 23.3 | 232 | 70
Tariverde - Constanta Nord | 30TCONS400TARV-Y | TEL | Tariverde | Constanta Nord | 400 | 1740 | 1920 | 1920 |  |  |  | - |  |  | 1.6769 | 15.8627 | 176.399 | 49.5
Tulcea Vest - Tariverde | 30TTARV400TULC1W | TEL | Tulcea Vest | Tariverde | 400 | - | - | - |  |  |  | 1920 |  |  | 2.3935 | 22.6628 | 288.537 | 74.8
Alba Iulia - Galceag | 30TAIUL220GILC-O | TEL | Alba Iulia | Galceag | 220 | - | - | - |  |  |  | 600 |  |  | 4.1 | 24.4 | 157.001 | 58
Alba Iulia - Mintia | 30TAIUL220MINT-3 | TEL | Alba Iulia | Mintia | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 6.4 | 35.8 | 229.999 | 84
Alba Iulia - Sugag | 30TAIUL220SUGA-T | TEL | Alba Iulia | Sugag | 220 | - | - | - |  |  |  | 600 |  |  | 3.34 | 19.74 | 126.999 | 47
Arad - Calea Aradului | 30TARAD220CARA-3 | TEL | Arad | Calea Aradului | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 3.384 | 20 | 128.601 | 48
Arad - Timisoara | 30TARAD220TIMI-5 | TEL | Arad | Timisoara | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 3.8 | 22.6 | 145 | 54
Arefu - Raureni | 30TAREF220RIUR-5 | TEL | Arefu | Raureni | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 3.3 | 19.8 | 126.999 | 81
Baia Mare 3 - Iernut | 30TBAMA220IERN-Y | TEL | Baia Mare 3 | Iernut | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 10.8 | 63.8 | 410 | 152
Baia Mare 3 - Rosiori c1 | 30TBAMA220ROSI1B | TEL | Baia Mare 3 | Rosiori | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 2.35 | 13.91 | 89.419 | 33
Baia Mare 3 - Rosiori c2 | 30TBAMA220ROSI29 | TEL | Baia Mare 3 | Rosiori | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 2.35 | 13.91 | 89.419 | 33
Baia Mare 3 - Tihau | 30TBAMA220TIHA-R | TEL | Baia Mare 3 | Tihau | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 4.1 | 24.2 | 155 | 57
Barbosi - Filesti | 30TBARB220FILE-I | TEL | Barbosi | Filesti | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 0.5 | 2.8 | 18.001 | 7
Baru Mare - Hasdat | 30TBARU220HASD-G | TEL | Baru Mare | Hasdat | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 2.94 | 17.42 | 112.001 | 44
Bradu - Arefu | 30TAREF220BRAD-U | TEL | Bradu | Arefu | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 5.3 | 31.2 | 200 | 74
Bradu - Pitesti Sud | 30TBRAD220PITS-W | TEL | Bradu | Pitesti Sud | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 0.45 | 2.7 | 16.999 | 6
Bradu - Targoviste A | 30TBRAD220TIRG1B | TEL | Bradu | Targoviste A | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 3.8 | 22.5 | 144.001 | 54
Bradu - Targoviste B | 30TBRAD220TIRG29 | TEL | Bradu | Targoviste B | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 3.8 | 22.5 | 144.001 | 54
Brazi Vest - Fundeni c1 | 30TBRAZ220FUND1P | TEL | Brazi Vest | Fundeni | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 4.77 | 28.27 | 181.999 | 67
Brazi Vest - Fundeni c2 | 30TBRAZ220FUND2N | TEL | Brazi Vest | Fundeni | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 4.77 | 28.27 | 181.999 | 67
Brazi Vest - Targoviste A | 30TBRAZ220TIRG1D | TEL | Brazi Vest | Targoviste A | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 3.6 | 21.2 | 136 | 50
Brazi Vest - Targoviste B | 30TBRAZ220TIRG2B | TEL | Brazi Vest | Targoviste B | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 3.6 | 21.2 | 136 | 50
Brazi Vest - Teleajen | 30TBRAZ220TELE-U | TEL | Brazi Vest | Teleajen | 220 | - | - | - |  |  |  | 720 |  |  | 1.3 | 12.4 | 123 | 32.8
Bucuresti Sud - Ghizdaru d. Mostistea | 30TBUCU220GHMO-E | TEL | Bucuresti Sud | d. Mostistea | 220 | - | - | - |  |  |  | 561 |  |  | 0.35 | 2.05 | 13 | 4.8
Bucuresti Sud - Fundeni c1 | 30TBUCU220FUND1H | TEL | Bucuresti Sud | Fundeni | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 1.8 | 10.5 | 67.579 | 25
Bucuresti Sud - Fundeni c2 | 30TBUCU220FUND2F | TEL | Bucuresti Sud | Fundeni | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 1.8 | 10.5 | 67.579 | 25
Bucuresti Sud - Ghizdaru | 30TBUCU220GHIZ-Y | TEL | Bucuresti Sud | Ghizdaru | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 5.14 | 30.4 | 196.001 | 72
Calea Aradului - Sacalaz | 30TCARA220SACA-P | TEL | Calea Aradului | Sacalaz | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 0.553 | 3.269 | 21.022 | 47.63
Campia Turzii - Iernut | 30TCTRZ220IERN-6 | TEL | Campia Turzii | Iernut | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 4.8 | 26.9 | 173.001 | 51
Cetate - Calafat | 30TCALF220CETA-C | TEL | Cetate | Calafat | 220 | - | - | - |  |  |  | 720 |  |  | 2.5 | 14.78 | 95.13 | 36
Cetate - Portile de Fier c1 | 30TCETA220PDFE14 | TEL | Cetate | Portile de Fier | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 6.56 | 38.84 | 250 | 92
Cetate - Portile de Fier c2 | 30TCETA220PDFE22 | TEL | Cetate | Portile de Fier | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 6.56 | 38.84 | 249.999 | 92
Cluj Floresti - Alba Iulia | 30TAIUL220CJFL-3 | TEL | Cluj Floresti | Alba Iulia | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 7.2 | 40.4 | 260.001 | 96
Cluj Floresti - Campia Turzii | 30TCJFL220CTRZ-R | TEL | Cluj Floresti | Campia Turzii | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 1.98 | 11.76 | 142.999 | 41
Cluj Floresti - Mariselu | 30TCJFL220MARI-2 | TEL | Cluj Floresti | Mariselu | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 1.8 | 10.7 | 68.999 | 25
Craiova Nord - Isalnita c1 | 30TCRAI220ISAL1H | TEL | Craiova Nord | Isalnita | 220 | - | - | - |  |  |  | 1185 |  |  | 0.57 | 3.709 | 15 | 10
Craiova Nord - Isalnita c2 | 30TCRAI220ISAL2F | TEL | Craiova Nord | Isalnita | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 0.68 | 3.84 | 26 | 10
Craiova Nord - Sardanesti | 30TCRAI220SARD-7 | TEL | Craiova Nord | Sardanesti | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 5.4 | 29.35 | 187.999 | 68.6
Craiova Nord - Slatina | 30TCRAI220SLAT-9 | TEL | Craiova Nord | Slatina | 220 | 1600 | 1780 | 1920 |  |  |  | - |  |  | 2 | 10.32 | 265.999 | 49
FAI - Gutinas | 30TGUTI220IASI-A | TEL | FAI | Gutinas | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 13.5 | 79.8 | 513 | 190
FAI - Munteni | 30TIASI220MUNV-I | TEL | FAI | Munteni | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 5.28 | 31.2 | 200 | 74
FAI - Suceava | 30TIASI220SUCE-3 | TEL | FAI | Suceava | 220 | - | - | - |  |  |  | 720 |  |  | 8.23 | 48.75 | 313 | 116
Fantanele - Gheorgheni | 30TFINT220GHEO-R | TEL | Fantanele | Gheorgheni | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 6.2 | 32.7 | 210 | 78
Filesti - Lacu Sarat | 30TFILE220LACS-F | TEL | Filesti | Lacu Sarat | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 2.1 | 12.2 | 77.999 | 29
Focsani Vest - Barbosi | 30TBARB220FCSV-6 | TEL | Focsani Vest | Barbosi | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 5.81 | 30.49 | 204.91 | 90
Gheorgheni - Stejaru | 30TGHEO220STEJ-L | TEL | Gheorgheni | Stejaru | 220 | 800 | 890 | 960 |  |  |  | - |  |  | 5.3 | 27.9 | 180.001 | 59.5
Ghizdaru - Turnu Magurele | 30TGHIZ220TMAG-W | TEL | Ghizdaru | Turnu Magurele | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 5.83 | 34.54 | 222.001 | 82
Gradiste - Isalnita | 30TGRAD220ISAL-J | TEL | Gradiste | Isalnita | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 2.564 | 15.167 | 290.99 | 60
Gutinas - Dumbrava | 30TDUMB220GUTI-U | TEL | Gutinas | Dumbrava | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 6.43 | 38.1 | 245 | 81
Gutinas - Focsani Vest | 30TFCSV220GUTI-S | TEL | Gutinas | Focsani Vest | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 5.552 | 29.15 | 196.14 | 86
Gutinas - Munteni | 30TGUTI220MUNV-F | TEL | Gutinas | Munteni | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 8.3 | 49.1 | 316 | 116
Hasdat - Mintia | 30THASD220MINT1W | TEL | Hasdat | Mintia | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 1.83 | 10.82 | 70.001 | 26
Hasdat - Otelarie H | 30THASD220HDOT-D | TEL | Hasdat | Otelarie H | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 0.53 | 3.12 | 19.999 | 7
Hasdat - Pestis | 30THASD220PEST-I | TEL | Hasdat | Pestis | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 1.3 | 7 | 45 | 16
Iaz - Resita c1 | 30TIAZU220RESI1Y | TEL | Iaz | Resita | 220 | - | - | - |  |  |  | 720 |  |  | 2.18 | 12.91 | 80.001 | 31
Iaz - Resita c2 | 30TIAZU220RESI2W | TEL | Iaz | Resita | 220 | - | - | - |  |  |  | 720 |  |  | 2.18 | 12.91 | 80.001 | 31
Iernut - Ungheni c1 | 30TIERN220UNGH1L | TEL | Iernut | Ungheni | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 2.28 | 12.31 | 78.998 | 29
Iernut - Ungheni c2 | 30TIERN220UNGH2J | TEL | Iernut | Ungheni | 220 | - | - | - |  |  |  | 1200 |  |  | 1.13 | 10 | 97 | 29
Lotru - Sibiu Sud c1 | 30TLOTR220SIBI12 | TEL | Lotru | Sibiu Sud | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 6.25 | 36.96 | 236.999 | 85
Lotru - Sibiu Sud c2 | 30TLOTR220SIBI20 | TEL | Lotru | Sibiu Sud | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 6.25 | 36.96 | 236.999 | 85
Mintia - Pestis c1 | 30TMINT220PEST17 | TEL | Mintia | Pestis | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 1.33 | 7.84 | 49.998 | 19
Mintia - Pestis c2 | 30TMINT220PEST2 | TEL | Mintia | Pestis | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 1.33 | 7.84 | 49.998 | 19
Mintia - Timisoara | 30TMINT220TIMI-O | TEL | Mintia | Timisoara | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 9.2 | 54.7 | 352 | 130
Paroseni - Baru Mare | 30TBARU220PARO-D | TEL | Paroseni | Baru Mare | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 1.6 | 8.5 | 55 | 20
Paroseni - Targiu Jiu Nord | 30TPARO220TRGJ-Q | TEL | Paroseni | Targiu Jiu Nord | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 3 | 15.83 | 102.001 | 38
Pestis - Otelarie H | 30THDOT220PEST-E | TEL | Pestis | Otelarie H | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 0.83 | 4.73 | 30.429 | 11
Portile de Fier - Resita c1 | 30TPDFE220RESI1S | TEL | Portile de Fier | Resita | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 8.3 | 49.14 | 316 | 117
Portile de Fier - Resita c2 | 30TPDFE220RESI2Q | TEL | Portile de Fier | Resita | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 8.3 | 49.14 | 316 | 117
Portile de Fier - Turnu Severin Est c1 | 30TDROB220PDFE1S | TEL | Portile de Fier | Turnu Severin Est | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 0.92 | 5.45 | 35 | 13
Portile de Fier - Turnu Severin Est c2 | 30TDROB220PDFE2Q | TEL | Portile de Fier | Turnu Severin Est | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 0.92 | 5.45 | 35 | 13
Raureni - Stuparei | 30TRIUR220STUP-M | TEL | Raureni | Stuparei | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 0.9 | 5.1 | 32.999 | 12
Resita - Timisoara c1 | 30TRESI220TIMI1L | TEL | Resita | Timisoara | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 5.2 | 30.7 | 197 | 73
Resita - Timisoara c2 | 30TRESI220TIMI2J | TEL | Resita | Timisoara | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 5.2 | 30.7 | 197 | 73
Retezat - Hasdat | 30THASD220RETE-A | TEL | Retezat | Hasdat | 220 | - | - | - |  |  |  | 1200 |  |  | 0.98 | 13.8 | 136.999 | 41
Rosiori - Vetis | 30TROSI220VETI--R | TEL | Rosiori | Vetis | 220 | - | - | - |  |  |  | 720 |  |  | 2.45 | 14.7 | 94.499 | 35
Sacalaz - Timisoara | 30TSACA220TIMI-K | TEL | Sacalaz | Timisoara | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 1.7 | 10.3 | 65.999 | 25
Sardanesti - Urechesti | 30TSARD220UREC-9 | TEL | Sardanesti | Urechesti | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 5.14 | 28.34 | 181.999 | 65.9
Slatina - Gradiste | 30TGRAD220SLAT-7 | TEL | Slatina | Gradiste | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 1.263 | 7.47 | 93.051 | 23.3
Stalpu - Teleajen | 30TTLP220TELEAJC | TEL | Stalpu | Teleajen | 220 | - | - | - |  |  |  | 960 |  |  | 1.9 | 17.9 | 177.999 | 53
Stejaru - Dumbrava | 30TDUMB220STEJ-K | TEL | Stejaru | Dumbrava | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 2.4 | 14.2 | 90.999 | 34
Stuparei - Bradu | 30TBRAD220STUP-1 | TEL | Stuparei | Bradu | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 5 | 29.7 | 190.999 | 71
Tihau - Cluj Floresti | 30TCJFL220TIHA-L | TEL | Tihau | Cluj Floresti | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 4.7 | 28 | 180.001 | 67
Tihau - Salaj | 30TSALJ220TIHA-N | TEL | Tihau | Salaj | 220 | 870 | 960 | 960 |  |  |  | - |  |  | 1.92 | 11.34 | 73.001 | 27
Turnu Magurele - Craiova Nord | 30TCRAI220TMAG-0 | TEL | Turnu Magurele | Craiova Nord | 220 | 870 | 970 | 1062 |  |  |  | - |  |  | 8.55 | 50.6 | 325.001 | 120
Ungheni - Fantanele | 30TFINT220UNGH-0 | TEL | Ungheni | Fantanele | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 2 | 11.3 | 73.001 | 26
Urechesti - Targu Jiu Nord | 30TTRGJ220UREC-1 | TEL | Urechesti | Targu Jiu Nord | 220 | 800 | 890 | 978 |  |  |  | - |  |  | 1.35 | 7.57 | 48.999 | 18

## Tielines
|  |  | Substation_1 | Substation_2 |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters |  |  | TSO Share until border
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Arad - Sandorfalva | 10T-HU-RO-000016 | TEL | Arad | Sandorfalva | 400 | [6 empty] | 1920 |  |  | 1.69 | 17.9 | 185.599 | 55 | Tie-line to HU (TEL)
Nadab - Bekescsaba | 10T-HU-RO-000024 | TEL | Nadab | Bekescsaba | 400 | [6 empty] | 2000 |  |  | 0.664 | 5.598 | 86.86 | 20.8 | Tie-line to HU (TEL)
Portile de Fier - Djerdap c1 | 10T-RO-RS-00001V | TEL | Portile de Fier | Djerdap | 400 | [6 empty] | 1920 |  |  | 0.034 | 0.323 | 3.311 | 0.75 | Tie-line to RS (TEL)
Rosiori - Mukacevo c1 | 10T-RO-UA-000010 | TEL | Rosiori | Mukacevo | 400 | [6 empty] | 1920 |  |  | 2.015 | 19.03 | 189.18 | 39 | Tie-line to UA (TEL)
Stupina - Varna c1 | 10T-RO-BG-000038 | TEL | Stupina | Varna | 400 | [6 empty] | 2000 |  |  | 1.474 | 21.559 | 298 | 67.5 | Tie-line to BG (TEL)
Tantareni - Kozlodui c1 | 10T-BG-RO-00001A | TEL | Tantareni | Kozlodui | 400 | [6 empty] | 1920 |  |  | 1.9 | 16.74 | 213.999 | 102 | Tie-line to BG (TEL)
Tantareni - Kozlodui c2 | 10T-RO-BG-00002A | TEL | Tantareni | Kozlodui | 400 | [6 empty] | 1920 |  |  | 1.9 | 16.74 | 213.999 | 102 | Tie-line to BG (TEL)
Rahman - Dobrudja | 10T-RO-BG-00001C | TEL | Dobrudja | Rahman | 400 | [6 empty] | 2000 |  |  | 2.125 | 25.825 | 338.71 | 94.2 | Tie-line to BG (TEL)

## Transformers
Location |  |  | Maximum Current Imax (A) primary |  |  | Voltage_level(kV) |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | EIC_Code | TSO | Min | Max | Fixed | Primary | Secondary | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B (µS) | Conductance_G (µS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
PST Arad 400/220 3 | 30T-ARAD400AT3-F | TEL |  |  | 577 | 400 | 231 | 1.02 | 45.988 | 1.8125 | -12.368 | -12;0 | 60 | Asymmetrical |  | 1.25
TR Bradu 400/220 1 | 30T-BRAD400AT3-3 | TEL |  |  | 577 | 400 | 231 | 0.48 | 45.757 | 0.4688 | -2.456 | 8;0 | 0 | Symmetrical | 1.25
TR Bradu 400/220 2 | 30T-BRAD400AT4-0 | TEL |  |  | 577 | 400 | 231 | 0.48 | 45.757 | 0.4688 | -2.456 | 8;0 | 0 | Symmetrical | 1.25
TR Brazi Vest 400/220 2 | 30T-BRAZ400AT3-R | TEL |  |  | 577 | 400 | 231 | 0.492 | 47.597 | 0.4688 | -4.978 | 8;0 | 0 | Symmetrical | 1.25
TR Bucuresti Sud 400/220 1 | 30T-BUCU400AT3-J | TEL |  |  | 577 | 400 | 231 | 0.51 | 51.997 | 0.6125 | -4.962 | 12;-1 | 0 | Symmetrical | 1.25
TR Bucuresti Sud 400/220 2 | 30T-BUCU400AT4-R | TEL |  |  | 577 | 400 | 231 | 0.51 | 51.997 | 0.6125 | -4.962 | 12;-1 | 0 | Symmetrical | 1.25
TR Gutinas 400/220 1 | 30T-GUTI400AT5-2 | TEL |  |  | 577 | 400 | 231 | 0.656 | 42.514 | 0.3875 | -4.985 | 8;-1 | 0 | Symmetrical | 1.25
TR Gutinas 400/220 2 | 30T-GUTI400AT61W | TEL |  |  | 577 | 400 | 231 | 0.656 | 42.514 | 0.3875 | -4.985 | 8;-1 | 0 | Symmetrical | 1.25
TR Iernut 400/220 1 | 30T-IERN400AT1-U | TEL |  |  | 577 | 400 | 231 | 0.845 | 40.671 | 0.5625 | -4.968 | 7;0 | 0 | Symmetrical | 1.25
TR Lacu Sarat 400/220 1 | 30T-LACS400AT3-Q | TEL |  |  | 577 | 400 | 231 | 0.487 | 47.557 | 0.4269 | -4.982 | 8;-3 | 0 | Symmetrical | 1.25
TR Lacu Sarat 400/220 2 | 30T-LACS400AT4-N | TEL |  |  | 577 | 400 | 231 | 0.4864 | 47.518 | 0.4131 | -4.983 | 8;-3 | 0 | Symmetrical | 1.25
TR Mintia 400/220 1 | 30T-MINT400AT3-T | TEL |  |  | 577 | 400 | 231 | 0.5448 | 47.277 | 0.4688 | -4.978 | 8;-2 | 0 | Symmetrical | 1.25
TR Mintia 400/220 2 | 30T-MINT400AT4-Q | TEL |  |  | 577 | 400 | 231 | 0.5404 | 47.117 | 0.4688 | -4.978 | 8;-2 | 0 | Symmetrical | 1.25
TR Portile de Fier 400/220 1 | 30T-PDFE400AT1-A | TEL |  |  | 577 | 400 | 231 | 1.02 | 45.988 | 1.8125 | -12.368 | 12;0 | 0 | Symmetrical | 1.25
TR Portile de Fier 400/220 2 | 30T-PDFE400AT2-7 | TEL |  |  | 721 | 400 | 231 | 0.4608 | 40.637 | 0.625 | -4.33 | 7;0 | 0 | Symmetrical | 1.25
TR Portile de Fier 400/220 3 | 30T-PDFE400AT3-4 | TEL |  |  | 721 | 400 | 231 | 0.4608 | 40.637 | 0.625 | -4.33 | 7;0 | 0 | Symmetrical | 1.25
TR Rosiori 400/220 | 30T-ROSI400AT--1 | TEL |  |  | 577 | 400 | 231 | 0.492 | 47.597 | 0.4688 | -4.978 | 8;0 | 0 | Symmetrical | 1.25
TR Sibiu Sud 400/220 1 | 30T-SIBI400AT5-M | TEL |  |  | 577 | 400 | 231 | 0.602 | 43.675 | 0.375 | -4.986 | 10;0 | 0 | Symmetrical | 1.25
TR Sibiu Sud 400/220 2 | 30T-SIBI400AT6-J | TEL |  |  | 577 | 400 | 231 | 0.602 | 43.675 | 0.375 | -4.986 | 10;0 | 0 | Symmetrical | 1
TR Slatina 400/220 1 | 30T-SLAT400AT1-N | TEL |  |  | 577 | 400 | 231 | 0.7 | 42.793 | 0.3875 | -4.985 | 8;0 | 0 | Symmetrical | 1
TR Slatina 400/220 2 | 30T-SLAT400AT2-K | TEL |  |  | 577 | 400 | 231 | 0.7 | 42.793 | 0.3875 | -4.985 | 8;0 | 0 | Symmetrical | 1.25
PST Urechesti 400/220 1 | 30T-UREC400AT--F | TEL |  |  | 577 | 400 | 231 | 1.02 | 45.988 | 1.8125 | -12.368 | -12;-1 | 60 | Asymmetrical |  | 1.25

## Remedial Actions
Location
Name of RA | TSO | Description
PST_ARAD_400/220_3 | TEL | Change of tap position of phase shifting transformer (400/220) in 400kV substation Arad
PST_URECHESTI_400/220_1 | TEL | Change of tap position of phase shifting transformer (400/220) in 400kV substation Urechesti
TOP_CLOSE_TR_MINTIA_400/220_3 | TEL | Connecting the second 400/220 kV transformer in substation Mintia (Normal operation: one transformer)