# Annex II – Core TSOs general measures and action plan to avoid future cross-zonal capacity reductions

Q2 2025

Table of Contents

Introduction	2

1.	CEPS	4

2.	DAVinCy TSOs	4

2.1.	APG	4

2.1.1	Overview	4

2.1.2	Conclusion	5

2.2.	German TSOs	5

2.3.	TENNET TSO BV	5

3.	ELES	5

4.	ELIA	5

5.	HOPS	5

6.	MAVIR	6

7.	PSE	6

8.	RTE	7

9.	SEPS	8

10.	Transelectrica	8

# Introduction

This annex contains the required information for each Core TSO that has applied capacity reductions for its CNECs in more than 1% of ID CC MTUs of the analysed quarter as described per Article 18(12).

# CEPS

During the second quarter of 2025, the Czech transmission system operator (ČEPS) applied the Individual Validation Adjustment (IVA) procedure a total of 49 times.

These adjustments were exclusively related to the V443, V444, and V245 interconnection lines located in the CZ–PL–SK corner of the grid—an area consistently subject to high transit flow pressure.

A significant portion of the IVA applications stemmed from the fact that these lines were already heavily utilized in the day-ahead market, despite meeting the 70% cross-zonal capacity criterion. This pre-existing usage limited operational flexibility and, in several cases, triggered the need for IVA due to insufficient margin for secure operation.

Additionally, some instances of IVA were prompted by unresolved grid issues within the DACF (Day-Ahead Congestion Forecast) models used for running the IDCC(b). These deficiencies made the initial forecasts unsuitable for reliable capacity evaluation, necessitating validation adjustments to maintain system security.

The increased frequency of IVA in Q2 reflects the operational challenges in a highly utilized grid region, while also underscoring ČEPS's proactive approach in adapting to forecast limitations and preserving grid security under pressure.

# DAVinCy TSOs

## APG

## German TSOs

## TENNET TSO BV

# ELES

# ELIA

# HOPS

General measures to avoid cross-zonal capacity reductions in the future, as per Articles 18(10)(h)(i) and 20(11)(b) of the ID CCM

General measures include, but are not limited to:

· Network development and optimization

The goal is to increase the transmission capacity and reduce grid congestion. The measures to achieve these goals include strengthening and optimizing the existing network and the development of new infrastructure.

· Improvements concerning congestion management

Core CCR coordinated improvements with coordinated actions to increase cross-zonal capacities (for example improvements of the outage planning coordination in order to increase flexibility of the grid). Introduction of additional effective remedial actions should help to relieve the congestion and therefore allows to reduce the number of IVA application. Also, inclusion of third countries could open further opportunities for HOPS (with planning process and implementation of remedial measures). Unscheduled allocated flows coming from commercial exchanges outside the Core CCR (Fuaf) has a strong impact on HOPS grid.

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future

In the analysed quarter (Q2 2025), HOPS applied reduction to around 0,50% MTUs. For most MTUs, the reductions are applied to:

· TL  220kV Pehlin - Divaca (0,50% MTUs, or around 100% of times of all HOPS applied reductions)

Applied reductions on network element are mostly low (less than 1,70% of Fmax), while for a few MTUs during June (BD20250626) slightly higher values are applied on TL 220kV Pehlin – Divaca due to unsolvable overloads in the relevant grid area caused by unavailability of grid elements in the surrounding area, additionally under the influence of high exchanges between Core and non-Core countries (impact of uncoordinated flows coming from third countries, mainly from the direction of RS and BA). It is important to emphasize that energy needs increased during Q2 2025 in SEE with significant flows in the network towards SEE, which is why some reductions were applied during Q2 2025 to maintain a secured network. Such reductions are planned to be solved by developing and optimising the transmission network.

In Q2 of 2025, HOPS installed HTLS conductors on TL 220 kV Brinje – VE Pađene that increases its maximum admissible power flow and improves available capacities.

Also, following the ongoing investigation of various options for increasing capacity for the TL 220 kV Pehlin – Divača, it is planned to start installing HTLS conductors on TL 220 kV Pehlin – Divača in Q4 2026.

Improvements are also expected with upcoming important processes such as coordinated validation capacities and Regional Operational Security Coordination.

# MAVIR

# PSE

# RTE

# SEPS

# Transelectrica