# Annex II – Core TSOs general measures and action plan to avoid future cross-zonal capacity reductions

Q4 2025

Table of Contents

Introduction	3

1.	CEPS	4

2.	DAVinCy TSOs	4

2.1.	APG	4

2.1.1	Overview	4

2.1.2	Conclusion	5

2.2.	German TSOs	6

2.3.	TENNET TSO BV	6

3.	ELES	6

4.	ELIA	7

5.	HOPS	7

6.	MAVIR	8

7.	PSE	8

8.	RTE	8

9.	SEPS	8

10.	Transelectrica	8

# Introduction

This annex contains the required information for each Core TSO that has applied capacity reductions for its CNECs in more than 1% of ID CC MTUs of the analysed quarter as described per Article 18(12).

# CEPS

During the fourth quarter of 2025, the Czech transmission system operator (ČEPS) applied the Individual Validation Adjustment (IVA) procedure a total of 945 times in 423 distinct MTUs.

These adjustments were exclusively related to the V404, V497, V443 and V444 interconnection lines located in the CZ–PL–SK corner of the grid—an area consistently subject to high transit flow pressure.

A significant portion of the IVA applications stemmed from the fact that these lines were already heavily utilized in the day-ahead market, despite meeting the 70% cross-zonal capacity criterion. This pre-existing usage limited operational flexibility and, in several cases, triggered the need for IVA due to insufficient margin for secure operation.

In this period (Q4/2025), one of the two 400 kV cross-zonal connections between the CZ and AT bidding zones was undergoing planned maintenance, and the remaining one was also subject to a temporary outage related to maintenance and partial upgrades. As a consequence, there was a period during which no 400 kV connection between the two bidding zones was available. During this time, all market flows in the highly in-demand direction from Western to Southeastern Europe were redirected to parallel transmission paths—primarily through the 220 kV cross-zonal lines between CZ and AT and through all available cross-zonal lines along the CZ–SK border. The resulting grid situation is illustrated in the accompanying figure (with lines in planned outage marked in blue and lines with IVA applications marked in red).

Additionally, some instances of IVA were prompted by unresolved grid issues within the DACF (Day-Ahead Congestion Forecast) models used for running the IDCC(b). These deficiencies made the initial forecasts unsuitable for reliable capacity evaluation, necessitating validation adjustments to maintain system security.

The increased frequency of IVA in Q4 reflects the operational challenges in a highly utilized grid region, while also underscoring ČEPS's proactive approach in adapting to forecast limitations and preserving grid security under pressure.

Starting in November, SEPS implemented its seasonal “winter” limit on the V404 Nošovice–Varín line, as it is not yet prepared to apply DLR, which would otherwise allow for higher utilization of this corridor. Since the beginning of the month, we have not observed any significant reductions. In Q1/2026 we can see a significant drop in IVA use.

# DAVinCy TSOs

## APG

### Overview

ATC reductions are essential to prevent network overloads due to the challenges outlined below along with their mitigation measures. For IDCC(a), APG performs ATC validation, while for IDCC(b), a dual-validation approach is applied, combining ATC validation with IVA validation in coordination with six iDaVincy TSOs. This dual approach ensures robustness, particularly in special grid situations or when delays or limitations occur in the IVA process due to its relative novelty.

APG’s geographic location and outdated trading results from non-Core bidding zones

APG’s central position in the interconnected European grid, belonging to three capacity calculation regions (Core, Italy North, and SNB), and its proximity to the Balkans, increases APG’s CNEC loading sensitivity to deviations between forecasted and actual conditions as well as misalignments between the regions. This unique position amplifies the impact of outdated market data. For IDCC(a), the use of outdated non-Core D-2 SDAC net positions often leads to discrepancies. Similarly, IDCC(b) is based on the non-Core SIDC status of 16:00 D-1, failing to account for market changes up to 21:40 D-1. This can result in overestimated ATCs that risk physical overloads.

To address these issues, APG updates non-Core net positions during validation to align with actual market outcome. Additionally, APG is driving enhancements to the Core Capacity Calculation Tool to enable IDCC(a) capacities to incorporate all updated SDAC net positions and IDCC(b) capacities to use all the latest SIDC net positions. These improvements aim to enhance accuracy, reduce unnecessary local reductions, and improve operational efficiency, leading to a significant decrease in limitations during the validation step.

In general, enhanced synchronization across CCRs can ensure more consistent and reliable capacity calculations, which could prevent mismatches and reduce the frequent triggering of local validations. The introduction of the CE CCR, that will cover the Core and the Italy North CCRs, represents a significant step toward more accurate IDCC(a) capacities.

Neglect CNECs with small PTDF and RAM combinations.

The central ATC extraction algorithm excludes CNECs with RAM below 10 MW for IDCC(a) and 50 MW for IDCC(b) border where their PTDF is ≤ 1% for IDCC(a) and 3% for IDCC(b). This can result in the allocation of non-existent capacities. To mitigate this and ensure operational grid security, APG validates all Austrian CNECs.

Need for limitations higher than initial ATCs due to ATC redistribution

During the validation process, APG can only assess whether the given initial ATCs result in a combination of ATCs that do not overload any APG CNEC. However, due to the central calculation design, a redistribution of ATCs after validation is possible. This redistribution can lead to a completely new set of ATCs that were not known during the validation phase.

As a result, even when the initial ATCs pose no risk, APG calculates validated ATCs that are slightly higher than the initial ATCs. These validated ATCs can subsequently limit the final ATCs in case of significant increases caused by redistribution.

This approach is particularly important given the impact of neglected flows, as it ensures grid security despite potential redistributions.

Unlike ATC validation, IVA validation can only result in lower capacities. Thus, a validated initial domain that does not compromise grid security will remain secure after the validation step because the IVA process effectively restricts the FB domain to ensure safety.

Congestion Management Process Design Risks

APG was a main driver in incorporating IDA1 and continuous trading results (up to 16:00 D-1) into DACF grid models, improving their quality for congestion management and IDCC(b) capacity calculations. However, several challenges remain: Not all TSOs provide power-plant-level data, reducing the models' granularity and trades occurring between 16:00 D-1 and 21:40 D-1 remain uncaptured. APG needs to consider these risks in its validation. To address these gaps, APG emphasizes the need for TSOs to include more granular data and advocates for faster congestion management processes. These improvements could mitigate risks and enhance the accuracy of IDCC(b) capacities.

### Conclusion

APG is actively addressing the challenges associated with IDCC(a) and IDCC(b) calculations. By improving market data synchronization, enhancing validation processes assumptions, and contributing to broader capacity calculation advancements, APG is working to minimize the need for capacity reductions while ensuring operational security and market efficiency. Furthermore, following the 6. Amendment of the Core Intraday Capacity Methodology, it will be possible to consider the latest market changes in the non-Core SDAC/SIDC bidding zones.

## German TSOs

## TENNET TSO BV

# ELES

General measures to avoid cross-zonal capacity reductions in the future, as per Article 18(11)(b) of ID CCM:

- Improvement in congestion management – we will continue to improve the quality of our inputs for CORE ID CC in order to avoid unnecessary IVA application in case of errors in inputs files.

Network development and optimisation.

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future as per Article 18(10)(h)(i) of ID CCM

In Q4 of 2025, ELES applied reduction in 10,82 % of MTU. 93% of these reductions were applied on CNECs on AT-SI and HU-SI borders (Kainachtall – Maribor 1&2, Maribor-Cirkovce 1&2 and Cirkovce-Heviz). The remaining 7% of applied reductions were applied on CNECs on the HR-SI border (Divaca-Pehlin and Krsko-Tumbri 1&2). The main reason for the above reductions at ELES lies in the fact, that we are in the cross-road of two CCR, which both aim to maximise capacities in order to fulfil 70% criteria in DA. Often, maximisation of the capacities in Italy North CCR have negative effect on the RAM of Slovenian elements in CORE CCR. This is mostly due to the fact, that we have a PST on the Slovenian – Italian border, that is used to maximise Italy North NTC values. Maximising capacities in DA often translates to low capacities available for Intraday.

Our plan to improve the situation consists of the following:

- Additional training of operators and improvement of the local validation tool in order to improve the process and improve stability and reliability of the tool

- Analysis will be performed on accuracy of validation tool (e.g. comparing the flows considered during the validation and realised flows). Based on the result of the analysis, the validation tool reliability margin will be adjusted in order to decrease the level of IVA application.

- Network development and optimisation - For AT-SI border, we are in the process to obtain and install a static serous synchronous compensator (SSSC) in Podlog substation (currently planned for Q4 2026 or early 2027) in order to be able to redistribute and relieve the flows on the elements Kainachtal – Maribor and Obersielach- Podlog. For the Divaca – Pehlin line, we are still investigation different possibilities to increase capacities (SSSC or high temperature lines).

- In Q1-Q2 2026 ELES plans to implement DTR on all SI-HR tie-lines, that will presumably increase its Fmax in most of MTUs (expected positive impact on Divača-Pehlin tie-line)

- Improve the outage planning coordination.

# ELIA

# HOPS

General measures to avoid cross-zonal capacity reductions in the future, as per Articles 18(10)(h)(i) and 20(11)(b) of the ID CCM

General measures include, but are not limited to:

Network development and optimization

The goal is to increase the transmission capacity and reduce grid congestion. The measures to achieve these goals include strengthening and optimizing the existing network and the development of new infrastructure.

Improvements concerning congestion management

Core CCR coordinated improvements with coordinated actions to increase cross-zonal capacities (for example improvements of the outage planning coordination in order to increase flexibility of the grid). Introduction of additional effective remedial actions should help to relieve the congestion and therefore allows to reduce the number of IVA application. Also, inclusion of third countries could open further opportunities for HOPS (with planning process and implementation of remedial measures). Unscheduled allocated flows coming from commercial exchanges outside the Core CCR (Fuaf) has a strong impact on HOPS grid.

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future

In the analysed quarter (Q4 2025), HOPS applied reduction to around 7,83% MTUs. For most MTUs, the reductions are applied to:

- TL 220kV Zakucac - Mostar (0,41 % MTUs, or around 4,89 % of times of all HOPS applied reductions)

- TL 400 kV Ernestinovo – Pecs 1 (0,63% MTUs, or around 7,61% of times of all HOPS applied reductions)

- TL 400 kV Ernestinovo – Pecs 2 (0,05% MTUs, or around 0,54% of times of all HOPS applied reductions)

- TL  220kV Pehlin - Divaca (7,02% MTUs, or around 84,24% of times of all HOPS applied reductions)

- TL   220kV Zerjavinec - Podlog (0,23% MTUs, or around 2,72% of times of all HOPS applied reductions)

Applied reductions on network element are mostly low (less than 3,04% of Fmax), while for a few MTUs during October (BD20251005) higher values are applied on TL 400kV Ernestinovo - Pecs 1 due to unsolvable overloads in the relevant grid area caused by unavailability of grid elements in the surrounding area, additionally under the influence of high exchanges between Core and non-Core countries (impact of uncoordinated flows coming from third countries, mainly from the direction of RS and BA). It is important to emphasize that energy needs increased during Q4 2025 in SEE with significant flows in the network towards SEE, which is why some reductions were applied during Q4 2025 to maintain a secured network. Such reductions are planned to be solved by developing and optimising the transmission network.

In Q2 of 2025, HOPS installed HTLS conductors on OHL 220 kV Brinje – VE Pađene that increases its maximum admissible power flow and improves available capacities, , while the upgrade continued in Q4 2025 and Q1 2026 on OHL 220 kV Brinje – VE Pađene and OHL 220 kV Konjsko – Pađene after which the entire Brinje – VE Pađene – Konjsko section will have HTLS installed.

Also, following the ongoing investigation of various options for increasing capacity for the TL 220 kV Pehlin – Divača, it is planned to start installing HTLS conductors on TL 220 kV Pehlin – Divača in Q4 2026.

Improvements are also expected with upcoming important processes such as coordinated validation capacities and Regional Operational Security Coordination.

# MAVIR

# PSE

# RTE

# SEPS

In the analysed quarter (Q4 2025), SEPS applied reductions in approximately 1.13% of MTUs, with a total curtailed volume of 5460 MW. For most MTUs, the reductions were applied on the following tie-lines:

- TL 400 kV [CZ–SK] Nosovice – Varin [DIR] [SK]

- TL 400 kV [SK–SK] Velky Dur – Levice 1 [DIR]

- TL 400 kV [SK–HU] Levice – Göd [DIR] [SK]

General measures to avoid cross-zonal capacity reductions in the future

A planned reinforcement of the Nošovice – Varín tie-line is expected to increase the maximum current (Imax) from 1740 A to 2000 A by 2029, which should reduce the IVA volume applied on this element.

For the CNE Veľký Ďur – Levice 1 and Levice – God the following solutions is planned:
The aim of the project is to connect the V492 Veľký Ďur – Horná Ždaňa line to the 400 kV switchyard in the Levice substation, to modify the connection of the V491 Veľký Ďur – Levice line in the 400 kV switchyard in the Levice substation, and to interconnect the V490 Veľký Ďur – Levice and V449 Levice – SK/HU state border (Göd) lines, including adjustments to secondary equipment in the related SEPS substations. The project is currently scheduled for completion by Q2 2029.

The national ten-year development plan also includes additional planned reinforcements.

# Transelectrica

In addition to being part of the Core CCR, Transelectrica is also part of SEE CCR with RO – BG border having operational processes for the First Intraday capacity calculation since October 2021 and Second Intraday capacity calculation since October 2022. Moreover, there are three non-EU borders for which there is no coordinated capacity calculation.

Regarding the capacity calculation process, the Core ID CCM allows TSOs to correct cross-zonal capacity for reasons of operational security during the validation process individually and in a coordinated way according to Article 18 (2): “Each Core TSO shall validate and have the right to decrease the RAM for reasons of operational security during individual validation. [...] IVA may reduce the RAM only to the minimum degree that is needed to ensure operational security, and only after all the expected available costly and non-costly remedial actions pursuant to Article 22 of the SO Regulation are considered”.

For the period 20251001 – 20251231, Transelectrica applied an Individual Validation Adjustment (IVA) on the following CNEs, for a total of 18.61% of MTUs. In the graph below the average IVA per CNE is represented for the timestamps where reductions were applied.

OHL 400 kV Portile de Fier – Djerdap is a tieline between Romania and Serbia, both countries having tielines with Bulgaria and Hungary. Because of this, the power flows on OHL 400 kV Portile de Fier – Djerdap are highly impacted by the cross-border exchanges between RO-BG, RO-RS, RO-HU.

General measures to avoid cross-zonal capacity reductions in the future, as per Articles 18(10)(h)(i) and 20(11)(b) of the ID CCM.

Development of the transmission grid

The main measure to reduce overloads in the capacity calculation process is to finalize investment projects with cross-border impact:

- New OHL 400 kV Portile de Fier – Resita and TIE 400 kV Resita – Pancevo circ. 2 have been commissioned in mid November 2024. TIE 400 kV Resita – Pancevo circ. 1 was commissioned in February 2025.

- New Autotransformer 400/220 kV in Rosiori substation to be commissioned in 2028;

- 400 kV OHL Resita – Timisoara – Sacalaz to be commissioned in 2027;

- 400 kV d.c. OHL Timisoara – Arad to be commissioned in 2028;

- Increasing the transmission capacity on the OHLs 220 kV Urechesti – Targu Jiu Nord – Paroseni – Baru Mare – Hasdat to be commissioned in 2028;

- Increasing the transmission capacity on the OHL 220 kV d.c. Portile de Fier – Resita to be commissioned in 2028;

- 400 kV TIE Nadab – Graniceri circ. 2 to be commissioned in 2028;

- 400 kV TIE Portile de Fier – Djerdap circ.2 to be commissioned in 2029;

- 400 kV TIE Oradea Sud – Josza to be commissioned in 2030.

Outage planning coordination

Relevant assets are coordinated in the Outage coordination regions. This coordination has the scope of avoiding simultaneous disconnection of multiple elements with cross-border impact, taking into consideration the system security as a first step. Lately it has been observed that the finalization of the Yearly Maintenance Plan is highly impacted by the level of cross-border capacities provided to the market. Thus, it became a necessity to coordinate the outage of relevant assets also from the perspective of the capacity calculation processes.

Implementation of regional coordinated processes for security analysis and redispatching and countertrading processes

Results of the intraday capacity calculation process come with a lot of uncertainties, mainly due to the input data, volumes of capacity allocated and available redispatching. Measures to decrease the need of application of IVA include the consideration of internal redispatching. Due to the proximity to real-time, multiple power plants cannot be considered. Also, depending on the location of the congested elements, there may be none, one or multiple generators that can help decreasing the overload, but not necessarily avoiding them altogether.

It is thus mandatory to have security analysis implemented at regional level before real-time with coordinated means of reducing the observed overloads.

At Core CCR level these processes are still under implementation.