## DA Results (hidden)
DA results
|  |  | TTC Adjustment |  |  | TTC Validated |  |  | ANTC |  |  | LimitedBy | [8 empty] | AT | AT | AT | AT | AT | AT | CH | CH | CH | CH | CH | CH | FR | FR | FR | FR | FR | FR | IT | IT | IT | IT | IT | IT | SI | SI | SI | SI | SI | SI
Business day | Month | Timestamp | TTC_Full_Import | TTCImport | TTCExport | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | 70% red | TTCRed_Import | TTCRed_Transit_Import | TTCRed_Transit_Export | TTCRed_Transit | TTC and 70% red | FLAG | Bilateral | MNII | Reason | Bilateral - Export | MNIE | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason
20250701 | July | 0030 | 8326 |  |  | 7816 |  |  | -1564 | -1564 | -1054 | Critical Branch | Validation phase | 0 | 510 | NA | NA | NA | 0 | 1 | CH: 7506; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250701 | July | 0130 | 8326 |  |  | 7816 |  |  | -1564 | -1564 | -1054 | Critical Branch | Validation phase | 0 | 510 | NA | NA | NA | 0 | 1 | CH: 7506; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250701 | July | 0230 | 8326 |  |  | 7816 |  |  | -1564 | -1564 | -1054 | Critical Branch | Validation phase | 0 | 510 | NA | NA | NA | 0 | 1 | CH: 7506; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250701 | July | 0330 | 8611 |  |  | 8493 |  |  | -1504 | -1504 | -1386 | Critical Branch | Validation phase | 0 | 118 | NA | NA | NA | 0 | 1 | CH: 8183; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0430 | 8611 |  |  | 8493 |  |  | -1504 | -1504 | -1386 | Critical Branch | Validation phase | 0 | 118 | NA | NA | NA | 0 | 1 | CH: 8183; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0530 | 8611 |  |  | 8493 |  |  | -1504 | -1504 | -1386 | Critical Branch | Validation phase | 0 | 118 | NA | NA | NA | 0 | 1 | CH: 8183; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0630 | 8411 |  |  | 8293 |  |  | -1283 | -1283 | -1165 | Critical Branch | Validation phase | 0 | 118 | NA | NA | NA | 0 | 1 | CH: 7983; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0730 | 8206 |  |  | 8158 |  |  | -5053 | -5053 | -5005 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | CH: 7843; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0830 | 8206 |  |  | 7990 |  |  | -5053 | -5053 | -4837 | Critical Branch | Smoothing ramp | 0 | 216 | NA | NA | NA | 0 | 1 | CH: 7843; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0930 | 6490 |  |  | 6490 |  |  | -70 | -70 | -70 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250701 | July | 1030 | 6490 |  |  | 6490 |  |  | -70 | -70 | -70 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250701 | July | 1130 | 6490 |  |  | 6441 |  |  | -70 | -70 | -21 | TTC Selection - LTTC | Smoothing ramp | 0 | 49 | NA | NA | NA | 0 | 1
20250701 | July | 1230 | 6490 |  |  | 4941 |  |  | -169 | -169 | 1380 | TTC Selection - LTTC | Validation phase | 0 | 1549 | NA | NA | NA | 2929 | 1 | CH: 4626; CH: Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA
20250701 | July | 1330 | 6490 |  |  | 4941 |  |  | -169 | -169 | 1380 | TTC Selection - LTTC | Validation phase | 0 | 1549 | NA | NA | NA | 2929 | 1 | CH: 4626; CH: Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA
20250701 | July | 1430 | 6490 |  |  | 4941 |  |  | -169 | -169 | 1380 | TTC Selection - LTTC | Validation phase | 0 | 1549 | NA | NA | NA | 2929 | 1 | CH: 4626; CH: Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA
20250701 | July | 1530 |  | 6570 | 564 |  | 6216 | 564 | 77 | 77 | 0 | Adjustment reached | Smoothing ramp | 0 | NA | 354 | 0 | 354 | -77 | 1
20250701 | July | 1630 |  | 6570 | 564 |  | 6570 | 564 | 77 | 77 | 0 | Adjustment reached | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | -77 | 0
20250701 | July | 1730 |  | 6570 | 564 |  | 6570 | 564 | 77 | 77 | 0 | Adjustment reached | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | -77 | 0
20250701 | July | 1830 |  | 7763 | 620 |  | 7712 | 616 | -1898 | -1898 | 0 | Critical Branch | Validation phase | 0 | NA | 51 | 4 | 55 | 1898 | 1 | CH: 7722; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 1930 |  | 7763 | 620 |  | 7712 | 616 | -1898 | -1898 | 0 | Critical Branch | Validation phase | 0 | NA | 51 | 4 | 55 | 1898 | 1 | CH: 7722; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2030 |  | 7763 | 620 |  | 7712 | 616 | -1898 | -1898 | 0 | Critical Branch | Validation phase | 0 | NA | 51 | 4 | 55 | 1898 | 1 | CH: 7722; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2130 |  | 7611 | 625 |  | 7578 | 622 | -1834 | -1834 | 0 | Critical Branch | Validation phase | 0 | NA | 33 | 3 | 36 | 1834 | 1 | CH: 7565; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2230 |  | 7611 | 625 |  | 7578 | 622 | -1834 | -1834 | 0 | Critical Branch | Validation phase | 0 | NA | 33 | 3 | 36 | 1834 | 1 | CH: 7565; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2330 |  | 7046 | 650 |  | 7033 | 649 | -1205 | -1205 | 0 | Critical Branch | Validation phase | 0 | NA | 13 | 1 | 14 | 1205 | 1 | CH: 6985; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250702 | July | 0030 | 7084 |  |  | 7084 |  |  | -3447 | -3447 | -3446 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0130 | 7084 |  |  | 7084 |  |  | -3447 | -3447 | -3446 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0230 | 7084 |  |  | 7084 |  |  | -3447 | -3447 | -3446 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0330 | 8923 |  |  | 8299 |  |  | -4881 | -4881 | -4257 | Critical Branch | Validation phase | 0 | 624 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0430 | 8923 |  |  | 8299 |  |  | -4881 | -4881 | -4257 | Critical Branch | Validation phase | 0 | 624 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0530 | 8923 |  |  | 8000 |  |  | -4881 | -4881 | -3959 | Critical Branch | Validation phase | 0 | 923 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0630 | 8723 |  |  | 6500 |  |  | -4673 | -4673 | -2456 | Critical Branch | Validation phase | 0 | 2223 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0730 | 7335 |  |  | 5000 |  |  | -1788 | -1788 | 547 | Critical Branch | Validation phase | 0 | 2335 | NA | NA | NA | 2882 | 1 | AT: 190; AT: 70; CH: 4685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0830 | 7335 |  |  | 5000 |  |  | -1788 | -1788 | 547 | Critical Branch | Validation phase | 0 | 2335 | NA | NA | NA | 2882 | 1 | AT: 176; AT: 70; CH: 4685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0930 | 5315 |  |  | 5000 |  |  | -84 | -84 | 231 | TTC Selection - LTTC | Validation phase | 0 | 315 | NA | NA | NA | 546 | 1 | AT: 164; AT: 70; CH: 4685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1030 | 5315 |  |  | 5000 |  |  | -84 | -84 | 231 | TTC Selection - LTTC | Validation phase | 0 | 315 | NA | NA | NA | 546 | 1 | AT: 164; AT: 70; CH: 4685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1130 | 5315 |  |  | 5000 |  |  | -84 | -84 | 231 | TTC Selection - LTTC | Validation phase | 0 | 315 | NA | NA | NA | 546 | 1 | AT: 164; AT: 70; CH: 4685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1230 | 6684 |  |  | 5500 |  |  | 890 | 469 | 1605 | Minimum Margin | Validation phase | 421 | 1184 | NA | NA | NA | 2741 | 1 | AT: 178; AT: 70; CH: 5185; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250702 | July | 1330 | 6426 |  |  | 5500 |  |  | 890 | 211 | 1605 | Minimum Margin | Validation phase | 679 | 926 | NA | NA | NA | 2999 | 1 | AT: 173; AT: 70; CH: 5185; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250702 | July | 1430 | 6383 |  |  | 5500 |  |  | 890 | 168 | 1605 | Minimum Margin | Validation phase | 722 | 883 | NA | NA | NA | 3042 | 1 | AT: 172; AT: 70; CH: 5185; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250702 | July | 1530 | 6215 |  |  | 5500 |  |  | -621 | -621 | 94 | TTC Selection - LTTC | Validation phase | 0 | 715 | NA | NA | NA | 809 | 1 | AT: 169; AT: 70; CH: 5185; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1630 | 6215 |  |  | 5500 |  |  | -621 | -621 | 94 | TTC Selection - LTTC | Validation phase | 0 | 715 | NA | NA | NA | 809 | 1 | AT: 169; AT: 70; CH: 5185; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1730 | 6515 |  |  | 6000 |  |  | -940 | -940 | -425 | TTC Selection - LTTC | Validation phase | 0 | 515 | NA | NA | NA | 0 | 1 | AT: 171; AT: 70; CH: 5685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1830 |  | 8103 | 700 |  | 5715 | 565 | -2249 | -2249 | 0 | Critical Branch | Validation phase | 0 | NA | 2388 | 135 | 2523 | 2249 | 1 | AT: 197; AT: 69; CH: 5685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1930 |  | 8103 | 700 |  | 5715 | 32 | -2249 | -2249 | 0 | Critical Branch | Validation phase | 0 | NA | 2388 | 668 | 3056 | 2249 | 1 | AT: 206; AT: 69; CH: 5685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: Forecasted Security Violations
20250702 | July | 2030 |  | 8103 | 700 |  | 5715 | 32 | -2249 | -2249 | 0 | Critical Branch | Validation phase | 0 | NA | 2388 | 668 | 3056 | 2249 | 1 | AT: 206; AT: 69; CH: 5685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: Forecasted Security Violations
20250702 | July | 2130 |  | 8376 | 715 |  | 5706 | 32 | -6111 | -6111 | 0 | Critical Branch | Validation phase | 0 | NA | 2670 | 683 | 3353 | 6111 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 68; AT: Reduction because NTC over thermal limit on border; CH: 5685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: Forecasted Security Violations
20250702 | July | 2230 |  | 8376 | 715 |  | 6706 | 577 | -6111 | -6111 | 0 | Critical Branch | Validation phase | 0 | NA | 1670 | 138 | 1808 | 6111 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 68; AT: Reduction because NTC over thermal limit on border; CH: 6685; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 2330 |  | 7806 | 740 |  | 7804 | 740 | -5498 | -5498 | 0 | Critical Branch | Validation phase | 0 | NA | 2 | 0 | 2 | 5498 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 69; AT: Reduction because NTC over thermal limit on border; CH: 7990; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250703 | July | 0030 | 8972 |  |  | 8920 |  |  | -1700 | -1700 | -1648 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | CH: 8610; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250703 | July | 0130 | 8972 |  |  | 8920 |  |  | -1700 | -1700 | -1648 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | CH: 8610; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250703 | July | 0230 | 8972 |  |  | 8920 |  |  | -1700 | -1700 | -1648 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | CH: 8610; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250703 | July | 0330 | 8784 |  |  | 8784 |  |  | -2869 | -2869 | -2869 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250703 | July | 0430 | 8784 |  |  | 8784 |  |  | -2869 | -2869 | -2869 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250703 | July | 0530 | 8784 |  |  | 8784 |  |  | -2869 | -2869 | -2869 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250703 | July | 0630 | 8584 |  |  | 8584 |  |  | -2638 | -2638 | -2638 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250703 | July | 0730 | 8485 |  |  | 7907 |  |  | -1743 | -1743 | -1165 | Critical Branch | Validation phase | 0 | 578 | NA | NA | NA | 0 | 1 | CH: 7592; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 0830 | 8485 |  |  | 7907 |  |  | -1743 | -1743 | -1165 | Critical Branch | Validation phase | 0 | 578 | NA | NA | NA | 0 | 1 | CH: 7592; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 0930 | 7530 |  |  | 6692 |  |  | -3717 | -3717 | -2879 | Critical Branch | Validation phase | 0 | 838 | NA | NA | NA | 0 | 1 | CH: 6377; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1030 | 7530 |  |  | 6692 |  |  | -3717 | -3717 | -2879 | Critical Branch | Validation phase | 0 | 838 | NA | NA | NA | 0 | 1 | CH: 6377; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1130 | 7530 |  |  | 6692 |  |  | -3717 | -3717 | -2879 | Critical Branch | Validation phase | 0 | 838 | NA | NA | NA | 0 | 1 | CH: 6377; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1230 | 8371 |  |  | 7065 |  |  | -646 | -646 | 660 | Critical Branch | Validation phase | 0 | 1306 | NA | NA | NA | 1966 | 1 | CH: 6750; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1330 | 8371 |  |  | 7065 |  |  | -646 | -646 | 660 | Critical Branch | Validation phase | 0 | 1306 | NA | NA | NA | 1966 | 1 | CH: 6750; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1430 | 8371 |  |  | 7065 |  |  | -646 | -646 | 660 | Critical Branch | Validation phase | 0 | 1306 | NA | NA | NA | 1966 | 1 | CH: 6750; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1530 | 8678 |  |  | 7847 |  |  | -1197 | -1197 | -366 | Critical Branch | Validation phase | 0 | 831 | NA | NA | NA | 0 | 1 | CH: 7532; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1630 | 8678 |  |  | 7847 |  |  | -1197 | -1197 | -366 | Critical Branch | Validation phase | 0 | 831 | NA | NA | NA | 0 | 1 | CH: 7532; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1730 | 8678 |  |  | 7847 |  |  | -1197 | -1197 | -366 | Critical Branch | Validation phase | 0 | 831 | NA | NA | NA | 0 | 1 | CH: 7532; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1830 |  | 8780 | 693 |  | 8780 | 556 | -2553 | -2553 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 0 | 137 | 137 | 2553 | 1
20250703 | July | 1930 |  | 8780 | 693 |  | 8780 | 31 | -2553 | -2553 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 662 | 662 | 2553 | 0 | IT: Forecasted Security Violations
20250703 | July | 2030 |  | 8780 | 693 |  | 8780 | 31 | -2553 | -2553 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 662 | 662 | 2553 | 0 | IT: Forecasted Security Violations
20250703 | July | 2130 |  | 8764 | 702 |  | 8764 | 31 | -5778 | -5778 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 671 | 671 | 5778 | 0 | IT: Forecasted Security Violations
20250703 | July | 2230 |  | 8764 | 702 |  | 8764 | 563 | -5778 | -5778 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 0 | 139 | 139 | 5778 | 1
20250703 | July | 2330 |  | 8184 | 727 |  | 8184 | 727 | -5151 | -5151 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5151 | 0
20250704 | July | 0030 | 8382 |  |  | 8023 |  |  | -3583 | -3583 | -3224 | Critical Branch | Validation phase | 0 | 359 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160; CH: 7713; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0130 | 8382 |  |  | 8023 |  |  | -3583 | -3583 | -3224 | Critical Branch | Validation phase | 0 | 359 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160; CH: 7713; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0230 | 8382 |  |  | 8023 |  |  | -3583 | -3583 | -3224 | Critical Branch | Validation phase | 0 | 359 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160; CH: 7713; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0330 | 8424 |  |  | 7680 |  |  | -4785 | -4785 | -4041 | Critical Branch | Validation phase | 0 | 744 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160; CH: 7370; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0430 | 8424 |  |  | 7680 |  |  | -4785 | -4785 | -4041 | Critical Branch | Validation phase | 0 | 744 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160; CH: 7370; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0530 | 8424 |  |  | 7680 |  |  | -4785 | -4785 | -4041 | Critical Branch | Validation phase | 0 | 744 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160; CH: 7370; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0630 | 8224 |  |  | 7480 |  |  | -4580 | -4580 | -3836 | Critical Branch | Validation phase | 0 | 744 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160; CH: 7170; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0730 | 8343 |  |  | 7347 |  |  | -4371 | -4371 | -3375 | Critical Branch | Validation phase | 0 | 996 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140; CH: 7032; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0830 | 8343 |  |  | 7347 |  |  | -4371 | -4371 | -3375 | Critical Branch | Validation phase | 0 | 996 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140; CH: 7032; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0930 | 7021 |  |  | 6640 |  |  | -3512 | -3512 | -3131 | Critical Branch | Validation phase | 0 | 381 | NA | NA | NA | 0 | 1 | AT: 343; AT: 140; CH: 6325; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1030 | 7021 |  |  | 6640 |  |  | -3512 | -3512 | -3131 | Critical Branch | Validation phase | 0 | 381 | NA | NA | NA | 0 | 1 | AT: 343; AT: 140; CH: 6325; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1130 | 7021 |  |  | 6403 |  |  | -3512 | -3512 | -2893 | Critical Branch | Validation phase | 0 | 618 | NA | NA | NA | 0 | 1 | AT: 343; AT: 140; CH: 6325; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1230 | 7075 |  |  | 4903 |  |  | 7348 | 345 | 9175 | Minimum Margin | Validation phase | 7003 | 2172 | NA | NA | NA | 18005 | 1 | AT: 346; AT: 140; CH: 4588; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250704 | July | 1330 | 7071 |  |  | 4903 |  |  | 7348 | 341 | 9175 | Minimum Margin | Validation phase | 7007 | 2168 | NA | NA | NA | 18009 | 1 | AT: 346; AT: 140; CH: 4588; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250704 | July | 1430 | 7049 |  |  | 4903 |  |  | 7348 | 319 | 9175 | Minimum Margin | Validation phase | 7029 | 2146 | NA | NA | NA | 18031 | 1 | AT: 345; AT: 140; CH: 4588; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250704 | July | 1530 | 7819 |  |  | 6092 |  |  | -663 | -663 | 1064 | Critical Branch | Validation phase | 0 | 1727 | NA | NA | NA | 2791 | 1 | AT: 378; AT: 140; CH: 5777; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1630 | 7819 |  |  | 6092 |  |  | -663 | -663 | 1064 | Critical Branch | Validation phase | 0 | 1727 | NA | NA | NA | 2791 | 1 | AT: 378; AT: 140; CH: 5777; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1730 | 7819 |  |  | 6092 |  |  | -663 | -663 | 1064 | Critical Branch | Validation phase | 0 | 1727 | NA | NA | NA | 2791 | 1 | AT: 378; AT: 140; CH: 5777; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1830 |  | 8571 | 678 |  | 7333 | 482 | -2320 | -2320 | 0 | Critical Branch | Validation phase | 0 | NA | 1238 | 196 | 1434 | 2320 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8526; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1930 |  | 8571 | 678 |  | 8353 | 244 | -2320 | -2320 | 0 | Critical Branch | Validation phase | 0 | NA | 218 | 434 | 652 | 2320 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8526; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 213; IT: Forecasted Security Violations
20250704 | July | 2030 |  | 8571 | 678 |  | 8353 | 244 | -2320 | -2320 | 0 | Critical Branch | Validation phase | 0 | NA | 218 | 434 | 652 | 2320 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8526; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 213; IT: Forecasted Security Violations
20250704 | July | 2130 |  | 8519 | 683 |  | 8517 | 244 | -2730 | -2730 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 439 | 441 | 2730 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; IT: 213; IT: Forecasted Security Violations
20250704 | July | 2230 |  | 8519 | 683 |  | 8517 | 496 | -2730 | -2730 | 0 | Critical Branch | Critical Branch | 0 | NA | 2 | 187 | 189 | 2730 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border
20250704 | July | 2330 |  | 7939 | 708 |  | 7938 | 690 | -2084 | -2084 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 18 | 19 | 2084 | 1 | AT: 415; AT: 158
20250705 | July | 0030 | 9031 |  |  | 9005 |  |  | -5384 | -5384 | -5351 | Critical Branch | Critical Branch | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0130 | 9031 |  |  | 9005 |  |  | -5384 | -5384 | -5351 | Critical Branch | Critical Branch | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0230 | 9031 |  |  | 9005 |  |  | -5384 | -5384 | -5351 | Critical Branch | Critical Branch | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0330 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 0 | 32 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0430 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 0 | 32 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0530 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 0 | 32 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0630 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 0 | 32 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250705 | July | 0730 | 8707 |  |  | 8574 |  |  | -5369 | -5369 | -5236 | Critical Branch | Validation phase | 0 | 133 | NA | NA | NA | 0 | 1 | AT: 410; AT: 140; CH: 8259; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 0830 | 8707 |  |  | 8379 |  |  | -5369 | -5369 | -5036 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140; CH: 8259; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 0930 | 6880 |  |  | 6879 |  |  | -3721 | -3721 | -3720 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 332; AT: 140
20250705 | July | 1030 | 6880 |  |  | 6879 |  |  | -3721 | -3721 | -3720 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 332; AT: 140
20250705 | July | 1130 | 6880 |  |  | 6879 |  |  | -3721 | -3721 | -3720 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 332; AT: 140
20250705 | July | 1230 | 6880 |  |  | 6879 |  |  | -10 | -10 | -9 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 332; AT: 140
20250705 | July | 1330 | 6880 |  |  | 6879 |  |  | -10 | -10 | -9 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 332; AT: 140
20250705 | July | 1430 | 6880 |  |  | 6879 |  |  | -10 | -10 | -9 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 332; AT: 140
20250705 | July | 1530 | 7032 |  |  | 7032 |  |  | -3626 | -3626 | -3626 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 339; AT: 140
20250705 | July | 1630 | 7032 |  |  | 7032 |  |  | -3626 | -3626 | -3626 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 339; AT: 140
20250705 | July | 1730 | 7032 |  |  | 7032 |  |  | -3626 | -3626 | -3626 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 339; AT: 140
20250705 | July | 1830 |  | 8443 | 693 |  | 8245 | 681 | -2402 | -2402 | 0 | Critical Branch | Validation phase | 0 | NA | 198 | 12 | 210 | 2402 | 1 | AT: 412; AT: 138; CH: 8416; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 1930 |  | 8443 | 693 |  | 8294 | 681 | -2402 | -2402 | 0 | Critical Branch | Validation phase | 0 | NA | 149 | 12 | 161 | 2402 | 1 | AT: 423; AT: 138; CH: 8416; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 2030 |  | 8443 | 693 |  | 8294 | 681 | -2402 | -2402 | 0 | Critical Branch | Validation phase | 0 | NA | 149 | 12 | 161 | 2402 | 1 | AT: 423; AT: 138; CH: 8416; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 2130 | 9087 |  |  | 9063 |  |  | -5088 | -5088 | -5065 | Critical Branch | Validation phase | 0 | 24 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8749; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250705 | July | 2230 | 9087 |  |  | 9063 |  |  | -5088 | -5088 | -5065 | Critical Branch | Validation phase | 0 | 24 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8749; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250705 | July | 2330 | 8487 |  |  | 8463 |  |  | -4479 | -4479 | -4456 | Critical Branch | Validation phase | 0 | 24 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8154; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250706 | July | 0030 | 8740 |  |  | 8727 |  |  | -2253 | -2253 | -2241 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0130 | 8740 |  |  | 8727 |  |  | -2253 | -2253 | -2241 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0230 | 8740 |  |  | 8727 |  |  | -2253 | -2253 | -2241 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0330 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0430 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0530 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0630 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 0730 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250706 | July | 0830 | 8450 |  |  | 8071 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 379 | NA | NA | NA | 0 | 1 | AT: 395; AT: 160
20250706 | July | 0930 | 6572 |  |  | 6571 |  |  | -367 | -367 | -366 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 330; AT: 160
20250706 | July | 1030 | 6572 |  |  | 6000 |  |  | -367 | -367 | 205 | Critical Branch | Validation phase | 0 | 572 | NA | NA | NA | 777 | 1 | AT: 330; AT: 160; IT: 5690; IT: Secure Value
20250706 | July | 1130 | 6572 |  |  | 6000 |  |  | -367 | -367 | 205 | Critical Branch | Validation phase | 0 | 572 | NA | NA | NA | 777 | 1 | AT: 330; AT: 160; IT: 5690; IT: Secure Value
20250706 | July | 1230 | 6280 |  |  | 5282 |  |  | -2875 | -2875 | -1877 | TTC Selection - LTTC | Validation phase | 0 | 998 | NA | NA | NA | 0 | 1 | AT: 317; AT: 160; CH: 4972; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 5690; IT: Secure Value
20250706 | July | 1330 | 6280 |  |  | 5282 |  |  | -2875 | -2875 | -1877 | TTC Selection - LTTC | Validation phase | 0 | 998 | NA | NA | NA | 0 | 1 | AT: 317; AT: 160; CH: 4972; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 5690; IT: Secure Value
20250706 | July | 1430 | 6280 |  |  | 5282 |  |  | -2875 | -2875 | -1877 | TTC Selection - LTTC | Validation phase | 0 | 998 | NA | NA | NA | 0 | 1 | AT: 317; AT: 160; CH: 4972; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 5690; IT: Secure Value
20250706 | July | 1530 | 6437 |  |  | 6000 |  |  | -2307 | -2307 | -1870 | Critical Branch | Validation phase | 0 | 437 | NA | NA | NA | 0 | 1 | AT: 324; AT: 160; IT: 5690; IT: Secure Value
20250706 | July | 1630 | 6437 |  |  | 6000 |  |  | -2307 | -2307 | -1870 | Critical Branch | Validation phase | 0 | 437 | NA | NA | NA | 0 | 1 | AT: 324; AT: 160; IT: 5690; IT: Secure Value
20250706 | July | 1730 | 6437 |  |  | 6437 |  |  | -2307 | -2307 | -2307 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 324; AT: 160
20250706 | July | 1830 | 8923 |  |  | 7937 |  |  | -1659 | -1659 | -690 | Critical Branch | Validation phase | 0 | 986 | NA | NA | NA | 0 | 1 | AT: 385; AT: 160; CH: 8523; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250706 | July | 1930 | 8923 |  |  | 8816 |  |  | -1659 | -1659 | -1558 | Critical Branch | Validation phase | 0 | 107 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8523; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250706 | July | 2030 | 8923 |  |  | 8816 |  |  | -1659 | -1659 | -1558 | Critical Branch | Validation phase | 0 | 107 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8523; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250706 | July | 2130 | 8682 |  |  | 8672 |  |  | -1531 | -1531 | -1524 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 2230 | 8682 |  |  | 8672 |  |  | -1531 | -1531 | -1524 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250706 | July | 2330 | 8682 |  |  | 8672 |  |  | -1531 | -1531 | -1524 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250707 | July | 0030 | 8016 |  |  | 8016 |  |  | -2085 | -2085 | -2085 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 160
20250707 | July | 0130 | 8016 |  |  | 8016 |  |  | -2085 | -2085 | -2085 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 160
20250707 | July | 0230 | 8016 |  |  | 8016 |  |  | -2085 | -2085 | -2085 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 160
20250707 | July | 0330 | 8411 |  |  | 8411 |  |  | -1954 | -1954 | -1953 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250707 | July | 0430 | 8411 |  |  | 8411 |  |  | -1954 | -1954 | -1953 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250707 | July | 0530 | 8411 |  |  | 8411 |  |  | -1954 | -1954 | -1953 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250707 | July | 0630 | 8211 |  |  | 8072 |  |  | -1715 | -1715 | -1576 | Critical Branch | Critical Branch | 0 | 139 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250707 | July | 0730 | 6993 |  |  | 6572 |  |  | -2513 | -2513 | -2163 | Critical Branch | Validation phase | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 342; AT: 140; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250707 | July | 0830 | 5693 |  |  | 5693 |  |  | -1332 | -1332 | -1332 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 327; AT: 140
20250707 | July | 0930 | 7718 |  |  | 7089 |  |  | -1709 | -1709 | -1080 | Critical Branch | Validation phase | 0 | 629 | NA | NA | NA | 0 | 1 | AT: 399; AT: 140; CH: 6774; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250707 | July | 1030 | 7718 |  |  | 7089 |  |  | -1709 | -1709 | -1080 | Critical Branch | Validation phase | 0 | 629 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6774; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250707 | July | 1130 | 7718 |  |  | 7089 |  |  | -1709 | -1709 | -1080 | Critical Branch | Validation phase | 0 | 629 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6774; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250707 | July | 1230 | 7118 |  |  | 7118 |  |  | -3383 | -3383 | -3383 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140
20250707 | July | 1330 | 7118 |  |  | 7118 |  |  | -3383 | -3383 | -3383 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140
20250707 | July | 1430 | 7118 |  |  | 7118 |  |  | -3383 | -3383 | -3383 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140
20250707 | July | 1530 | 7713 |  |  | 7707 |  |  | -4375 | -4375 | -4371 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250707 | July | 1630 | 7713 |  |  | 7707 |  |  | -4375 | -4375 | -4371 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250707 | July | 1730 | 7713 |  |  | 7707 |  |  | -4375 | -4375 | -4371 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250707 | July | 1830 |  | 6768 | 637 |  | 6767 | 637 | -2640 | -2640 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2640 | 1 | AT: 402; AT: 140
20250707 | July | 1930 |  | 6768 | 637 |  | 6767 | 637 | -2640 | -2640 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2640 | 1 | AT: 402; AT: 140
20250707 | July | 2030 |  | 6768 | 637 |  | 6767 | 637 | -2640 | -2640 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2640 | 1 | AT: 402; AT: 140
20250707 | July | 2130 |  | 6847 | 660 |  | 6847 | 660 | -2085 | -2085 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2085 | 1 | AT: 407; AT: 139
20250707 | July | 2230 |  | 6847 | 660 |  | 6847 | 660 | -2085 | -2085 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2085 | 1 | AT: 407; AT: 139
20250707 | July | 2330 |  | 6267 | 685 |  | 6266 | 685 | -1463 | -1463 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1463 | 1 | AT: 394; AT: 159
20250708 | July | 0030 | 7586 |  |  | 7563 |  |  | -4254 | -4254 | -4240 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0130 | 7586 |  |  | 7563 |  |  | -4254 | -4254 | -4240 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0230 | 7586 |  |  | 7563 |  |  | -4254 | -4254 | -4240 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0330 | 7466 |  |  | 7449 |  |  | -3932 | -3932 | -3921 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0430 | 7466 |  |  | 7449 |  |  | -3932 | -3932 | -3921 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0530 | 7466 |  |  | 7449 |  |  | -3932 | -3932 | -3921 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0630 | 7266 |  |  | 7248 |  |  | -3724 | -3724 | -3714 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250708 | July | 0730 | 7108 |  |  | 7107 |  |  | -4452 | -4452 | -4452 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 399; AT: 140
20250708 | July | 0830 | 7108 |  |  | 7107 |  |  | -4452 | -4452 | -4452 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 399; AT: 140
20250708 | July | 0930 | 6028 |  |  | 6027 |  |  | -1279 | -1279 | -1278 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 344; AT: 140
20250708 | July | 1030 | 6028 |  |  | 6027 |  |  | -1279 | -1279 | -1278 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 344; AT: 140
20250708 | July | 1130 | 6028 |  |  | 6027 |  |  | -1279 | -1279 | -1278 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 344; AT: 140
20250708 | July | 1230 | 6944 |  |  | 6944 |  |  | -1793 | -1793 | -1793 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140
20250708 | July | 1330 | 6729 |  |  | 6729 |  |  | -1643 | -1643 | -1643 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 196; AT: 70
20250708 | July | 1430 | 6729 |  |  | 6729 |  |  | -1643 | -1643 | -1643 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 196; AT: 70
20250708 | July | 1530 | 6207 |  |  | 6206 |  |  | -1233 | -1233 | -1233 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 184; AT: 70
20250708 | July | 1630 | 6207 |  |  | 6206 |  |  | -1233 | -1233 | -1233 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 184; AT: 70
20250708 | July | 1730 | 6422 |  |  | 6421 |  |  | -1386 | -1386 | -1385 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 364; AT: 140
20250708 | July | 1830 |  | 5470 | 515 |  | 5469 | 515 | -1793 | -1793 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1793 | 1 | AT: 332; AT: 140
20250708 | July | 1930 |  | 5470 | 515 |  | 5469 | 515 | -1793 | -1793 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1793 | 1 | AT: 332; AT: 140
20250708 | July | 2030 |  | 5470 | 515 |  | 5469 | 515 | -1793 | -1793 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1793 | 1 | AT: 332; AT: 140
20250708 | July | 2130 | 5838 |  |  | 5838 |  |  | -1823 | -1823 | -1822 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250708 | July | 2230 | 5838 |  |  | 5838 |  |  | -1823 | -1823 | -1822 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250708 | July | 2330 | 5238 |  |  | 5238 |  |  | -1217 | -1217 | -1217 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 312; AT: 160
20250709 | July | 0030 | 7638 |  |  | 7585 |  |  | -4577 | -4577 | -4534 | Critical Branch | Validation phase | 0 | 53 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7300; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 0130 | 7638 |  |  | 7585 |  |  | -4577 | -4577 | -4534 | Critical Branch | Validation phase | 0 | 53 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7300; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 0230 | 7638 |  |  | 7585 |  |  | -4577 | -4577 | -4534 | Critical Branch | Validation phase | 0 | 53 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7300; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 0330 | 7228 |  |  | 7224 |  |  | -2065 | -2065 | -2063 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250709 | July | 0430 | 7228 |  |  | 7224 |  |  | -2065 | -2065 | -2063 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250709 | July | 0530 | 7228 |  |  | 7224 |  |  | -2065 | -2065 | -2063 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250709 | July | 0630 | 7028 |  |  | 7024 |  |  | -1852 | -1852 | -1850 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250709 | July | 0730 | 6861 |  |  | 6861 |  |  | -1648 | -1648 | -1647 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 387; AT: 140
20250709 | July | 0830 | 6861 |  |  | 6861 |  |  | -1648 | -1648 | -1647 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 387; AT: 140
20250709 | July | 0930 | 7554 |  |  | 7538 |  |  | -1599 | -1599 | -1583 | Critical Branch | Validation phase | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 7223; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 1030 | 7554 |  |  | 7538 |  |  | -1599 | -1599 | -1583 | Critical Branch | Validation phase | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 7223; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 1130 | 7554 |  |  | 7538 |  |  | -1599 | -1599 | -1583 | Critical Branch | Validation phase | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 7223; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 1230 | 7880 |  |  | 7866 |  |  | -4338 | -4338 | -4319 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250709 | July | 1330 | 7880 |  |  | 7866 |  |  | -4338 | -4338 | -4319 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250709 | July | 1430 | 7880 |  |  | 7866 |  |  | -4338 | -4338 | -4319 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250709 | July | 1530 | 6956 |  |  | 6956 |  |  | -1720 | -1720 | -1720 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 140
20250709 | July | 1630 | 6956 |  |  | 6956 |  |  | -1720 | -1720 | -1720 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 140
20250709 | July | 1730 | 6956 |  |  | 6956 |  |  | -1720 | -1720 | -1720 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 140
20250709 | July | 1830 | 7215 |  |  | 7215 |  |  | -4588 | -4588 | -4588 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 398; AT: 140
20250709 | July | 1930 | 7215 |  |  | 7215 |  |  | -4588 | -4588 | -4588 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 398; AT: 140
20250709 | July | 2030 | 7215 |  |  | 7215 |  |  | -4588 | -4588 | -4588 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 398; AT: 140
20250709 | July | 2130 | 7054 |  |  | 7054 |  |  | -4188 | -4188 | -4188 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 390; AT: 140
20250709 | July | 2230 | 7054 |  |  | 7054 |  |  | -4188 | -4188 | -4188 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 390; AT: 140
20250709 | July | 2330 | 6454 |  |  | 6453 |  |  | -3585 | -3585 | -3585 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160
20250710 | July | 0030 | 8169 |  |  | 7913 |  |  | -4228 | -4228 | -3973 | Critical Branch | Validation phase | 0 | 256 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7741; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250710 | July | 0130 | 8169 |  |  | 7913 |  |  | -4228 | -4228 | -3973 | Critical Branch | Validation phase | 0 | 256 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7741; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250710 | July | 0230 | 8169 |  |  | 7913 |  |  | -4228 | -4228 | -3973 | Critical Branch | Validation phase | 0 | 256 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7741; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250710 | July | 0330 | 7766 |  |  | 7733 |  |  | -3723 | -3723 | -3684 | Critical Branch | Critical Branch | 0 | 33 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250710 | July | 0430 | 7766 |  |  | 7733 |  |  | -3723 | -3723 | -3684 | Critical Branch | Critical Branch | 0 | 33 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250710 | July | 0530 | 7766 |  |  | 7733 |  |  | -3723 | -3723 | -3684 | Critical Branch | Critical Branch | 0 | 33 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250710 | July | 0630 | 7566 |  |  | 7532 |  |  | -3517 | -3517 | -3477 | Critical Branch | Critical Branch | 0 | 34 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250710 | July | 0730 | 6976 |  |  | 6976 |  |  | -1915 | -1915 | -1915 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 393; AT: 140
20250710 | July | 0830 | 6976 |  |  | 6976 |  |  | -1915 | -1915 | -1915 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 393; AT: 140
20250710 | July | 0930 | 7243 |  |  | 7242 |  |  | -3426 | -3426 | -3425 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 406; AT: 140
20250710 | July | 1030 | 7243 |  |  | 7242 |  |  | -3426 | -3426 | -3425 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 406; AT: 140
20250710 | July | 1130 | 7243 |  |  | 7242 |  |  | -3426 | -3426 | -3425 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 406; AT: 140
20250710 | July | 1230 | 7834 |  |  | 7822 |  |  | -3300 | -3300 | -3293 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250710 | July | 1330 | 7834 |  |  | 7822 |  |  | -3300 | -3300 | -3293 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250710 | July | 1430 | 7834 |  |  | 7822 |  |  | -3300 | -3300 | -3293 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250710 | July | 1530 | 8128 |  |  | 7910 |  |  | 1562 | 168 | 1586 | Minimum Margin | TTC Validation phase - bilateral reduction | 1394 | 218 | NA | NA | NA | 3004 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250710 | July | 1630 | 7962 |  |  | 7813 |  |  | 1562 | 2 | 1691 | Minimum Margin | TTC Validation phase - bilateral reduction | 1560 | 149 | NA | NA | NA | 3380 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250710 | July | 1730 | 7960 |  |  | 7811 |  |  | 1562 | 0 | 1693 | Critical Branch | TTC Validation phase - bilateral reduction | 1562 | 149 | NA | NA | NA | 3386 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250710 | July | 1830 | 7399 |  |  | 7399 |  |  | -4791 | -4791 | -4791 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 407; AT: 140
20250710 | July | 1930 | 7399 |  |  | 7399 |  |  | -4791 | -4791 | -4791 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 407; AT: 140
20250710 | July | 2030 | 7399 |  |  | 7399 |  |  | -4791 | -4791 | -4791 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 407; AT: 140
20250710 | July | 2130 | 7777 |  |  | 7776 |  |  | -5208 | -5208 | -5207 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250710 | July | 2230 | 7777 |  |  | 7776 |  |  | -5208 | -5208 | -5207 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250710 | July | 2330 | 7177 |  |  | 7176 |  |  | -4606 | -4606 | -4605 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250711 | July | 0030 | 7724 |  |  | 7688 |  |  | -4672 | -4672 | -4649 | Critical Branch | Critical Branch | 0 | 36 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250711 | July | 0130 | 7724 |  |  | 7688 |  |  | -4672 | -4672 | -4649 | Critical Branch | Critical Branch | 0 | 36 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250711 | July | 0230 | 7724 |  |  | 7688 |  |  | -4672 | -4672 | -4649 | Critical Branch | Critical Branch | 0 | 36 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250711 | July | 0330 | 8023 |  |  | 7944 |  |  | -4460 | -4460 | -4402 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7747; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0430 | 8023 |  |  | 7944 |  |  | -4460 | -4460 | -4402 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7747; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0530 | 8023 |  |  | 7944 |  |  | -4460 | -4460 | -4402 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7747; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0630 | 7823 |  |  | 7743 |  |  | -4249 | -4249 | -4190 | Critical Branch | Validation phase | 0 | 80 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7547; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0730 | 6817 |  |  | 6817 |  |  | -4534 | -4534 | -4534 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 140
20250711 | July | 0830 | 6817 |  |  | 6817 |  |  | -4534 | -4534 | -4534 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 140
20250711 | July | 0930 | 7880 |  |  | 7108 |  |  | -3326 | -3326 | -2554 | Critical Branch | Validation phase | 0 | 772 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6858; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250711 | July | 1030 | 7880 |  |  | 7108 |  |  | -3326 | -3326 | -2554 | Critical Branch | Validation phase | 0 | 772 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6858; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250711 | July | 1130 | 7880 |  |  | 7108 |  |  | -3326 | -3326 | -2554 | Critical Branch | Validation phase | 0 | 772 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6858; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250711 | July | 1230 | 7827 |  |  | 7813 |  |  | -4228 | -4228 | -4219 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250711 | July | 1330 | 7827 |  |  | 7813 |  |  | -4228 | -4228 | -4219 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250711 | July | 1430 | 7827 |  |  | 7813 |  |  | -4228 | -4228 | -4219 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250711 | July | 1530 | 7518 |  |  | 7518 |  |  | -3592 | -3592 | -3592 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 140
20250711 | July | 1630 | 7518 |  |  | 7518 |  |  | -3592 | -3592 | -3592 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 140
20250711 | July | 1730 | 7518 |  |  | 7518 |  |  | -3592 | -3592 | -3592 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 140
20250711 | July | 1830 |  | 6047 | 562 |  | 6046 | 562 | -4196 | -4196 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4196 | 1 | AT: 353; AT: 140
20250711 | July | 1930 |  | 6047 | 562 |  | 6046 | 562 | -4196 | -4196 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4196 | 1 | AT: 353; AT: 140
20250711 | July | 2030 |  | 6047 | 562 |  | 6046 | 562 | -4196 | -4196 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4196 | 1 | AT: 353; AT: 140
20250711 | July | 2130 | 7035 |  |  | 7035 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 383; AT: 140
20250711 | July | 2230 | 7035 |  |  | 7035 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 383; AT: 140
20250711 | July | 2330 | 6435 |  |  | 6435 |  |  | -3889 | -3889 | -3889 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250712 | July | 0030 | 7639 |  |  | 7488 |  |  | -3394 | -3394 | -3250 | Critical Branch | Validation phase | 0 | 151 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7197; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250712 | July | 0130 | 7639 |  |  | 7488 |  |  | -3394 | -3394 | -3250 | Critical Branch | Validation phase | 0 | 151 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7197; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250712 | July | 0230 | 7639 |  |  | 7488 |  |  | -3394 | -3394 | -3250 | Critical Branch | Validation phase | 0 | 151 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7197; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250712 | July | 0330 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 0 | 191 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7361; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0430 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 0 | 191 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7361; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0530 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 0 | 191 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7361; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0630 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 0 | 191 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7361; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0730 | 7580 |  |  | 7537 |  |  | -3151 | -3151 | -3108 | Critical Branch | Validation phase | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 7222; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0830 | 7580 |  |  | 7537 |  |  | -3151 | -3151 | -3108 | Critical Branch | Validation phase | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 7222; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0930 | 7444 |  |  | 7302 |  |  | -2601 | -2601 | -2459 | Critical Branch | Validation phase | 0 | 142 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6987; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 1030 | 7444 |  |  | 7302 |  |  | -2601 | -2601 | -2459 | Critical Branch | Validation phase | 0 | 142 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6987; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 1130 | 7444 |  |  | 7302 |  |  | -2601 | -2601 | -2459 | Critical Branch | Validation phase | 0 | 142 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6987; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 1230 | 7775 |  |  | 7774 |  |  | -4106 | -4106 | -4104 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250712 | July | 1330 | 7775 |  |  | 7774 |  |  | -4106 | -4106 | -4104 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250712 | July | 1430 | 7775 |  |  | 7774 |  |  | -4106 | -4106 | -4104 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250712 | July | 1530 |  | 7190 | 672 |  | 7189 | 672 | -4598 | -4598 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4598 | 1 | AT: 425; AT: 139
20250712 | July | 1630 |  | 7190 | 672 |  | 7189 | 672 | -4598 | -4598 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4598 | 1 | AT: 425; AT: 139
20250712 | July | 1730 |  | 7190 | 672 |  | 7189 | 672 | -4598 | -4598 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4598 | 1 | AT: 425; AT: 139
20250712 | July | 1830 |  | 6657 | 637 |  | 6656 | 637 | -3472 | -3472 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3472 | 1 | AT: 396; AT: 140
20250712 | July | 1930 |  | 6657 | 637 |  | 6656 | 637 | -3472 | -3472 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3472 | 1 | AT: 396; AT: 140
20250712 | July | 2030 |  | 6657 | 637 |  | 6656 | 637 | -3472 | -3472 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3472 | 1 | AT: 396; AT: 140
20250712 | July | 2130 | 6889 |  |  | 6834 |  |  | -3205 | -3205 | -3150 | Critical Branch | Validation phase | 0 | 55 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6519; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 2230 | 6889 |  |  | 6834 |  |  | -3205 | -3205 | -3150 | Critical Branch | Validation phase | 0 | 55 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6519; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 2330 | 6289 |  |  | 6234 |  |  | -2601 | -2601 | -2546 | Critical Branch | Validation phase | 0 | 55 | NA | NA | NA | 0 | 1 | AT: 368; AT: 160; CH: 5924; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250713 | July | 0030 | 7590 |  |  | 7566 |  |  | -4280 | -4280 | -4265 | Critical Branch | Critical Branch | 0 | 24 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 0130 | 7590 |  |  | 7566 |  |  | -4280 | -4280 | -4265 | Critical Branch | Critical Branch | 0 | 24 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 0230 | 7590 |  |  | 7566 |  |  | -4280 | -4280 | -4265 | Critical Branch | Critical Branch | 0 | 24 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 0330 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250713 | July | 0430 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250713 | July | 0530 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250713 | July | 0630 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250713 | July | 0730 | 7681 |  |  | 7652 |  |  | -3219 | -3219 | -3201 | Critical Branch | Critical Branch | 0 | 29 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 0830 | 7681 |  |  | 7652 |  |  | -3219 | -3219 | -3201 | Critical Branch | Critical Branch | 0 | 29 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 0930 | 7324 |  |  | 7315 |  |  | -3939 | -3939 | -3928 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 1030 | 7324 |  |  | 7315 |  |  | -3939 | -3939 | -3928 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 1130 | 7324 |  |  | 7315 |  |  | -3939 | -3939 | -3928 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250713 | July | 1230 | 6359 |  |  | 6359 |  |  | -2851 | -2851 | -2851 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 372; AT: 160
20250713 | July | 1330 | 6359 |  |  | 6359 |  |  | -2851 | -2851 | -2851 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 372; AT: 160
20250713 | July | 1430 | 6359 |  |  | 6359 |  |  | -2851 | -2851 | -2851 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 372; AT: 160
20250713 | July | 1530 |  | 7851 | 883 |  | 7545 | 883 | -5681 | -5681 | 0 | Critical Branch | Critical Branch | 0 | NA | 306 | 0 | 306 | 5681 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250713 | July | 1630 |  | 7851 | 883 |  | 7779 | 883 | -5681 | -5681 | 0 | Critical Branch | Critical Branch | 0 | NA | 72 | 0 | 72 | 5681 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250713 | July | 1730 |  | 7851 | 883 |  | 7729 | 883 | -5681 | -5681 | 0 | Critical Branch | Critical Branch | 0 | NA | 122 | 0 | 122 | 5681 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250713 | July | 1830 |  | 6289 | 717 |  | 6288 | 717 | -4390 | -4390 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4390 | 1 | AT: 395; AT: 158
20250713 | July | 1930 |  | 6289 | 717 |  | 6288 | 717 | -4390 | -4390 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4390 | 1 | AT: 395; AT: 158
20250713 | July | 2030 |  | 6289 | 717 |  | 6288 | 717 | -4390 | -4390 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4390 | 1 | AT: 395; AT: 158
20250713 | July | 2130 | 6582 |  |  | 6582 |  |  | -4239 | -4239 | -4238 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 384; AT: 160
20250713 | July | 2230 | 6582 |  |  | 6582 |  |  | -4239 | -4239 | -4238 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 384; AT: 160
20250713 | July | 2330 | 6582 |  |  | 6582 |  |  | -4239 | -4239 | -4238 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 384; AT: 160
20250714 | July | 0030 | 6595 |  |  | 6595 |  |  | -3725 | -3725 | -3725 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 160
20250714 | July | 0130 | 6595 |  |  | 6595 |  |  | -3725 | -3725 | -3725 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 160
20250714 | July | 0230 | 6595 |  |  | 6595 |  |  | -3725 | -3725 | -3725 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 160
20250714 | July | 0330 | 7133 |  |  | 7133 |  |  | -4012 | -4012 | -4011 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250714 | July | 0430 | 7133 |  |  | 7133 |  |  | -4012 | -4012 | -4011 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250714 | July | 0530 | 7133 |  |  | 7133 |  |  | -4012 | -4012 | -4011 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250714 | July | 0630 | 6933 |  |  | 6933 |  |  | -3806 | -3806 | -3806 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250714 | July | 0730 | 7413 |  |  | 7395 |  |  | -2716 | -2716 | -2698 | Critical Branch | Validation phase | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140; CH: 7080; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250714 | July | 0830 | 7413 |  |  | 7395 |  |  | -2716 | -2716 | -2698 | Critical Branch | Validation phase | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140; CH: 7080; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250714 | July | 0930 | 7793 |  |  | 7593 |  |  | -3378 | -3378 | -3178 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7278; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250714 | July | 1030 | 7793 |  |  | 7593 |  |  | -3378 | -3378 | -3178 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7278; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250714 | July | 1130 | 7793 |  |  | 7593 |  |  | -3378 | -3378 | -3178 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7278; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250714 | July | 1230 | 7862 |  |  | 7849 |  |  | -1523 | -1523 | -1511 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250714 | July | 1330 | 7862 |  |  | 7849 |  |  | -1523 | -1523 | -1511 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250714 | July | 1430 | 7862 |  |  | 7849 |  |  | -1523 | -1523 | -1511 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250714 | July | 1530 | 7528 |  |  | 7528 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250714 | July | 1630 | 7528 |  |  | 7528 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250714 | July | 1730 | 7528 |  |  | 7528 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250714 | July | 1830 |  | 6278 | 579 |  | 6278 | 579 | -2699 | -2699 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2699 | 1 | AT: 376; AT: 140
20250714 | July | 1930 |  | 6278 | 579 |  | 6278 | 579 | -2699 | -2699 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2699 | 1 | AT: 376; AT: 140
20250714 | July | 2030 |  | 6278 | 579 |  | 6278 | 579 | -2699 | -2699 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2699 | 1 | AT: 376; AT: 140
20250714 | July | 2130 |  | 6568 | 620 |  | 6567 | 620 | -4766 | -4766 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4766 | 1 | AT: 391; AT: 140
20250714 | July | 2230 |  | 6568 | 620 |  | 6567 | 620 | -4766 | -4766 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4766 | 1 | AT: 391; AT: 140
20250714 | July | 2330 |  | 5988 | 645 |  | 5987 | 645 | -4138 | -4138 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4138 | 1 | AT: 378; AT: 160
20250715 | July | 0030 | 6542 |  |  | 6542 |  |  | -3554 | -3554 | -3554 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160
20250715 | July | 0130 | 6542 |  |  | 6542 |  |  | -3554 | -3554 | -3554 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160
20250715 | July | 0230 | 6542 |  |  | 6542 |  |  | -3554 | -3554 | -3554 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160
20250715 | July | 0330 | 7121 |  |  | 7121 |  |  | -3730 | -3730 | -3729 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250715 | July | 0430 | 7121 |  |  | 7121 |  |  | -3730 | -3730 | -3729 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250715 | July | 0530 | 7121 |  |  | 7121 |  |  | -3730 | -3730 | -3729 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250715 | July | 0630 | 6921 |  |  | 6921 |  |  | -3522 | -3522 | -3522 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 413; AT: 160
20250715 | July | 0730 | 6511 |  |  | 6510 |  |  | -3723 | -3723 | -3722 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140
20250715 | July | 0830 | 6511 |  |  | 6510 |  |  | -3723 | -3723 | -3722 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140
20250715 | July | 0930 | 7982 |  |  | 7937 |  |  | -4265 | -4265 | -4228 | Critical Branch | Validation phase | 0 | 45 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7708; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250715 | July | 1030 | 6782 |  |  | 6732 |  |  | -3003 | -3003 | -2964 | Critical Branch | Validation phase | 0 | 50 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6508; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250715 | July | 1130 | 6782 |  |  | 6732 |  |  | -3003 | -3003 | -2964 | Critical Branch | Validation phase | 0 | 50 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6508; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250715 | July | 1230 | 7501 |  |  | 7501 |  |  | -1022 | -1022 | -1022 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 419; AT: 140
20250715 | July | 1330 | 7501 |  |  | 7501 |  |  | -1022 | -1022 | -1022 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 419; AT: 140
20250715 | July | 1430 | 7501 |  |  | 7501 |  |  | -1022 | -1022 | -1022 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 419; AT: 140
20250715 | July | 1530 | 7326 |  |  | 7325 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 408; AT: 140
20250715 | July | 1630 | 7326 |  |  | 7325 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 408; AT: 140
20250715 | July | 1730 | 7326 |  |  | 7079 |  |  | -1169 | -1169 | -923 | Critical Branch | Critical Branch | 0 | 247 | NA | NA | NA | 0 | 1 | AT: 393; AT: 140
20250715 | July | 1830 | 5580 |  |  | 5579 |  |  | -2920 | -2920 | -2920 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 297; AT: 140
20250715 | July | 1930 | 5580 |  |  | 5579 |  |  | -2920 | -2920 | -2920 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 297; AT: 140
20250715 | July | 2030 | 5580 |  |  | 5579 |  |  | -2920 | -2920 | -2920 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 297; AT: 140
20250715 | July | 2130 | 6752 |  |  | 6752 |  |  | -4347 | -4347 | -4347 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 366; AT: 140
20250715 | July | 2230 | 6752 |  |  | 6752 |  |  | -4347 | -4347 | -4347 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 366; AT: 140
20250715 | July | 2330 | 6152 |  |  | 6151 |  |  | -3743 | -3743 | -3743 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 352; AT: 160
20250716 | July | 0030 | 6884 |  |  | 6508 |  |  | -3795 | -3795 | -3419 | Critical Branch | Validation phase | 0 | 376 | NA | NA | NA | 0 | 1 | AT: 398; AT: 160; CH: 6258; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0130 | 6884 |  |  | 6508 |  |  | -3795 | -3795 | -3419 | Critical Branch | Validation phase | 0 | 376 | NA | NA | NA | 0 | 1 | AT: 398; AT: 160; CH: 6258; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0230 | 6884 |  |  | 6508 |  |  | -3795 | -3795 | -3419 | Critical Branch | Validation phase | 0 | 376 | NA | NA | NA | 0 | 1 | AT: 398; AT: 160; CH: 6258; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0330 | 7208 |  |  | 6657 |  |  | -2501 | -2501 | -1950 | Critical Branch | Validation phase | 0 | 551 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6407; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0430 | 7208 |  |  | 6657 |  |  | -2501 | -2501 | -1950 | Critical Branch | Validation phase | 0 | 551 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6407; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0530 | 7208 |  |  | 6657 |  |  | -2501 | -2501 | -1950 | Critical Branch | Validation phase | 0 | 551 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6407; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0630 | 7008 |  |  | 6457 |  |  | -2289 | -2289 | -1738 | Critical Branch | Validation phase | 0 | 551 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6207; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0730 | 6512 |  |  | 6169 |  |  | -3992 | -3992 | -3649 | Critical Branch | Validation phase | 0 | 343 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 5919; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0830 | 6512 |  |  | 6169 |  |  | -3992 | -3992 | -3649 | Critical Branch | Validation phase | 0 | 343 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 5919; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0930 | 7921 |  |  | 7669 |  |  | -4356 | -4356 | -4111 | Critical Branch | Critical Branch | 0 | 252 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250716 | July | 1030 | 7921 |  |  | 7902 |  |  | -4356 | -4356 | -4344 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250716 | July | 1130 | 7921 |  |  | 7902 |  |  | -4356 | -4356 | -4344 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250716 | July | 1230 | 7666 |  |  | 7034 |  |  | -4005 | -4005 | -3373 | Critical Branch | Validation phase | 0 | 632 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6784; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250716 | July | 1330 | 7666 |  |  | 7034 |  |  | -4005 | -4005 | -3373 | Critical Branch | Validation phase | 0 | 632 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6784; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250716 | July | 1430 | 7666 |  |  | 7034 |  |  | -4005 | -4005 | -3373 | Critical Branch | Validation phase | 0 | 632 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6784; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250716 | July | 1530 | 7998 |  |  | 6818 |  |  | -1870 | -1870 | -690 | Critical Branch | Validation phase | 0 | 1180 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6568; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 1630 | 7998 |  |  | 6818 |  |  | -1870 | -1870 | -690 | Critical Branch | Validation phase | 0 | 1180 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6568; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 1730 | 7998 |  |  | 6818 |  |  | -1870 | -1870 | -690 | Critical Branch | Validation phase | 0 | 1180 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6568; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 1830 |  | 6153 | 568 |  | 6153 | 568 | -4313 | -4313 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4313 | 1 | AT: 360; AT: 140
20250716 | July | 1930 |  | 6153 | 568 |  | 6153 | 568 | -4313 | -4313 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4313 | 1 | AT: 360; AT: 140
20250716 | July | 2030 |  | 6153 | 568 |  | 6153 | 568 | -4313 | -4313 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4313 | 1 | AT: 360; AT: 140
20250716 | July | 2130 | 7288 |  |  | 6754 |  |  | -4704 | -4704 | -4170 | Critical Branch | Validation phase | 0 | 534 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6504; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 2230 | 7288 |  |  | 6754 |  |  | -4704 | -4704 | -4170 | Critical Branch | Validation phase | 0 | 534 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6504; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 2330 | 6688 |  |  | 6154 |  |  | -4100 | -4100 | -3566 | Critical Branch | Validation phase | 0 | 534 | NA | NA | NA | 0 | 1 | AT: 386; AT: 160; CH: 5904; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250717 | July | 0030 | 7331 |  |  | 7108 |  |  | -4073 | -4073 | -3850 | Critical Branch | Validation phase | 0 | 223 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6858; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0130 | 7331 |  |  | 7108 |  |  | -4073 | -4073 | -3850 | Critical Branch | Validation phase | 0 | 223 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6858; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0230 | 7331 |  |  | 7108 |  |  | -4073 | -4073 | -3850 | Critical Branch | Validation phase | 0 | 223 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6858; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0330 | 7474 |  |  | 7263 |  |  | -4139 | -4139 | -3930 | Critical Branch | Validation phase | 0 | 211 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7020; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0430 | 7474 |  |  | 7263 |  |  | -4139 | -4139 | -3930 | Critical Branch | Validation phase | 0 | 211 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7020; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0530 | 7474 |  |  | 7263 |  |  | -4139 | -4139 | -3930 | Critical Branch | Validation phase | 0 | 211 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7020; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0630 | 7274 |  |  | 7062 |  |  | -3934 | -3934 | -3725 | Critical Branch | Validation phase | 0 | 212 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6820; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0730 | 7037 |  |  | 6864 |  |  | -4289 | -4289 | -4116 | Critical Branch | Validation phase | 0 | 173 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 6614; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0830 | 7037 |  |  | 6864 |  |  | -4289 | -4289 | -4116 | Critical Branch | Validation phase | 0 | 173 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 6614; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0930 | 7013 |  |  | 6818 |  |  | -3046 | -3046 | -2851 | Critical Branch | Validation phase | 0 | 195 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140; CH: 6568; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1030 | 7013 |  |  | 6818 |  |  | -3046 | -3046 | -2851 | Critical Branch | Validation phase | 0 | 195 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140; CH: 6568; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1130 | 7013 |  |  | 6818 |  |  | -3046 | -3046 | -2851 | Critical Branch | Validation phase | 0 | 195 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140; CH: 6568; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1230 | 7368 |  |  | 7084 |  |  | -3974 | -3974 | -3690 | Critical Branch | Validation phase | 0 | 284 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; CH: 6834; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1330 | 7368 |  |  | 7084 |  |  | -3974 | -3974 | -3690 | Critical Branch | Validation phase | 0 | 284 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; CH: 6834; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1430 | 7368 |  |  | 7084 |  |  | -3974 | -3974 | -3690 | Critical Branch | Validation phase | 0 | 284 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; CH: 6834; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1530 | 7282 |  |  | 7059 |  |  | -3557 | -3557 | -3334 | Critical Branch | Validation phase | 0 | 223 | NA | NA | NA | 0 | 1 | AT: 206; AT: 70; CH: 6809; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1630 | 7497 |  |  | 7079 |  |  | -3733 | -3733 | -3389 | Critical Branch | Validation phase | 0 | 418 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7024; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1730 | 7497 |  |  | 7274 |  |  | -3733 | -3733 | -3510 | Critical Branch | Validation phase | 0 | 223 | NA | NA | NA | 0 | 1 | AT: 418; AT: 140; CH: 7024; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1830 |  | 6845 | 666 |  | 6844 | 666 | -5120 | -5120 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5120 | 1 | AT: 403; AT: 139
20250717 | July | 1930 |  | 6845 | 666 |  | 6844 | 666 | -5120 | -5120 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5120 | 1 | AT: 403; AT: 139
20250717 | July | 2030 |  | 6845 | 666 |  | 6844 | 666 | -5120 | -5120 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5120 | 1 | AT: 403; AT: 139
20250717 | July | 2130 | 7162 |  |  | 6878 |  |  | -4832 | -4832 | -4548 | Critical Branch | Validation phase | 0 | 284 | NA | NA | NA | 0 | 1 | AT: 390; AT: 140; CH: 6628; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 2230 | 7162 |  |  | 6878 |  |  | -4832 | -4832 | -4548 | Critical Branch | Validation phase | 0 | 284 | NA | NA | NA | 0 | 1 | AT: 390; AT: 140; CH: 6628; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 2330 | 6562 |  |  | 6278 |  |  | -4228 | -4228 | -3944 | Critical Branch | Validation phase | 0 | 284 | NA | NA | NA | 0 | 1 | AT: 378; AT: 160; CH: 6028; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250718 | July | 0030 | 7182 |  |  | 6847 |  |  | -4008 | -4008 | -3676 | Critical Branch | Validation phase | 0 | 335 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6923; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0130 | 7182 |  |  | 6847 |  |  | -4008 | -4008 | -3676 | Critical Branch | Validation phase | 0 | 335 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6923; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0230 | 7182 |  |  | 6847 |  |  | -4008 | -4008 | -3676 | Critical Branch | Validation phase | 0 | 335 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6923; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0330 | 7248 |  |  | 6891 |  |  | -4147 | -4147 | -3767 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0430 | 7248 |  |  | 6891 |  |  | -4147 | -4147 | -3767 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0530 | 7248 |  |  | 6891 |  |  | -4147 | -4147 | -3767 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0630 | 7048 |  |  | 6689 |  |  | -3942 | -3942 | -3560 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 359 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0730 | 6742 |  |  | 6505 |  |  | -4349 | -4349 | -4110 | Critical Branch | Validation phase | 0 | 237 | NA | NA | NA | 0 | 1 | AT: 373; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0830 | 6742 |  |  | 6505 |  |  | -4349 | -4349 | -4110 | Critical Branch | Validation phase | 0 | 237 | NA | NA | NA | 0 | 1 | AT: 373; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0930 | 7600 |  |  | 7056 |  |  | -2837 | -2837 | -2294 | Critical Branch | Validation phase | 0 | 544 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1030 | 7600 |  |  | 7056 |  |  | -2837 | -2837 | -2294 | Critical Branch | Validation phase | 0 | 544 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1130 | 7600 |  |  | 7056 |  |  | -2837 | -2837 | -2294 | Critical Branch | Validation phase | 0 | 544 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1230 | 8091 |  |  | 7342 |  |  | -1211 | -1211 | -566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 749 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1330 | 8091 |  |  | 7342 |  |  | -1211 | -1211 | -566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 749 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1430 | 8091 |  |  | 7342 |  |  | -1211 | -1211 | -566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 749 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1530 | 7344 |  |  | 6891 |  |  | -2847 | -2847 | -2376 | Critical Branch | Validation phase | 0 | 453 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1630 | 7344 |  |  | 6891 |  |  | -2847 | -2847 | -2376 | Critical Branch | Validation phase | 0 | 453 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1730 | 7344 |  |  | 6891 |  |  | -2847 | -2847 | -2376 | Critical Branch | Validation phase | 0 | 453 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1830 |  | 6787 | 671 |  | 6391 | 671 | -5225 | -5225 | 0 | Critical Branch | Validation phase | 0 | NA | 396 | 0 | 396 | 5225 | 1 | AT: 400; AT: 139; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1930 |  | 6787 | 671 |  | 6391 | 671 | -5225 | -5225 | 0 | Critical Branch | Validation phase | 0 | NA | 396 | 0 | 396 | 5225 | 1 | AT: 400; AT: 139; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2030 |  | 6787 | 671 |  | 6391 | 671 | -5225 | -5225 | 0 | Critical Branch | Validation phase | 0 | NA | 396 | 0 | 396 | 5225 | 1 | AT: 400; AT: 139; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2130 | 6986 |  |  | 6710 |  |  | -4598 | -4598 | -4307 | Critical Branch | Validation phase | 0 | 276 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2230 | 6986 |  |  | 6710 |  |  | -4598 | -4598 | -4307 | Critical Branch | Validation phase | 0 | 276 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; FR: 2000; FR: Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2330 | 6386 |  |  | 6386 |  |  | -3994 | -3994 | -3994 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 367; AT: 160
20250719 | July | 0030 | 6799 |  |  | 6789 |  |  | -3785 | -3785 | -3775 | Critical Branch | Validation phase | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 393; AT: 160; CH: 6539; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 0130 | 6799 |  |  | 6789 |  |  | -3785 | -3785 | -3775 | Critical Branch | Validation phase | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 393; AT: 160; CH: 6539; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 0230 | 6799 |  |  | 6789 |  |  | -3785 | -3785 | -3775 | Critical Branch | Validation phase | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 393; AT: 160; CH: 6539; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 0330 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 160
20250719 | July | 0430 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 160
20250719 | July | 0530 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 160
20250719 | July | 0630 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 160
20250719 | July | 0730 | 7138 |  |  | 7138 |  |  | -2739 | -2739 | -2739 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140
20250719 | July | 0830 | 7138 |  |  | 7138 |  |  | -2739 | -2739 | -2739 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140
20250719 | July | 0930 | 7614 |  |  | 7614 |  |  | -4375 | -4375 | -4375 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 140
20250719 | July | 1030 | 7614 |  |  | 7614 |  |  | -4375 | -4375 | -4375 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 140
20250719 | July | 1130 | 7614 |  |  | 7614 |  |  | -4375 | -4375 | -4375 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 140
20250719 | July | 1230 | 8165 |  |  | 7837 |  |  | -1629 | -1629 | -1301 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7592; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250719 | July | 1330 | 8165 |  |  | 7837 |  |  | -1629 | -1629 | -1301 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7592; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250719 | July | 1430 | 8165 |  |  | 7837 |  |  | -1629 | -1629 | -1301 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7592; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250719 | July | 1530 | 7287 |  |  | 7212 |  |  | -4057 | -4057 | -3982 | Critical Branch | Validation phase | 0 | 75 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6962; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 1630 | 7287 |  |  | 7212 |  |  | -4057 | -4057 | -3982 | Critical Branch | Validation phase | 0 | 75 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6962; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 1730 | 7287 |  |  | 7212 |  |  | -4057 | -4057 | -3982 | Critical Branch | Validation phase | 0 | 75 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6962; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 1830 | 5814 |  |  | 5813 |  |  | -3755 | -3755 | -3755 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 311; AT: 140
20250719 | July | 1930 | 5814 |  |  | 5813 |  |  | -3755 | -3755 | -3755 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 311; AT: 140
20250719 | July | 2030 | 5814 |  |  | 5813 |  |  | -3755 | -3755 | -3755 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 311; AT: 140
20250719 | July | 2130 | 5788 |  |  | 5787 |  |  | -3078 | -3078 | -3077 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 309; AT: 140
20250719 | July | 2230 | 5788 |  |  | 5787 |  |  | -3078 | -3078 | -3077 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 309; AT: 140
20250719 | July | 2330 | 5188 |  |  | 5187 |  |  | -2473 | -2473 | -2473 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 292; AT: 160
20250720 | July | 0030 | 5889 |  |  | 5815 |  |  | -1196 | -1196 | -1122 | Critical Branch | Validation phase | 0 | 74 | NA | NA | NA | 0 | 1 | AT: 336; AT: 160; CH: 5565; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0130 | 5889 |  |  | 5815 |  |  | -1196 | -1196 | -1122 | Critical Branch | Validation phase | 0 | 74 | NA | NA | NA | 0 | 1 | AT: 336; AT: 160; CH: 5565; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0230 | 5889 |  |  | 5815 |  |  | -1196 | -1196 | -1122 | Critical Branch | Validation phase | 0 | 74 | NA | NA | NA | 0 | 1 | AT: 336; AT: 160; CH: 5565; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0330 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 0 | 64 | NA | NA | NA | 0 | 1 | AT: 397; AT: 160; CH: 6562; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0430 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 0 | 64 | NA | NA | NA | 0 | 1 | AT: 397; AT: 160; CH: 6562; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0530 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 0 | 64 | NA | NA | NA | 0 | 1 | AT: 397; AT: 160; CH: 6562; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0630 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 0 | 64 | NA | NA | NA | 0 | 1 | AT: 397; AT: 160; CH: 6562; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0730 | 7299 |  |  | 7290 |  |  | -3598 | -3598 | -3592 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 0830 | 7299 |  |  | 7290 |  |  | -3598 | -3598 | -3592 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 0930 | 7747 |  |  | 7710 |  |  | -4810 | -4810 | -4785 | Critical Branch | Critical Branch | 0 | 37 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 1030 | 7747 |  |  | 7710 |  |  | -4810 | -4810 | -4785 | Critical Branch | Critical Branch | 0 | 37 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 1130 | 7747 |  |  | 7710 |  |  | -4810 | -4810 | -4785 | Critical Branch | Critical Branch | 0 | 37 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 1230 | 7358 |  |  | 7345 |  |  | -3914 | -3914 | -3898 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 1330 | 7358 |  |  | 7345 |  |  | -3914 | -3914 | -3898 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 1430 | 7358 |  |  | 7345 |  |  | -3914 | -3914 | -3898 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250720 | July | 1530 | 7088 |  |  | 7088 |  |  | -3586 | -3586 | -3585 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250720 | July | 1630 | 7088 |  |  | 7088 |  |  | -3586 | -3586 | -3585 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250720 | July | 1730 | 7088 |  |  | 7088 |  |  | -3586 | -3586 | -3585 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250720 | July | 1830 |  | 5656 | 592 |  | 5656 | 592 | -4133 | -4133 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4133 | 1 | AT: 350; AT: 160
20250720 | July | 1930 |  | 5656 | 592 |  | 5656 | 592 | -4133 | -4133 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4133 | 1 | AT: 350; AT: 160
20250720 | July | 2030 |  | 5656 | 592 |  | 5656 | 592 | -4133 | -4133 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4133 | 1 | AT: 350; AT: 160
20250720 | July | 2130 | 5812 |  |  | 5811 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 331; AT: 160
20250720 | July | 2230 | 5812 |  |  | 5811 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 331; AT: 160
20250720 | July | 2330 | 5812 |  |  | 5811 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 331; AT: 160
20250721 | July | 0030 | 7122 |  |  | 7099 |  |  | -3783 | -3783 | -3760 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | CH: 6849; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0130 | 7122 |  |  | 7099 |  |  | -3796 | -3796 | -3773 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | CH: 6849; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0230 | 7122 |  |  | 7099 |  |  | -3796 | -3796 | -3773 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | CH: 6849; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0330 | 6895 |  |  | 6865 |  |  | -3244 | -3244 | -3214 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | CH: 6615; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0430 | 6895 |  |  | 6865 |  |  | -3244 | -3244 | -3214 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | CH: 6615; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0530 | 6895 |  |  | 6865 |  |  | -3244 | -3244 | -3214 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | CH: 6615; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0630 | 6695 |  |  | 6665 |  |  | -3032 | -3032 | -3002 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | CH: 6420; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0730 | 7389 |  |  | 7389 |  |  | -4621 | -4621 | -4621 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 0830 | 7389 |  |  | 7389 |  |  | -4621 | -4621 | -4621 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 0930 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1030 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1130 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1230 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1330 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1430 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1530 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1630 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1730 | 7600 |  |  | 7600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1830 | 6597 |  |  | 6597 |  |  | -2620 | -2620 | -2620 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 1930 | 6597 |  |  | 6597 |  |  | -2620 | -2620 | -2620 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 2030 | 6597 |  |  | 6597 |  |  | -2620 | -2620 | -2620 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 2130 | 6590 |  |  | 6590 |  |  | -4275 | -4275 | -4275 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 2230 | 6590 |  |  | 6590 |  |  | -4275 | -4275 | -4275 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250721 | July | 2330 | 5990 |  |  | 5990 |  |  | -3668 | -3668 | -3668 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250722 | July | 0030 | 7207 |  |  | 7150 |  |  | -3597 | -3597 | 0 | Critical Branch | Critical Branch | 0 | 57 | NA | NA | NA | 3597 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0130 | 7207 |  |  | 7150 |  |  | -3597 | -3597 | 0 | Critical Branch | Critical Branch | 0 | 57 | NA | NA | NA | 3597 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0230 | 7207 |  |  | 7150 |  |  | -3597 | -3597 | 0 | Critical Branch | Critical Branch | 0 | 57 | NA | NA | NA | 3597 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0330 | 7282 |  |  | 7150 |  |  | -3943 | -3943 | 0 | Critical Branch | Critical Branch | 0 | 132 | NA | NA | NA | 3943 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0430 | 7282 |  |  | 7150 |  |  | -3943 | -3943 | 0 | Critical Branch | Critical Branch | 0 | 132 | NA | NA | NA | 3943 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0530 | 7282 |  |  | 7150 |  |  | -3943 | -3943 | 0 | Critical Branch | Critical Branch | 0 | 132 | NA | NA | NA | 3943 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0630 | 7082 |  |  | 6950 |  |  | -3742 | -3742 | 0 | Critical Branch | Critical Branch | 0 | 132 | NA | NA | NA | 3742 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250722 | July | 0730 | 6566 |  |  | 7000 |  |  | -3591 | -3591 | 0 | Critical Branch | Critical Branch | 0 | -434 | NA | NA | NA | 3591 | 1 | AT: 363; AT: 140
20250722 | July | 0830 | 6566 |  |  | 5500 |  |  | -3591 | -3591 | 0 | Critical Branch | Critical Branch | 0 | 1066 | NA | NA | NA | 3591 | 1 | AT: 363; AT: 140
20250722 | July | 0930 | 7275 |  |  | 4000 |  |  | -2605 | -2605 | 0 | Critical Branch | Validation phase | 0 | 3275 | NA | NA | NA | 2605 | 1 | AT: 405; AT: 140
20250722 | July | 1030 | 7275 |  |  | 4000 |  |  | -2605 | -2605 | 0 | Critical Branch | Validation phase | 0 | 3275 | NA | NA | NA | 2605 | 1 | AT: 405; AT: 140
20250722 | July | 1130 | 7275 |  |  | 4000 |  |  | -2605 | -2605 | 0 | Critical Branch | Validation phase | 0 | 3275 | NA | NA | NA | 2605 | 1 | AT: 405; AT: 140
20250722 | July | 1230 | 8014 |  |  | 4000 |  |  | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 4014 | NA | NA | NA | 997 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250722 | July | 1330 | 8014 |  |  | 5500 |  |  | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2514 | NA | NA | NA | 997 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250722 | July | 1430 | 8014 |  |  | 7000 |  |  | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1014 | NA | NA | NA | 997 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250722 | July | 1530 | 7946 |  |  | 7600 |  |  | -3787 | -3787 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 346 | NA | NA | NA | 3787 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250722 | July | 1630 | 7946 |  |  | 7600 |  |  | -3787 | -3787 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 346 | NA | NA | NA | 3787 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250722 | July | 1730 | 7946 |  |  | 7600 |  |  | -3787 | -3787 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 346 | NA | NA | NA | 3787 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2544; FR: Planned outage Venaus Villarodin 400kV
20250722 | July | 1830 |  | 7054 | 654 | 7742 |  |  | -4795 | -4795 | 0 | Critical Branch | Critical Branch | 0 | NA | NA | NA | NA | 4795 | 1 | AT: 417; AT: 140
20250722 | July | 1930 |  | 7054 | 654 | 7742 |  |  | -4795 | -4795 | 0 | Critical Branch | Critical Branch | 0 | NA | NA | NA | NA | 4795 | 1 | AT: 417; AT: 140
20250722 | July | 2030 |  | 7054 | 654 | 7742 |  |  | -4795 | -4795 | 0 | Critical Branch | Critical Branch | 0 | NA | NA | NA | NA | 4795 | 1 | AT: 417; AT: 140
20250722 | July | 2130 | 7088 |  |  | 7711 |  |  | -4192 | -4192 | 0 | Critical Branch | Critical Branch | 0 | -623 | NA | NA | NA | 4192 | 1 | AT: 386; AT: 140
20250722 | July | 2230 | 7088 |  |  | 7711 |  |  | -4192 | -4192 | 0 | Critical Branch | Critical Branch | 0 | -623 | NA | NA | NA | 4192 | 1 | AT: 386; AT: 140
20250722 | July | 2330 | 6488 |  |  | 7108 |  |  | -3588 | -3588 | 0 | Critical Branch | Critical Branch | 0 | -620 | NA | NA | NA | 3588 | 1 | AT: 373; AT: 160
20250723 | July | 0030 | 7197 |  |  | 7076 |  |  | -2764 | -2764 | -2643 | Critical Branch | Validation phase | 0 | 121 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6826; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0130 | 7197 |  |  | 7076 |  |  | -2764 | -2764 | -2643 | Critical Branch | Validation phase | 0 | 121 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6826; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0230 | 7197 |  |  | 7076 |  |  | -2764 | -2764 | -2643 | Critical Branch | Validation phase | 0 | 121 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6826; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0330 | 6521 |  |  | 6429 |  |  | -2871 | -2871 | -2779 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 375; AT: 160; CH: 6179; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0430 | 6521 |  |  | 6429 |  |  | -2871 | -2871 | -2779 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 375; AT: 160; CH: 6179; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0530 | 6521 |  |  | 6429 |  |  | -2871 | -2871 | -2779 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 375; AT: 160; CH: 6179; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0630 | 6321 |  |  | 6229 |  |  | -2663 | -2663 | -2571 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160; CH: 5979; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0730 | 6679 |  |  | 6678 |  |  | -3571 | -3571 | -3570 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140
20250723 | July | 0830 | 6679 |  |  | 6678 |  |  | -3571 | -3571 | -3570 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140
20250723 | July | 0930 | 7682 |  |  | 7637 |  |  | -4255 | -4255 | -4210 | Critical Branch | Validation phase | 0 | 45 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7389; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 1030 | 7682 |  |  | 7637 |  |  | -4255 | -4255 | -4210 | Critical Branch | Validation phase | 0 | 45 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7389; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 1130 | 7682 |  |  | 7637 |  |  | -4255 | -4255 | -4210 | Critical Branch | Validation phase | 0 | 45 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7389; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 1230 | 7771 |  |  | 7761 |  |  | -1126 | -1126 | -1116 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250723 | July | 1330 | 7771 |  |  | 7761 |  |  | -1126 | -1126 | -1116 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250723 | July | 1430 | 7771 |  |  | 7761 |  |  | -1126 | -1126 | -1116 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250723 | July | 1530 |  | 7037 | 718 |  | 7036 | 718 | -476 | -476 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 476 | 1 | AT: 425; AT: 137
20250723 | July | 1630 |  | 8341 | 718 |  | 8340 | 718 | -1633 | -1633 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1633 | 1 | AT: 425; AT: 137
20250723 | July | 1730 |  | 8341 | 718 |  | 8340 | 718 | -1633 | -1633 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1633 | 1 | AT: 425; AT: 137
20250723 | July | 1830 |  | 8330 | 649 |  | 7928 | 618 | -5621 | -5621 | 0 | Critical Branch | Validation phase | 0 | NA | 402 | 31 | 433 | 5621 | 1 | AT: 416; AT: 140; CH: 8216; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 1930 |  | 8330 | 649 |  | 7928 | 519 | -5621 | -5621 | 0 | Critical Branch | Validation phase | 0 | NA | 402 | 130 | 532 | 5621 | 1 | AT: 416; AT: 140; CH: 8216; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES; IT: 488; IT: Forecasted Security Violations
20250723 | July | 2030 |  | 8330 | 649 |  | 7928 | 519 | -5621 | -5621 | 0 | Critical Branch | Validation phase | 0 | NA | 402 | 130 | 532 | 5621 | 1 | AT: 416; AT: 140; CH: 8216; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES; IT: 488; IT: Forecasted Security Violations
20250723 | July | 2130 |  | 8455 | 663 |  | 7894 | 519 | -5774 | -5774 | 0 | Critical Branch | Validation phase | 0 | NA | 561 | 144 | 705 | 5774 | 1 | AT: 423; AT: 139; CH: 8190; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES; IT: 488; IT: Forecasted Security Violations
20250723 | July | 2230 |  | 8455 | 663 |  | 7894 | 620 | -5774 | -5774 | 0 | Critical Branch | Validation phase | 0 | NA | 561 | 43 | 604 | 5774 | 1 | AT: 423; AT: 139; CH: 8190; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 2330 |  | 7875 | 688 |  | 7334 | 646 | -5141 | -5141 | 0 | Critical Branch | Validation phase | 0 | NA | 541 | 42 | 583 | 5141 | 1 | AT: 412; AT: 159; CH: 7590; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250724 | July | 0030 | 8931 |  |  | 8582 |  |  | -3264 | -3264 | -2918 | Critical Branch | Validation phase | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8339; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0130 | 8931 |  |  | 8582 |  |  | -3264 | -3264 | -2918 | Critical Branch | Validation phase | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8339; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0230 | 8931 |  |  | 8582 |  |  | -3264 | -3264 | -2918 | Critical Branch | Validation phase | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8339; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0330 | 8623 |  |  | 8210 |  |  | -4205 | -4205 | -3792 | Critical Branch | Validation phase | 0 | 413 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7960; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0430 | 8623 |  |  | 8210 |  |  | -4205 | -4205 | -3792 | Critical Branch | Validation phase | 0 | 413 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7960; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0530 | 8623 |  |  | 8210 |  |  | -4205 | -4205 | -3792 | Critical Branch | Validation phase | 0 | 413 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7960; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0630 | 8423 |  |  | 8010 |  |  | -3994 | -3994 | -3581 | Critical Branch | Validation phase | 0 | 413 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7760; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0730 | 8209 |  |  | 8209 |  |  | -4914 | -4914 | -4914 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 390; AT: 140
20250724 | July | 0830 | 8209 |  |  | 8209 |  |  | -4914 | -4914 | -4914 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 390; AT: 140
20250724 | July | 0930 | 8513 |  |  | 8513 |  |  | 2489 | 0 | 2489 | Critical Branch | Critical Branch | 2489 | 0 | NA | NA | NA | 2489 | 1 | AT: 405; AT: 140
20250724 | July | 1030 | 8513 |  |  | 8513 |  |  | 2489 | 0 | 2489 | Critical Branch | Critical Branch | 2489 | 0 | NA | NA | NA | 2489 | 1 | AT: 405; AT: 140
20250724 | July | 1130 | 8725 |  |  | 8698 |  |  | 2489 | 212 | 2302 | Minimum Margin | Minimum Margin | 2277 | 27 | NA | NA | NA | 4392 | 1 | AT: 414; AT: 140
20250724 | July | 1230 | 7199 |  |  | 7198 |  |  | 2962 | 58 | 2904 | Minimum Margin | Minimum Margin | 2904 | 1 | NA | NA | NA | 5750 | 1 | AT: 338; AT: 140
20250724 | July | 1330 | 7199 |  |  | 7198 |  |  | 2962 | 58 | 2904 | Minimum Margin | Minimum Margin | 2904 | 1 | NA | NA | NA | 5750 | 1 | AT: 338; AT: 140
20250724 | July | 1430 | 7199 |  |  | 7198 |  |  | 2962 | 58 | 2904 | Minimum Margin | Minimum Margin | 2904 | 1 | NA | NA | NA | 5750 | 1 | AT: 338; AT: 140
20250724 | July | 1530 | 9073 |  |  | 8439 |  |  | -4739 | -4739 | -4105 | Critical Branch | Validation phase | 0 | 634 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 8189; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250724 | July | 1630 | 9073 |  |  | 8439 |  |  | -4739 | -4739 | -4105 | Critical Branch | Validation phase | 0 | 634 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8189; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250724 | July | 1730 | 9073 |  |  | 8439 |  |  | -4739 | -4739 | -4105 | Critical Branch | Validation phase | 0 | 634 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8189; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250724 | July | 1830 | 8267 |  |  | 8267 |  |  | -5259 | -5259 | -5259 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140
20250724 | July | 1930 | 8267 |  |  | 8267 |  |  | -5259 | -5259 | -5259 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140; IT: 578; IT: Forecasted Security Violations
20250724 | July | 2030 | 8267 |  |  | 8267 |  |  | -5259 | -5259 | -5259 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140; IT: 578; IT: Forecasted Security Violations
20250724 | July | 2130 | 8499 |  |  | 8498 |  |  | -5401 | -5401 | -5401 | Critical Branch | Validation phase | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; IT: 578; IT: Forecasted Security Violations
20250724 | July | 2230 | 8499 |  |  | 8498 |  |  | -5401 | -5401 | -5401 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140
20250724 | July | 2330 | 7899 |  |  | 7899 |  |  | -4796 | -4796 | -4796 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 386; AT: 160
20250725 | July | 0030 | 8891 |  |  | 8868 |  |  | -3639 | -3639 | -3625 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250725 | July | 0130 | 8891 |  |  | 8868 |  |  | -3639 | -3639 | -3625 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250725 | July | 0230 | 8891 |  |  | 8868 |  |  | -3639 | -3639 | -3625 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250725 | July | 0330 | 9126 |  |  | 8957 |  |  | -5690 | -5690 | -5532 | Critical Branch | Validation phase | 0 | 169 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8735; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0430 | 9126 |  |  | 8957 |  |  | -5690 | -5690 | -5532 | Critical Branch | Validation phase | 0 | 169 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8735; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0530 | 9126 |  |  | 8957 |  |  | -5690 | -5690 | -5532 | Critical Branch | Validation phase | 0 | 169 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8735; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0630 | 8926 |  |  | 8756 |  |  | -5483 | -5483 | -5324 | Critical Branch | Validation phase | 0 | 170 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8535; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0730 | 8314 |  |  | 8314 |  |  | -5245 | -5245 | -5244 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 140
20250725 | July | 0830 | 8314 |  |  | 8314 |  |  | -5245 | -5245 | -5244 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 140
20250725 | July | 0930 | 9099 |  |  | 9030 |  |  | -5361 | -5361 | -5291 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8787; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250725 | July | 1030 | 9099 |  |  | 9030 |  |  | -5361 | -5361 | -5291 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8787; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250725 | July | 1130 | 9099 |  |  | 7750 |  |  | -5361 | -5361 | -4005 | Critical Branch | Validation phase | 0 | 1349 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140; CH: 8787; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250725 | July | 1230 | 6790 |  |  | 6250 |  |  | 4626 | 60 | 5106 | Minimum Margin | Validation phase | 4566 | 540 | NA | NA | NA | 10152 | 1 | AT: 318; AT: 140; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250725 | July | 1330 | 6790 |  |  | 6250 |  |  | 4626 | 60 | 5106 | Minimum Margin | Validation phase | 4566 | 540 | NA | NA | NA | 10152 | 1 | AT: 318; AT: 140; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250725 | July | 1430 | 6790 |  |  | 6250 |  |  | 4626 | 60 | 5106 | Minimum Margin | Validation phase | 4566 | 540 | NA | NA | NA | 10152 | 1 | AT: 318; AT: 140; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250725 | July | 1530 | 7975 |  |  | 7750 |  |  | 4168 | 87 | 4306 | Minimum Margin | Minimum Margin | 4081 | 225 | NA | NA | NA | 8525 | 1 | AT: 378; AT: 140
20250725 | July | 1630 | 7975 |  |  | 7975 |  |  | 4168 | 87 | 4081 | Minimum Margin | Minimum Margin | 4081 | 0 | NA | NA | NA | 8075 | 1 | AT: 378; AT: 140
20250725 | July | 1730 | 7975 |  |  | 7975 |  |  | 4168 | 87 | 4081 | Minimum Margin | Minimum Margin | 4081 | 0 | NA | NA | NA | 8075 | 1 | AT: 378; AT: 140
20250725 | July | 1830 |  | 7703 | 595 |  | 7702 | 595 | -5287 | -5287 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5287 | 1 | AT: 383; AT: 140
20250725 | July | 1930 |  | 7703 | 595 |  | 7702 | 548 | -5287 | -5287 | 0 | Critical Branch | Validation phase | 0 | NA | 1 | 47 | 48 | 5287 | 1 | AT: 383; AT: 140; IT: 517; IT: Forecasted Security Violations
20250725 | July | 2030 |  | 7703 | 595 |  | 7702 | 548 | -5287 | -5287 | 0 | Critical Branch | Validation phase | 0 | NA | 1 | 47 | 48 | 5287 | 1 | AT: 383; AT: 140; IT: 517; IT: Forecasted Security Violations
20250725 | July | 2130 |  | 8141 | 629 |  | 8140 | 548 | -5781 | -5781 | 0 | Critical Branch | Validation phase | 0 | NA | 1 | 81 | 82 | 5781 | 1 | AT: 406; AT: 140; IT: 517; IT: Forecasted Security Violations
20250725 | July | 2230 |  | 8141 | 629 |  | 8140 | 629 | -5781 | -5781 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5781 | 1 | AT: 406; AT: 140
20250725 | July | 2330 |  | 7581 | 654 |  | 7580 | 654 | -5159 | -5159 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5159 | 1 | AT: 395; AT: 160
20250726 | July | 0030 | 7794 |  |  | 7723 |  |  | -4240 | -4240 | -4169 | Critical Branch | Validation phase | 0 | 71 | NA | NA | NA | 0 | 1 | CH: 7473; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250726 | July | 0130 | 7794 |  |  | 7723 |  |  | -4240 | -4240 | -4169 | Critical Branch | Validation phase | 0 | 71 | NA | NA | NA | 0 | 1 | CH: 7473; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250726 | July | 0230 | 7794 |  |  | 7723 |  |  | -4240 | -4240 | -4169 | Critical Branch | Validation phase | 0 | 71 | NA | NA | NA | 0 | 1 | CH: 7473; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250726 | July | 0330 | 8039 |  |  | 8039 |  |  | -2319 | -2319 | -2319 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 0430 | 8039 |  |  | 8039 |  |  | -2319 | -2319 | -2319 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 0530 | 8039 |  |  | 8039 |  |  | -2319 | -2319 | -2319 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 0630 | 8039 |  |  | 8039 |  |  | -2319 | -2319 | -2319 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 0730 | 7901 |  |  | 7901 |  |  | -2316 | -2316 | -2316 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 0830 | 7901 |  |  | 7901 |  |  | -2316 | -2316 | -2316 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 0930 | 8636 |  |  | 8636 |  |  | -4713 | -4713 | -4713 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1030 | 8636 |  |  | 8636 |  |  | -4713 | -4713 | -4713 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1130 | 8636 |  |  | 8636 |  |  | -4713 | -4713 | -4713 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1230 | 8283 |  |  | 8283 |  |  | -4065 | -4065 | -4065 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1330 | 8283 |  |  | 8283 |  |  | -4065 | -4065 | -4065 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1430 | 8283 |  |  | 8283 |  |  | -4065 | -4065 | -4065 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1530 | 7966 |  |  | 7966 |  |  | -3377 | -3377 | -3377 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1630 | 7966 |  |  | 7966 |  |  | -3377 | -3377 | -3377 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1730 | 7966 |  |  | 7966 |  |  | -3377 | -3377 | -3377 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1830 | 7707 |  |  | 7707 |  |  | -4749 | -4749 | -4749 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 1930 | 7707 |  |  | 7707 |  |  | -4749 | -4749 | -4749 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 2030 | 7707 |  |  | 7707 |  |  | -4749 | -4749 | -4749 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 2130 | 8222 |  |  | 8222 |  |  | -5063 | -5063 | -5063 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 2230 | 8222 |  |  | 8222 |  |  | -5063 | -5063 | -5063 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250726 | July | 2330 | 7622 |  |  | 7622 |  |  | -4456 | -4456 | -4456 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250727 | July | 0030 |  | 8368 | 726 |  | 8259 | 718 | -5140 | -5140 | 0 | Critical Branch | Validation phase | 0 | NA | 109 | 8 | 117 | 5140 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 8378; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0130 |  | 8368 | 726 |  | 8259 | 718 | -5140 | -5140 | 0 | Critical Branch | Validation phase | 0 | NA | 109 | 8 | 117 | 5140 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 8378; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0230 |  | 8368 | 726 |  | 8259 | 718 | -5140 | -5140 | 0 | Critical Branch | Validation phase | 0 | NA | 109 | 8 | 117 | 5140 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 8378; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0330 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250727 | July | 0430 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250727 | July | 0530 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250727 | July | 0630 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250727 | July | 0730 | 8467 |  |  | 8467 |  |  | -4844 | -4844 | -4844 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160
20250727 | July | 0830 | 8467 |  |  | 8467 |  |  | -4844 | -4844 | -4844 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160
20250727 | July | 0930 |  | 7924 | 755 |  | 7923 | 755 | -4428 | -4428 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4428 | 1 | AT: 402; AT: 156
20250727 | July | 1030 |  | 7924 | 755 |  | 7923 | 755 | -4428 | -4428 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4428 | 1 | AT: 402; AT: 156
20250727 | July | 1130 |  | 7924 | 755 |  | 7923 | 755 | -4428 | -4428 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4428 | 1 | AT: 402; AT: 156
20250727 | July | 1230 |  | 8141 | 728 |  | 8141 | 728 | -4413 | -4413 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4413 | 1 | AT: 414; AT: 157
20250727 | July | 1330 |  | 8141 | 728 |  | 8141 | 728 | -4413 | -4413 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4413 | 1 | AT: 414; AT: 157
20250727 | July | 1430 |  | 8141 | 728 |  | 8141 | 728 | -4413 | -4413 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4413 | 1 | AT: 414; AT: 157
20250727 | July | 1530 |  | 8204 | 707 |  | 8201 | 707 | -4857 | -4857 | 0 | Critical Branch | Critical Branch | 0 | NA | 3 | 0 | 3 | 4857 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250727 | July | 1630 |  | 8204 | 707 |  | 8201 | 707 | -4857 | -4857 | 0 | Critical Branch | Critical Branch | 0 | NA | 3 | 0 | 3 | 4857 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250727 | July | 1730 |  | 8204 | 707 |  | 8201 | 707 | -4857 | -4857 | 0 | Critical Branch | Critical Branch | 0 | NA | 3 | 0 | 3 | 4857 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250727 | July | 1830 |  | 7697 | 660 |  | 7696 | 660 | -4931 | -4931 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4931 | 1 | AT: 390; AT: 160
20250727 | July | 1930 |  | 7697 | 660 |  | 7696 | 660 | -4931 | -4931 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4931 | 1 | AT: 390; AT: 160
20250727 | July | 2030 |  | 7697 | 660 |  | 7696 | 660 | -4931 | -4931 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4931 | 1 | AT: 390; AT: 160
20250727 | July | 2130 |  | 7763 | 665 |  | 7762 | 665 | -5069 | -5069 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5069 | 1 | AT: 393; AT: 160
20250727 | July | 2230 |  | 7763 | 665 |  | 7762 | 665 | -5069 | -5069 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5069 | 1 | AT: 393; AT: 160
20250727 | July | 2330 |  | 7535 | 665 |  | 7535 | 665 | -4854 | -4854 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4854 | 1 | AT: 393; AT: 160
20250728 | July | 0030 | 9198 |  |  | 9096 |  |  | -3550 | -3550 | -3463 | Critical Branch | Validation phase | 0 | 102 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8882; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0130 | 9198 |  |  | 9096 |  |  | -3550 | -3550 | -3463 | Critical Branch | Validation phase | 0 | 102 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8882; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0230 | 9198 |  |  | 9096 |  |  | -3550 | -3550 | -3463 | Critical Branch | Validation phase | 0 | 102 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8882; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0330 | 9019 |  |  | 8936 |  |  | -4912 | -4912 | -4838 | Critical Branch | Validation phase | 0 | 83 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8713; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0430 | 9019 |  |  | 8936 |  |  | -4912 | -4912 | -4838 | Critical Branch | Validation phase | 0 | 83 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8713; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0530 | 9019 |  |  | 8936 |  |  | -4912 | -4912 | -4838 | Critical Branch | Validation phase | 0 | 83 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8713; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0630 | 8819 |  |  | 8736 |  |  | -4704 | -4704 | -4630 | Critical Branch | Validation phase | 0 | 83 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8513; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0730 | 8376 |  |  | 8366 |  |  | -3428 | -3428 | -3423 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250728 | July | 0830 | 8376 |  |  | 8366 |  |  | -3428 | -3428 | -3423 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250728 | July | 0930 | 7977 |  |  | 7976 |  |  | 4119 | 280 | 3840 | Minimum Margin | Minimum Margin | 3839 | 1 | NA | NA | NA | 7400 | 1 | AT: 412; AT: 140
20250728 | July | 1030 | 7977 |  |  | 7976 |  |  | 4119 | 280 | 3840 | Minimum Margin | Minimum Margin | 3839 | 1 | NA | NA | NA | 7400 | 1 | AT: 412; AT: 140
20250728 | July | 1130 | 7977 |  |  | 7530 |  |  | 4119 | 280 | 4274 | Minimum Margin | Minimum Margin | 3839 | 447 | NA | NA | NA | 8268 | 1 | AT: 388; AT: 140
20250728 | July | 1230 | 6030 |  |  | 6030 |  |  | -465 | -465 | -465 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 305; AT: 140
20250728 | July | 1330 | 6030 |  |  | 6030 |  |  | -465 | -465 | -465 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 305; AT: 140
20250728 | July | 1430 | 6030 |  |  | 6030 |  |  | -465 | -465 | -465 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 305; AT: 140
20250728 | July | 1530 | 8337 |  |  | 7530 |  |  | -417 | -417 | 365 | Critical Branch | Critical Branch | 0 | 807 | NA | NA | NA | 1147 | 1 | AT: 388; AT: 140
20250728 | July | 1630 | 8337 |  |  | 8329 |  |  | -417 | -417 | -414 | Critical Branch | Critical Branch | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250728 | July | 1730 | 8337 |  |  | 8329 |  |  | -417 | -417 | -414 | Critical Branch | Critical Branch | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250728 | July | 1830 |  | 8580 | 747 |  | 8247 | 747 | -5439 | -5439 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 333 | 0 | 333 | 5439 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage on Chaffard-Grande Ile 2
20250728 | July | 1930 |  | 8580 | 747 |  | 8247 | 747 | -5439 | -5439 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 333 | 0 | 333 | 5439 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2030 |  | 8580 | 747 |  | 8247 | 747 | -5439 | -5439 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 333 | 0 | 333 | 5439 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2130 |  | 8605 | 741 |  | 8260 | 741 | -4142 | -4142 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 345 | 0 | 345 | 4142 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2230 |  | 8605 | 741 |  | 8260 | 741 | -4142 | -4142 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 345 | 0 | 345 | 4142 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2330 |  | 8025 | 766 |  | 7912 | 766 | -3510 | -3510 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 113 | 0 | 113 | 3510 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 156; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage on Chaffard-Grande Ile 2
20250729 | July | 0030 | 8945 |  |  | 8877 |  |  | -1616 | -1616 | -1554 | Critical Branch | Critical Branch | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0130 | 8945 |  |  | 8877 |  |  | -1616 | -1616 | -1554 | Critical Branch | Critical Branch | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0230 | 8945 |  |  | 8877 |  |  | -1616 | -1616 | -1554 | Critical Branch | Critical Branch | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0330 | 8902 |  |  | 8836 |  |  | -5105 | -5105 | -5019 | Critical Branch | Critical Branch | 0 | 66 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0430 | 8902 |  |  | 8836 |  |  | -5105 | -5105 | -5019 | Critical Branch | Critical Branch | 0 | 66 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0530 | 8902 |  |  | 8836 |  |  | -5105 | -5105 | -5019 | Critical Branch | Critical Branch | 0 | 66 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0630 | 8702 |  |  | 8634 |  |  | -4900 | -4900 | -4811 | Critical Branch | Critical Branch | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0730 | 8335 |  |  | 8328 |  |  | -1814 | -1814 | -1807 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0830 | 8335 |  |  | 8328 |  |  | -1814 | -1814 | -1807 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250729 | July | 0930 | 7483 |  |  | 7483 |  |  | -3232 | -3232 | -3231 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250729 | July | 1030 | 7483 |  |  | 7483 |  |  | -3232 | -3232 | -3231 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250729 | July | 1130 | 7483 |  |  | 7483 |  |  | -3232 | -3232 | -3231 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250729 | July | 1230 | 7413 |  |  | 7412 |  |  | -3679 | -3679 | -3678 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140
20250729 | July | 1330 | 7413 |  |  | 7412 |  |  | -3679 | -3679 | -3678 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140
20250729 | July | 1430 | 7413 |  |  | 7412 |  |  | -3679 | -3679 | -3678 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140
20250729 | July | 1530 | 8225 |  |  | 8224 |  |  | -4218 | -4218 | -4216 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250729 | July | 1630 | 8225 |  |  | 8224 |  |  | -4218 | -4218 | -4216 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250729 | July | 1730 | 8925 |  |  | 8924 |  |  | -4898 | -4898 | -4897 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250729 | July | 1830 |  | 8519 | 726 |  | 8517 | 726 | -1865 | -1865 | 0 | Critical Branch | Critical Branch | 0 | NA | 2 | 0 | 2 | 1865 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250729 | July | 1930 |  | 8519 | 726 |  | 8517 | 726 | -1865 | -1865 | 0 | Critical Branch | Critical Branch | 0 | NA | 2 | 0 | 2 | 1865 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250729 | July | 2030 |  | 8519 | 726 |  | 8517 | 726 | -1865 | -1865 | 0 | Critical Branch | Critical Branch | 0 | NA | 2 | 0 | 2 | 1865 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250729 | July | 2130 |  | 8901 | 731 |  | 8879 | 731 | -4572 | -4572 | 0 | Critical Branch | Critical Branch | 0 | NA | 22 | 0 | 22 | 4572 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250729 | July | 2230 |  | 8901 | 731 |  | 8879 | 731 | -4572 | -4572 | 0 | Critical Branch | Critical Branch | 0 | NA | 22 | 0 | 22 | 4572 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250729 | July | 2330 |  | 8321 | 756 |  | 8299 | 756 | -3946 | -3946 | 0 | Critical Branch | Critical Branch | 0 | NA | 22 | 0 | 22 | 3946 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 156; AT: Reduction because NTC over thermal limit on border
20250730 | July | 0030 | 9481 |  |  | 7476 |  |  | -3782 | -3782 | -1777 | Critical Branch | Validation phase | 0 | 2005 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7226; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 0130 | 9481 |  |  | 7476 |  |  | -3782 | -3782 | -1777 | Critical Branch | Validation phase | 0 | 2005 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7226; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 0230 | 9481 |  |  | 7476 |  |  | -3782 | -3782 | -1777 | Critical Branch | Validation phase | 0 | 2005 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7226; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 0330 | 9423 |  |  | 8567 |  |  | -3667 | -3667 | -2814 | Critical Branch | Validation phase | 0 | 856 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8323; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0430 | 9423 |  |  | 8567 |  |  | -3667 | -3667 | -2814 | Critical Branch | Validation phase | 0 | 856 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8323; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0530 | 9423 |  |  | 8567 |  |  | -3667 | -3667 | -2814 | Critical Branch | Validation phase | 0 | 856 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8323; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0630 | 9223 |  |  | 8366 |  |  | -3442 | -3442 | -2588 | Critical Branch | Validation phase | 0 | 857 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8123; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0730 | 8794 |  |  | 8181 |  |  | -1783 | -1783 | -1170 | Critical Branch | Validation phase | 0 | 613 | NA | NA | NA | 0 | 1 | AT: 419; AT: 140; CH: 7931; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0830 | 8794 |  |  | 8181 |  |  | -1783 | -1783 | -1170 | Critical Branch | Validation phase | 0 | 613 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 7931; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0930 | 7183 |  |  | 7183 |  |  | -3245 | -3245 | -3245 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 361; AT: 140
20250730 | July | 1030 | 7183 |  |  | 7183 |  |  | -3245 | -3245 | -3245 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 361; AT: 140
20250730 | July | 1130 | 7183 |  |  | 7183 |  |  | -3245 | -3245 | -3245 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 361; AT: 140
20250730 | July | 1230 | 6196 |  |  | 6195 |  |  | -2343 | -2343 | -2342 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 307; AT: 140
20250730 | July | 1330 | 6196 |  |  | 6195 |  |  | -2343 | -2343 | -2342 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 307; AT: 140
20250730 | July | 1430 | 6196 |  |  | 6195 |  |  | -2343 | -2343 | -2342 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 307; AT: 140
20250730 | July | 1530 | 9266 |  |  | 7695 |  |  | -1546 | -1546 | 20 | Critical Branch | Validation phase | 0 | 1571 | NA | NA | NA | 1586 | 1 | AT: 364; AT: 140; CH: 7978; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 1630 | 9266 |  |  | 8228 |  |  | -1546 | -1546 | -508 | Critical Branch | Validation phase | 0 | 1038 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7978; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 1730 | 9266 |  |  | 8228 |  |  | -1546 | -1546 | -508 | Critical Branch | Validation phase | 0 | 1038 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7978; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 1830 |  | 8545 | 673 |  | 7857 | 620 | -5474 | -5474 | 0 | Critical Branch | Validation phase | 0 | NA | 688 | 53 | 741 | 5474 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border; CH: 8159; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250730 | July | 1930 |  | 8545 | 673 |  | 7857 | 620 | -5474 | -5474 | 0 | Critical Branch | Validation phase | 0 | NA | 688 | 53 | 741 | 5474 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border; CH: 8159; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250730 | July | 2030 |  | 8545 | 673 |  | 7857 | 620 | -5474 | -5474 | 0 | Critical Branch | Validation phase | 0 | NA | 688 | 53 | 741 | 5474 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border; CH: 8159; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250730 | July | 2130 |  | 8633 | 692 |  | 8564 | 687 | -4330 | -4330 | 0 | Critical Branch | Validation phase | 0 | NA | 69 | 5 | 74 | 4330 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8677; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 2230 |  | 8633 | 692 |  | 8564 | 687 | -4330 | -4330 | 0 | Critical Branch | Validation phase | 0 | NA | 69 | 5 | 74 | 4330 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8677; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 2330 |  | 8053 | 717 |  | 8003 | 714 | -3703 | -3703 | 0 | Critical Branch | Validation phase | 0 | NA | 50 | 3 | 53 | 3703 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 8077; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250731 | July | 0030 | 9161 |  |  | 8418 |  |  | -4909 | -4909 | -4166 | Critical Branch | Validation phase | 0 | 743 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8168; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0130 | 9161 |  |  | 8418 |  |  | -4909 | -4909 | -4166 | Critical Branch | Validation phase | 0 | 743 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8168; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0230 | 9161 |  |  | 8418 |  |  | -4909 | -4909 | -4166 | Critical Branch | Validation phase | 0 | 743 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8168; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0330 | 9157 |  |  | 8919 |  |  | -4911 | -4911 | -4682 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8695; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0430 | 9157 |  |  | 8919 |  |  | -4911 | -4911 | -4682 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8695; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0530 | 9157 |  |  | 8919 |  |  | -4911 | -4911 | -4682 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8695; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0630 | 8957 |  |  | 8718 |  |  | -4704 | -4704 | -4475 | Critical Branch | Validation phase | 0 | 239 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8495; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0730 | 8642 |  |  | 7895 |  |  | -2043 | -2043 | -1296 | Critical Branch | Validation phase | 0 | 747 | NA | NA | NA | 0 | 1 | AT: 411; AT: 140; CH: 7645; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0830 | 8642 |  |  | 7895 |  |  | -2043 | -2043 | -1296 | Critical Branch | Validation phase | 0 | 747 | NA | NA | NA | 0 | 1 | AT: 411; AT: 140; CH: 7645; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0930 | 7994 |  |  | 7994 |  |  | -4792 | -4792 | -4792 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 379; AT: 140
20250731 | July | 1030 | 7994 |  |  | 7994 |  |  | -4792 | -4792 | -4792 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 379; AT: 140
20250731 | July | 1130 | 7994 |  |  | 7994 |  |  | -4792 | -4792 | -4792 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 379; AT: 140
20250731 | July | 1230 | 9132 |  |  | 8165 |  |  | -4374 | -4374 | -3407 | Critical Branch | Validation phase | 0 | 967 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7915; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1330 | 9132 |  |  | 8165 |  |  | -4374 | -4374 | -3407 | Critical Branch | Validation phase | 0 | 967 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7915; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1430 | 9132 |  |  | 8165 |  |  | -4374 | -4374 | -3407 | Critical Branch | Validation phase | 0 | 967 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7915; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1530 | 8601 |  |  | 8472 |  |  | -3673 | -3673 | -3544 | Critical Branch | Validation phase | 0 | 129 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 8222; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 1630 | 8601 |  |  | 8472 |  |  | -3673 | -3673 | -3544 | Critical Branch | Validation phase | 0 | 129 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 8222; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 1730 | 8601 |  |  | 8472 |  |  | -3673 | -3673 | -3544 | Critical Branch | Validation phase | 0 | 129 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 8222; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 1830 |  | 8644 | 678 |  | 8568 | 673 | -4284 | -4284 | 0 | Critical Branch | Validation phase | 0 | NA | 76 | 5 | 81 | 4284 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8689; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1930 |  | 8644 | 678 |  | 8568 | 673 | -4284 | -4284 | 0 | Critical Branch | Validation phase | 0 | NA | 76 | 5 | 81 | 4284 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8689; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 2030 |  | 8644 | 678 |  | 8568 | 673 | -4284 | -4284 | 0 | Critical Branch | Validation phase | 0 | NA | 76 | 5 | 81 | 4284 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 8689; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 2130 |  | 8703 | 673 |  | 8691 | 673 | -4127 | -4127 | 0 | Critical Branch | Critical Branch | 0 | NA | 12 | 0 | 12 | 4127 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250731 | July | 2230 |  | 8703 | 673 |  | 8691 | 673 | -4127 | -4127 | 0 | Critical Branch | Critical Branch | 0 | NA | 12 | 0 | 12 | 4127 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250731 | July | 2330 |  | 8123 | 698 |  | 8112 | 698 | -3504 | -3504 | 0 | Critical Branch | Critical Branch | 0 | NA | 11 | 0 | 11 | 3504 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250801 | August | 0030 | 8910 |  |  | 8712 |  |  | -2167 | -2167 | -1969 | Critical Branch | Validation phase | 0 | 198 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250801 | August | 0130 | 8910 |  |  | 8712 |  |  | -2167 | -2167 | -1969 | Critical Branch | Validation phase | 0 | 198 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250801 | August | 0230 | 8910 |  |  | 8712 |  |  | -2167 | -2167 | -1969 | Critical Branch | Validation phase | 0 | 198 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250801 | August | 0330 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8669; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0430 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8669; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0530 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8669; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0630 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8669; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0730 | 8654 |  |  | 8654 |  |  | -1679 | -1679 | -1679 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 140
20250801 | August | 0830 | 8654 |  |  | 8654 |  |  | -1679 | -1679 | -1679 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 140
20250801 | August | 0930 | 8572 |  |  | 8572 |  |  | -4609 | -4609 | -4609 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250801 | August | 1030 | 8572 |  |  | 8572 |  |  | -4609 | -4609 | -4609 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250801 | August | 1130 | 8572 |  |  | 8572 |  |  | -4609 | -4609 | -4609 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250801 | August | 1230 | 8573 |  |  | 8573 |  |  | -4753 | -4753 | -4753 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250801 | August | 1330 | 8573 |  |  | 8573 |  |  | -4753 | -4753 | -4753 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250801 | August | 1430 | 8573 |  |  | 8573 |  |  | -4753 | -4753 | -4753 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250801 | August | 1530 | 8035 |  |  | 8034 |  |  | -4414 | -4414 | -4414 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140
20250801 | August | 1630 | 8035 |  |  | 8034 |  |  | -4414 | -4414 | -4414 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140
20250801 | August | 1730 | 8035 |  |  | 8034 |  |  | -4414 | -4414 | -4414 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140
20250801 | August | 1830 |  | 8589 | 668 |  | 8583 | 668 | -5937 | -5937 | 0 | Critical Branch | Critical Branch | 0 | NA | 6 | 0 | 6 | 5937 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250801 | August | 1930 |  | 8589 | 668 |  | 8583 | 668 | -5937 | -5937 | 0 | Critical Branch | Critical Branch | 0 | NA | 6 | 0 | 6 | 5937 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250801 | August | 2030 |  | 8589 | 668 |  | 8583 | 668 | -5937 | -5937 | 0 | Critical Branch | Critical Branch | 0 | NA | 6 | 0 | 6 | 5937 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250801 | August | 2130 |  | 8561 | 668 |  | 8557 | 668 | -5755 | -5755 | 0 | Critical Branch | Critical Branch | 0 | NA | 4 | 0 | 4 | 5755 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250801 | August | 2230 |  | 8561 | 668 |  | 8557 | 668 | -5755 | -5755 | 0 | Critical Branch | Critical Branch | 0 | NA | 4 | 0 | 4 | 5755 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250801 | August | 2330 |  | 7981 | 693 |  | 7978 | 693 | -5128 | -5128 | 0 | Critical Branch | Critical Branch | 0 | NA | 3 | 0 | 3 | 5128 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250802 | August | 0030 | 9450 |  |  | 9274 |  |  | -5024 | -5024 | -4864 | Critical Branch | Validation phase | 0 | 176 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 9069; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250802 | August | 0130 | 9450 |  |  | 9274 |  |  | -5024 | -5024 | -4864 | Critical Branch | Validation phase | 0 | 176 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 9069; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250802 | August | 0230 | 9450 |  |  | 9274 |  |  | -5024 | -5024 | -4864 | Critical Branch | Validation phase | 0 | 176 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 9069; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250802 | August | 0330 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8923; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0430 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8923; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0530 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8923; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0630 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8923; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0730 | 9146 |  |  | 9141 |  |  | -5506 | -5506 | -5500 | Critical Branch | Critical Branch | 0 | 5 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250802 | August | 0830 | 9146 |  |  | 9141 |  |  | -5506 | -5506 | -5500 | Critical Branch | Critical Branch | 0 | 5 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250802 | August | 0930 | 8072 |  |  | 8072 |  |  | -3982 | -3982 | -3982 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 376; AT: 140
20250802 | August | 1030 | 8072 |  |  | 8072 |  |  | -3982 | -3982 | -3982 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 376; AT: 140
20250802 | August | 1130 | 8072 |  |  | 8072 |  |  | -3982 | -3982 | -3982 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 376; AT: 140
20250802 | August | 1230 | 8509 |  |  | 8509 |  |  | -5054 | -5054 | -5054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 398; AT: 140
20250802 | August | 1330 | 8509 |  |  | 8509 |  |  | -5054 | -5054 | -5054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 398; AT: 140
20250802 | August | 1430 | 8509 |  |  | 8509 |  |  | -5054 | -5054 | -5054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 398; AT: 140
20250802 | August | 1530 | 8897 |  |  | 8897 |  |  | -3560 | -3560 | -3560 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 140
20250802 | August | 1630 | 8897 |  |  | 8897 |  |  | -3560 | -3560 | -3560 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 140
20250802 | August | 1730 | 8897 |  |  | 8897 |  |  | -3560 | -3560 | -3560 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 140
20250802 | August | 1830 |  | 8574 | 682 |  | 8569 | 682 | -4924 | -4924 | 0 | Critical Branch | Critical Branch | 0 | NA | 5 | 0 | 5 | 4924 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border
20250802 | August | 1930 |  | 8574 | 682 |  | 8569 | 682 | -4924 | -4924 | 0 | Critical Branch | Critical Branch | 0 | NA | 5 | 0 | 5 | 4924 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border
20250802 | August | 2030 |  | 8574 | 682 |  | 8569 | 682 | -4924 | -4924 | 0 | Critical Branch | Critical Branch | 0 | NA | 5 | 0 | 5 | 4924 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border
20250802 | August | 2130 | 8859 |  |  | 8858 |  |  | -5115 | -5115 | -5115 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140
20250802 | August | 2230 | 8859 |  |  | 8858 |  |  | -5115 | -5115 | -5115 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140
20250802 | August | 2330 | 8259 |  |  | 8259 |  |  | -4511 | -4511 | -4511 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160
20250803 | August | 0030 | 9279 |  |  | 9236 |  |  | -5149 | -5149 | -5120 | Critical Branch | Critical Branch | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0130 | 9279 |  |  | 9236 |  |  | -5149 | -5149 | -5120 | Critical Branch | Critical Branch | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0230 | 9279 |  |  | 9236 |  |  | -5149 | -5149 | -5120 | Critical Branch | Critical Branch | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0330 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0430 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0530 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0630 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0730 | 8722 |  |  | 8708 |  |  | -5768 | -5768 | -5749 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0830 | 8722 |  |  | 8708 |  |  | -5768 | -5768 | -5749 | Critical Branch | Critical Branch | 0 | 14 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 0930 | 8558 |  |  | 8552 |  |  | -4182 | -4182 | -4178 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1030 | 8558 |  |  | 8552 |  |  | -4182 | -4182 | -4178 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1130 | 8558 |  |  | 8552 |  |  | -4182 | -4182 | -4178 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1230 | 8589 |  |  | 8582 |  |  | -1353 | -1353 | -1346 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1330 | 8589 |  |  | 8582 |  |  | -1353 | -1353 | -1346 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1430 | 8589 |  |  | 8582 |  |  | -1353 | -1353 | -1346 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1530 |  | 8518 | 774 |  | 8485 | 774 | -1068 | -1068 | 0 | Critical Branch | Critical Branch | 0 | NA | 33 | 0 | 33 | 1068 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1630 |  | 8518 | 774 |  | 8485 | 774 | -1068 | -1068 | 0 | Critical Branch | Critical Branch | 0 | NA | 33 | 0 | 33 | 1068 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1730 |  | 8518 | 774 |  | 8485 | 774 | -1068 | -1068 | 0 | Critical Branch | Critical Branch | 0 | NA | 33 | 0 | 33 | 1068 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1830 |  | 8851 | 796 |  | 8799 | 796 | -3429 | -3429 | 0 | Critical Branch | Critical Branch | 0 | NA | 52 | 0 | 52 | 3429 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250803 | August | 1930 |  | 8851 | 796 |  | 8799 | 796 | -3429 | -3429 | 0 | Critical Branch | Critical Branch | 0 | NA | 52 | 0 | 52 | 3429 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250803 | August | 2030 |  | 8851 | 796 |  | 8799 | 796 | -3429 | -3429 | 0 | Critical Branch | Critical Branch | 0 | NA | 52 | 0 | 52 | 3429 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250803 | August | 2130 | 9271 |  |  | 9228 |  |  | -3343 | -3343 | -3318 | Critical Branch | Critical Branch | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 2230 | 9271 |  |  | 9228 |  |  | -3343 | -3343 | -3318 | Critical Branch | Critical Branch | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250803 | August | 2330 | 9271 |  |  | 9228 |  |  | -3343 | -3343 | -3318 | Critical Branch | Critical Branch | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0030 | 8815 |  |  | 8796 |  |  | -5588 | -5588 | -5575 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0130 | 8815 |  |  | 8796 |  |  | -5588 | -5588 | -5575 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0230 | 8815 |  |  | 8796 |  |  | -5588 | -5588 | -5575 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0330 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0430 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0530 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0630 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250804 | August | 0730 | 7995 |  |  | 7624 |  |  | -3980 | -3980 | -3609 | Critical Branch | Validation phase | 0 | 371 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 7374; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 0830 | 6595 |  |  | 6224 |  |  | -2615 | -2615 | -2244 | Critical Branch | Validation phase | 0 | 371 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 5974; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 0930 | 6360 |  |  | 6224 |  |  | -3673 | -3673 | -3537 | Critical Branch | Validation phase | 0 | 136 | NA | NA | NA | 0 | 1 | AT: 376; AT: 140; CH: 5974; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1030 | 6360 |  |  | 6224 |  |  | -3673 | -3673 | -3537 | Critical Branch | Validation phase | 0 | 136 | NA | NA | NA | 0 | 1 | AT: 376; AT: 140; CH: 5974; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1130 | 6360 |  |  | 6224 |  |  | -3673 | -3673 | -3537 | Critical Branch | Validation phase | 0 | 136 | NA | NA | NA | 0 | 1 | AT: 376; AT: 140; CH: 5974; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1230 | 6101 |  |  | 6100 |  |  | -3348 | -3348 | -3348 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140
20250804 | August | 1330 | 6101 |  |  | 6100 |  |  | -3348 | -3348 | -3348 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140
20250804 | August | 1430 | 6101 |  |  | 6100 |  |  | -3348 | -3348 | -3348 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140
20250804 | August | 1530 |  | 6366 | 0 |  | 6306 | 0 | -4307 | -4307 | 0 | TTC Selection - LTTCExport | Validation phase | 0 | NA | 60 | 0 | 60 | 4307 | 1 | AT: 376; AT: 140; CH: 6056; CH: Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250804 | August | 1630 |  | 6366 | 0 |  | 6306 | 0 | -4307 | -4307 | 0 | TTC Selection - LTTCExport | Validation phase | 0 | NA | 60 | 0 | 60 | 4307 | 1 | AT: 376; AT: 140; CH: 6056; CH: Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250804 | August | 1730 |  | 6366 | 0 |  | 6306 | 0 | -4307 | -4307 | 0 | TTC Selection - LTTCExport | Validation phase | 0 | NA | 60 | 0 | 60 | 4307 | 1 | AT: 376; AT: 140; CH: 6056; CH: Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250804 | August | 1830 |  | 6303 | 0 |  | 6258 | 0 | -4259 | -4259 | 0 | TTC Selection - LTTCExport | Validation phase | 0 | NA | 45 | 0 | 45 | 4259 | 1 | AT: 372; AT: 140; CH: 6008; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1930 |  | 6303 | 0 |  | 6258 | 0 | -4259 | -4259 | 0 | TTC Selection - LTTCExport | Validation phase | 0 | NA | 45 | 0 | 45 | 4259 | 1 | AT: 372; AT: 140; CH: 6008; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 2030 |  | 6303 | 0 |  | 6258 | 0 | -4259 | -4259 | 0 | TTC Selection - LTTCExport | Validation phase | 0 | NA | 45 | 0 | 45 | 4259 | 1 | AT: 372; AT: 140; CH: 6008; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 2130 |  | 5678 | 0 |  | 5677 | 0 | -3395 | -3395 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 1 | 0 | 1 | 3395 | 1 | AT: 332; AT: 140
20250804 | August | 2230 |  | 5378 | 0 |  | 5378 | 0 | -3110 | -3110 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 3110 | 1 | AT: 328; AT: 140
20250804 | August | 2330 |  | 4818 | 0 |  | 4818 | 0 | -2543 | -2543 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 2543 | 1 | AT: 311; AT: 160
20250805 | August | 0030 | 5565 |  |  | 5565 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0130 | 5565 |  |  | 5565 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0230 | 5565 |  |  | 5565 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0330 | 5751 |  |  | 5751 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0430 | 5751 |  |  | 5751 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0530 | 5751 |  |  | 5751 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0630 | 5751 |  |  | 5751 |  |  | -1510 | -1510 | -1510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0730 | 5657 |  |  | 5657 |  |  | -1633 | -1633 | -1633 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0830 | 5657 |  |  | 5657 |  |  | -1633 | -1633 | -1633 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 0930 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1030 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1130 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1230 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1330 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1430 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1530 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1630 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1730 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | CH: 5407; CH: No calculation has been done
20250805 | August | 1830 | 5354 |  |  | 5354 |  |  | -1412 | -1412 | -1412 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 1930 | 5354 |  |  | 5354 |  |  | -1412 | -1412 | -1412 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 2030 | 5354 |  |  | 5354 |  |  | -1412 | -1412 | -1412 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 2130 | 4992 |  |  | 4992 |  |  | -1483 | -1483 | -1483 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 2230 | 4692 |  |  | 4692 |  |  | -1185 | -1185 | -1185 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250805 | August | 2330 | 4132 |  |  | 4132 |  |  | -620 | -620 | -620 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250806 | August | 0030 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0130 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0230 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0330 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0430 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0530 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0630 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0730 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0830 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0930 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1030 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1130 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1230 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1330 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1430 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1530 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1630 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1730 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1830 |  | 5616 | 0 |  | 5616 | 0 | -2341 | -2341 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 2341 | 1 | CH: 6866; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1930 |  | 5616 | 0 |  | 5616 | 0 | -2341 | -2341 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 2341 | 1 | CH: 6866; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2030 |  | 5616 | 0 |  | 5616 | 0 | -2341 | -2341 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 2341 | 1 | CH: 6866; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2130 | 6131 |  |  | 6131 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6866; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2230 | 6131 |  |  | 6131 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6866; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2330 | 5571 |  |  | 5571 |  |  | -1011 | -1011 | -1011 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6306; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250807 | August | 0030 | 6367 |  |  | 6367 |  |  | -1297 | -1297 | -1297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0130 | 6367 |  |  | 6367 |  |  | -1297 | -1297 | -1297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0230 | 6367 |  |  | 6367 |  |  | -1297 | -1297 | -1297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0330 | 6144 |  |  | 6144 |  |  | -1347 | -1347 | -1347 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0430 | 6144 |  |  | 6144 |  |  | -1347 | -1347 | -1347 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0530 | 6144 |  |  | 6144 |  |  | -1347 | -1347 | -1347 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0630 | 6144 |  |  | 6144 |  |  | -1347 | -1347 | -1347 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0730 | 6199 |  |  | 6199 |  |  | -1496 | -1496 | -1496 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0830 | 6199 |  |  | 6199 |  |  | -1496 | -1496 | -1496 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 0930 | 5852 |  |  | 5852 |  |  | -1361 | -1361 | -1361 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1030 | 5852 |  |  | 5852 |  |  | -1361 | -1361 | -1361 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1130 | 5852 |  |  | 5852 |  |  | -1361 | -1361 | -1361 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1230 | 6317 |  |  | 6317 |  |  | -863 | -863 | -863 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1330 | 6317 |  |  | 6317 |  |  | -863 | -863 | -863 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1430 | 6317 |  |  | 6317 |  |  | -863 | -863 | -863 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1530 | 6457 |  |  | 6457 |  |  | -2777 | -2777 | -2777 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1630 | 6457 |  |  | 6457 |  |  | -2777 | -2777 | -2777 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1730 | 6457 |  |  | 6457 |  |  | -2777 | -2777 | -2777 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 1830 |  | 5678 | 0 |  | 5678 | 0 | -4012 | -4012 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 4012 | 0
20250807 | August | 1930 |  | 5678 | 0 |  | 5678 | 0 | -4012 | -4012 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 4012 | 0
20250807 | August | 2030 |  | 5678 | 0 |  | 5678 | 0 | -4012 | -4012 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 4012 | 0
20250807 | August | 2130 | 6061 |  |  | 6061 |  |  | -3977 | -3977 | -3977 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 2230 | 6061 |  |  | 6061 |  |  | -3977 | -3977 | -3977 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250807 | August | 2330 | 5501 |  |  | 5501 |  |  | -3415 | -3415 | -3415 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0030 | 6395 |  |  | 6395 |  |  | -3619 | -3619 | -3619 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0130 | 6395 |  |  | 6395 |  |  | -3619 | -3619 | -3619 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0230 | 6395 |  |  | 6395 |  |  | -3619 | -3619 | -3619 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0330 | 6314 |  |  | 6314 |  |  | -3510 | -3510 | -3510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0430 | 6314 |  |  | 6314 |  |  | -3510 | -3510 | -3510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0530 | 6314 |  |  | 6314 |  |  | -3510 | -3510 | -3510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0630 | 6314 |  |  | 6314 |  |  | -3510 | -3510 | -3510 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0730 | 6289 |  |  | 6289 |  |  | -1301 | -1301 | -1301 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0830 | 6289 |  |  | 6289 |  |  | -1301 | -1301 | -1301 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 0930 | 6374 |  |  | 6374 |  |  | -3461 | -3461 | -3461 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 1030 | 6374 |  |  | 6374 |  |  | -3461 | -3461 | -3461 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 1130 | 6374 |  |  | 6374 |  |  | -3461 | -3461 | -3461 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250808 | August | 1230 | 6369 |  |  | 6250 |  |  | -1025 | -1025 | -906 | Critical Branch | Validation phase | 0 | 119 | NA | NA | NA | 0 | 1 | CH: 6000; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1330 | 6369 |  |  | 6250 |  |  | -1025 | -1025 | -906 | Critical Branch | Validation phase | 0 | 119 | NA | NA | NA | 0 | 1 | CH: 6000; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1430 | 6369 |  |  | 6250 |  |  | -1025 | -1025 | -906 | Critical Branch | Validation phase | 0 | 119 | NA | NA | NA | 0 | 1 | CH: 6000; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1530 | 6375 |  |  | 6271 |  |  | -962 | -962 | -858 | Critical Branch | Validation phase | 0 | 104 | NA | NA | NA | 0 | 1 | CH: 6021; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1630 | 6375 |  |  | 6271 |  |  | -962 | -962 | -858 | Critical Branch | Validation phase | 0 | 104 | NA | NA | NA | 0 | 1 | CH: 6021; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1730 | 6375 |  |  | 6271 |  |  | -962 | -962 | -858 | Critical Branch | Validation phase | 0 | 104 | NA | NA | NA | 0 | 1 | CH: 6021; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1830 |  | 6105 | 0 |  | 6105 | 0 | -1751 | -1751 | 0 | TTC Selection - LTTCExport | Full import calculation | 0 | NA | 0 | 0 | 0 | 1751 | 0
20250808 | August | 1930 |  | 6105 | 0 |  | 6105 | 0 | -1751 | -1751 | 0 | TTC Selection - LTTCExport | Full import calculation | 0 | NA | 0 | 0 | 0 | 1751 | 0
20250808 | August | 2030 |  | 6105 | 0 |  | 6105 | 0 | -1751 | -1751 | 0 | TTC Selection - LTTCExport | Full import calculation | 0 | NA | 0 | 0 | 0 | 1751 | 0
20250808 | August | 2130 |  | 5928 | 0 |  | 5928 | 0 | -1311 | -1311 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1311 | 0
20250808 | August | 2230 |  | 5928 | 0 |  | 5928 | 0 | -1311 | -1311 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1311 | 0
20250808 | August | 2330 |  | 5368 | 0 |  | 5368 | 0 | -750 | -750 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 750 | 0
20250809 | August | 0030 | 6193 |  |  | 6193 |  |  | -1450 | -1450 | -1450 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0130 | 6193 |  |  | 6193 |  |  | -1450 | -1450 | -1450 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0230 | 6193 |  |  | 6193 |  |  | -1450 | -1450 | -1450 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0330 | 6288 |  |  | 6288 |  |  | -1494 | -1494 | -1494 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0430 | 6288 |  |  | 6288 |  |  | -1494 | -1494 | -1494 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0530 | 6288 |  |  | 6288 |  |  | -1494 | -1494 | -1494 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0630 | 6288 |  |  | 6288 |  |  | -1494 | -1494 | -1494 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0730 | 6437 |  |  | 6437 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0830 | 6437 |  |  | 6437 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 0930 |  | 5803 | 0 |  | 5803 | 0 | -1084 | -1084 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1084 | 0
20250809 | August | 1030 |  | 5803 | 0 |  | 5803 | 0 | -1084 | -1084 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1084 | 0
20250809 | August | 1130 |  | 5803 | 0 |  | 5803 | 0 | -1084 | -1084 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1084 | 0
20250809 | August | 1230 | 5255 |  |  | 5124 |  |  | -499 | -499 | -368 | Critical Branch | Validation phase | 0 | 131 | NA | NA | NA | 0 | 1 | CH: 4874; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250809 | August | 1330 | 5255 |  |  | 5124 |  |  | -499 | -499 | -368 | Critical Branch | Validation phase | 0 | 131 | NA | NA | NA | 0 | 1 | CH: 4874; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250809 | August | 1430 | 5255 |  |  | 5124 |  |  | -499 | -499 | -368 | Critical Branch | Validation phase | 0 | 131 | NA | NA | NA | 0 | 1 | CH: 4874; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250809 | August | 1530 |  | 6178 | 0 |  | 6178 | 0 | -1233 | -1233 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1233 | 0
20250809 | August | 1630 |  | 6178 | 0 |  | 6178 | 0 | -1233 | -1233 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1233 | 0
20250809 | August | 1730 |  | 6178 | 0 |  | 6178 | 0 | -1233 | -1233 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 1233 | 0
20250809 | August | 1830 |  | 6241 | 0 |  | 6241 | 0 | -3103 | -3103 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 3103 | 0
20250809 | August | 1930 |  | 6241 | 0 |  | 6241 | 0 | -3103 | -3103 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 3103 | 0
20250809 | August | 2030 |  | 6241 | 0 |  | 6241 | 0 | -3103 | -3103 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 3103 | 0
20250809 | August | 2130 | 6342 |  |  | 6342 |  |  | -1535 | -1535 | -1535 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 2230 | 6342 |  |  | 6342 |  |  | -1535 | -1535 | -1535 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250809 | August | 2330 | 5782 |  |  | 5782 |  |  | -974 | -974 | -974 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0030 | 6287 |  |  | 6287 |  |  | -3213 | -3213 | -3213 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0130 | 6287 |  |  | 6287 |  |  | -3213 | -3213 | -3213 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0230 | 6287 |  |  | 6287 |  |  | -3213 | -3213 | -3213 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0330 | 6395 |  |  | 6395 |  |  | -3328 | -3328 | -3328 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0430 | 6395 |  |  | 6395 |  |  | -3328 | -3328 | -3328 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0530 | 6395 |  |  | 6395 |  |  | -3328 | -3328 | -3328 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0630 | 6395 |  |  | 6395 |  |  | -3328 | -3328 | -3328 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 0730 |  | 5806 | 0 |  | 5806 | 0 | -719 | -719 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 719 | 0
20250810 | August | 0830 |  | 5806 | 0 |  | 5806 | 0 | -719 | -719 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 719 | 0
20250810 | August | 0930 | 5619 |  |  | 5619 |  |  | -777 | -777 | -777 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 1030 | 5619 |  |  | 5619 |  |  | -777 | -777 | -777 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 1130 | 5619 |  |  | 5619 |  |  | -777 | -777 | -777 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 1230 | 5039 |  |  | 5039 |  |  | -462 | -462 | -462 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 1330 | 5039 |  |  | 5039 |  |  | -462 | -462 | -462 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 1430 | 5039 |  |  | 5039 |  |  | -462 | -462 | -462 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 1530 |  | 5443 | 0 |  | 5443 | 0 | 12 | 12 | 0 | Adjustment reached | Adjustment reached | 0 | NA | 0 | 0 | 0 | -12 | 0
20250810 | August | 1630 |  | 5443 | 0 |  | 5443 | 0 | 12 | 12 | 0 | Adjustment reached | Adjustment reached | 0 | NA | 0 | 0 | 0 | -12 | 0
20250810 | August | 1730 |  | 5443 | 0 |  | 5443 | 0 | 12 | 12 | 0 | Adjustment reached | Adjustment reached | 0 | NA | 0 | 0 | 0 | -12 | 0
20250810 | August | 1830 |  | 5993 | 0 |  | 5993 | 0 | -808 | -808 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 808 | 0
20250810 | August | 1930 |  | 5993 | 0 |  | 5993 | 0 | -808 | -808 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 808 | 0
20250810 | August | 2030 |  | 5993 | 0 |  | 5993 | 0 | -808 | -808 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | 0 | NA | 0 | 0 | 0 | 808 | 0
20250810 | August | 2130 | 6067 |  |  | 6067 |  |  | -1314 | -1314 | -1314 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 2230 | 6067 |  |  | 6067 |  |  | -1314 | -1314 | -1314 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250810 | August | 2330 | 6067 |  |  | 6067 |  |  | -1314 | -1314 | -1314 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 0030 | 5969 |  |  | 5969 |  |  | -1163 | -1163 | -1163 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 0130 | 5969 |  |  | 5969 |  |  | -1163 | -1163 | -1163 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 0230 | 5969 |  |  | 5969 |  |  | -1163 | -1163 | -1163 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 0330 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 0 | 251 | NA | NA | NA | 0 | 1 | CH: 5571; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0430 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 0 | 251 | NA | NA | NA | 0 | 1 | CH: 5571; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0530 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 0 | 251 | NA | NA | NA | 0 | 1 | CH: 5571; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0630 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 0 | 251 | NA | NA | NA | 0 | 1 | CH: 5571; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0730 | 6022 |  |  | 6022 |  |  | -1380 | -1380 | -1380 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 0830 | 6022 |  |  | 6022 |  |  | -1380 | -1380 | -1380 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 0930 | 5378 |  |  | 5038 |  |  | 2680 | 432 | 2588 | Minimum Margin | Validation phase | 2248 | 340 | NA | NA | NA | 4744 | 1 | CH: 4788; CH: Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250811 | August | 1030 | 5378 |  |  | 5038 |  |  | 2680 | 432 | 2588 | Minimum Margin | Validation phase | 2248 | 340 | NA | NA | NA | 4744 | 1 | CH: 4788; CH: Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250811 | August | 1130 | 5378 |  |  | 5038 |  |  | 2680 | 432 | 2588 | Minimum Margin | Validation phase | 2248 | 340 | NA | NA | NA | 4744 | 1 | CH: 4788; CH: Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250811 | August | 1230 | 5377 |  |  | 5365 |  |  | -461 | -461 | -449 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 5115; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250811 | August | 1330 | 5377 |  |  | 5365 |  |  | -461 | -461 | -449 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 5115; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250811 | August | 1430 | 5377 |  |  | 5365 |  |  | -461 | -461 | -449 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 5115; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250811 | August | 1530 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 1630 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 1730 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 1830 | 5345 |  |  | 5345 |  |  | -3231 | -3231 | -3231 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 1930 | 5345 |  |  | 5345 |  |  | -3231 | -3231 | -3231 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 2030 | 5345 |  |  | 5345 |  |  | -3231 | -3231 | -3231 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 2130 | 6317 |  |  | 6317 |  |  | -1438 | -1438 | -1438 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 2230 | 6317 |  |  | 6317 |  |  | -1438 | -1438 | -1438 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250811 | August | 2330 | 5757 |  |  | 5757 |  |  | -877 | -877 | -877 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 0030 |  | 5869 | 168 |  | 5869 | 168 | -2897 | -2897 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2897 | 0
20250812 | August | 0130 |  | 5869 | 168 |  | 5869 | 168 | -2897 | -2897 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2897 | 0
20250812 | August | 0230 |  | 5869 | 168 |  | 5869 | 168 | -2897 | -2897 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2897 | 0
20250812 | August | 0330 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 0 | 241 | NA | NA | NA | 0 | 1 | CH: 5599; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0430 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 0 | 241 | NA | NA | NA | 0 | 1 | CH: 5599; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0530 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 0 | 241 | NA | NA | NA | 0 | 1 | CH: 5599; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0630 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 0 | 241 | NA | NA | NA | 0 | 1 | CH: 5599; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0730 |  | 5451 | 125 |  | 5451 | 125 | -2815 | -2815 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2815 | 0
20250812 | August | 0830 |  | 5451 | 125 |  | 5451 | 125 | -2815 | -2815 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2815 | 0
20250812 | August | 0930 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1030 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1130 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1230 | 6184 |  |  | 6184 |  |  | -1476 | -1476 | -1476 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1330 | 6184 |  |  | 6184 |  |  | -1476 | -1476 | -1476 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1430 | 6184 |  |  | 6184 |  |  | -1476 | -1476 | -1476 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1530 | 6153 |  |  | 6153 |  |  | -876 | -876 | -876 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1630 | 6153 |  |  | 6153 |  |  | -876 | -876 | -876 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1730 | 6153 |  |  | 6153 |  |  | -876 | -876 | -876 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250812 | August | 1830 |  | 4978 | 114 |  | 4978 | 114 | -1709 | -1709 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1709 | 0
20250812 | August | 1930 |  | 4978 | 114 |  | 4978 | 114 | -1709 | -1709 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1709 | 0
20250812 | August | 2030 |  | 4978 | 114 |  | 4978 | 114 | -1709 | -1709 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1709 | 0
20250812 | August | 2130 |  | 5789 | 134 |  | 5789 | 134 | -3164 | -3164 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3164 | 0
20250812 | August | 2230 |  | 5789 | 134 |  | 5789 | 134 | -3164 | -3164 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3164 | 0
20250812 | August | 2330 |  | 5235 | 154 |  | 5235 | 154 | -2598 | -2598 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2598 | 0
20250813 | August | 0030 | 6333 |  |  | 6333 |  |  | -2801 | -2801 | -2801 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 0130 | 6333 |  |  | 6333 |  |  | -2801 | -2801 | -2801 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 0230 | 6333 |  |  | 6333 |  |  | -2801 | -2801 | -2801 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 0330 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6118; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0430 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6118; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0530 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6118; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0630 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6118; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0730 | 5614 |  |  | 5614 |  |  | -2590 | -2590 | -2590 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 0830 | 5614 |  |  | 5614 |  |  | -2590 | -2590 | -2590 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 0930 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1030 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1130 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1230 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1330 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1430 | 4946 |  |  | 4946 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1530 | 5656 |  |  | 5656 |  |  | -1976 | -1976 | -1976 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1630 | 6190 |  |  | 6190 |  |  | -2432 | -2432 | -2432 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1730 | 6190 |  |  | 6190 |  |  | -2432 | -2432 | -2432 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 1830 |  | 4745 | 575 |  | 4745 | 575 | -3659 | -3659 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 3659 | 0
20250813 | August | 1930 |  | 4745 | 575 |  | 4745 | 575 | -3659 | -3659 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 3659 | 0
20250813 | August | 2030 |  | 4745 | 575 |  | 4745 | 575 | -3659 | -3659 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 3659 | 0
20250813 | August | 2130 | 6027 |  |  | 6027 |  |  | -1699 | -1699 | -1699 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 2230 | 6027 |  |  | 6027 |  |  | -1699 | -1699 | -1699 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250813 | August | 2330 | 5427 |  |  | 5427 |  |  | -1093 | -1093 | -1093 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0030 | 6883 |  |  | 6871 |  |  | -3705 | -3705 | -3693 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6621; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250814 | August | 0130 | 6883 |  |  | 6871 |  |  | -3705 | -3705 | -3693 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6621; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250814 | August | 0230 | 6883 |  |  | 6871 |  |  | -3705 | -3705 | -3693 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | CH: 6621; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250814 | August | 0330 | 6415 |  |  | 6415 |  |  | -3005 | -3005 | -3005 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0430 | 6415 |  |  | 6415 |  |  | -3005 | -3005 | -3005 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0530 | 6415 |  |  | 6415 |  |  | -3005 | -3005 | -3005 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0630 | 6415 |  |  | 6415 |  |  | -3005 | -3005 | -3005 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0730 | 5480 |  |  | 5480 |  |  | -2753 | -2753 | -2753 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0830 | 5480 |  |  | 5480 |  |  | -2753 | -2753 | -2753 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 0930 | 5480 |  |  | 5250 |  |  | -4242 | -4242 | -4012 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1030 | 5480 |  |  | 5250 |  |  | -4242 | -4242 | -4012 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1130 | 5480 |  |  | 5250 |  |  | -4242 | -4242 | -4012 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1230 | 5480 |  |  | 5250 |  |  | -3281 | -3281 | -3051 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1330 | 5480 |  |  | 5250 |  |  | -3281 | -3281 | -3051 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1430 | 5480 |  |  | 5250 |  |  | -3281 | -3281 | -3051 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1530 | 6911 |  |  | 6750 |  |  | -3608 | -3608 | -3447 | Critical Branch | Smoothing ramp | 0 | 161 | NA | NA | NA | 0 | 1
20250814 | August | 1630 | 6911 |  |  | 6911 |  |  | -3608 | -3608 | -3608 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 1730 | 6911 |  |  | 6911 |  |  | -3608 | -3608 | -3608 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 1830 |  | 5428 | 508 |  | 5428 | 508 | -3533 | -3533 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3533 | 0
20250814 | August | 1930 |  | 5428 | 508 |  | 5428 | 508 | -3533 | -3533 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3533 | 0
20250814 | August | 2030 |  | 5428 | 508 |  | 5428 | 508 | -3533 | -3533 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3533 | 0
20250814 | August | 2130 | 6732 |  |  | 6732 |  |  | -3559 | -3559 | -3559 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 2230 | 6732 |  |  | 6732 |  |  | -3559 | -3559 | -3559 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250814 | August | 2330 | 6132 |  |  | 6132 |  |  | -2953 | -2953 | -2953 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250815 | August | 0030 |  | 7209 | 192 |  | 4996 | 160 | -4486 | -4486 | 0 | Critical Branch | Validation phase | 0 | NA | 2213 | 32 | 2245 | 4486 | 1 | AT: 220; AT: 160; CH: 6189; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0130 |  | 7209 | 192 |  | 4996 | 160 | -4486 | -4486 | 0 | Critical Branch | Validation phase | 0 | NA | 2213 | 32 | 2245 | 4486 | 1 | AT: 220; AT: 160; CH: 6189; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0230 |  | 7209 | 192 |  | 4996 | 160 | -4486 | -4486 | 0 | Critical Branch | Validation phase | 0 | NA | 2213 | 32 | 2245 | 4486 | 1 | AT: 220; AT: 160; CH: 6189; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0330 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 0 | 2374 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5191; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0430 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 0 | 2374 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5191; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0530 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 0 | 2374 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5191; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0630 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 0 | 2374 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5191; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0730 |  | 6553 | 173 |  | 4695 | 145 | -3807 | -3807 | 0 | Critical Branch | Validation phase | 0 | NA | 1858 | 28 | 1886 | 3807 | 1 | AT: 198; AT: 140; CH: 5680; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0830 |  | 6553 | 173 |  | 4695 | 145 | -3807 | -3807 | 0 | Critical Branch | Validation phase | 0 | NA | 1858 | 28 | 1886 | 3807 | 1 | AT: 198; AT: 140; CH: 5680; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 0930 | 5658 |  |  | 4571 |  |  | -1790 | -1790 | -785 | Critical Branch | Validation phase | 0 | 1087 | NA | NA | NA | 0 | 1 | AT: 325; AT: 160; CH: 4873; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1030 | 5658 |  |  | 4571 |  |  | -1790 | -1790 | -785 | Critical Branch | Validation phase | 0 | 1087 | NA | NA | NA | 0 | 1 | AT: 325; AT: 160; CH: 4873; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1130 | 5658 |  |  | 4571 |  |  | -1790 | -1790 | -785 | Critical Branch | Validation phase | 0 | 1087 | NA | NA | NA | 0 | 1 | AT: 325; AT: 160; CH: 4873; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1230 | 6470 |  |  | 4989 |  |  | -3546 | -3546 | -2047 | Critical Branch | Validation phase | 0 | 1481 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160; CH: 5504; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1330 | 6470 |  |  | 4989 |  |  | -3546 | -3546 | -2047 | Critical Branch | Validation phase | 0 | 1481 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160; CH: 5504; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1430 | 6470 |  |  | 4989 |  |  | -3546 | -3546 | -2047 | Critical Branch | Validation phase | 0 | 1481 | NA | NA | NA | 0 | 1 | AT: 377; AT: 160; CH: 5504; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1530 |  | 6609 | 724 |  | 4600 | 594 | -2817 | -2817 | 0 | Critical Branch | Validation phase | 0 | NA | 2009 | 130 | 2139 | 2817 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 5665; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1630 |  | 6609 | 724 |  | 4600 | 594 | -2817 | -2817 | 0 | Critical Branch | Validation phase | 0 | NA | 2009 | 130 | 2139 | 2817 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 5665; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1730 |  | 6609 | 724 |  | 4600 | 594 | -2817 | -2817 | 0 | Critical Branch | Validation phase | 0 | NA | 2009 | 130 | 2139 | 2817 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 5665; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1830 |  | 6555 | 704 |  | 4609 | 581 | -4187 | -4187 | 0 | Critical Branch | Validation phase | 0 | NA | 1946 | 123 | 2069 | 4187 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border; CH: 5675; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 1930 |  | 6555 | 704 |  | 4609 | 581 | -4187 | -4187 | 0 | Critical Branch | Validation phase | 0 | NA | 1946 | 123 | 2069 | 4187 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border; CH: 5675; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 2030 |  | 6555 | 704 |  | 4609 | 581 | -4187 | -4187 | 0 | Critical Branch | Validation phase | 0 | NA | 1946 | 123 | 2069 | 4187 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border; CH: 5675; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 2130 |  | 7308 | 811 |  | 5165 | 701 | -5260 | -5260 | 0 | Critical Branch | Validation phase | 0 | NA | 2143 | 110 | 2253 | 5260 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 6611; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 2230 |  | 7308 | 811 |  | 5165 | 701 | -5260 | -5260 | 0 | Critical Branch | Validation phase | 0 | NA | 2143 | 110 | 2253 | 5260 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 6611; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250815 | August | 2330 |  | 7308 | 811 |  | 5165 | 701 | -5260 | -5260 | 0 | Critical Branch | Validation phase | 0 | NA | 2143 | 110 | 2253 | 5260 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 6601; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 1200; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 1017; IT: Outage of HVDC FIL link 1 and link 2
20250816 | August | 0030 | 7253 |  |  | 6018 |  |  | -3699 | -3699 | -2464 | Critical Branch | Validation phase | 0 | 1235 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5768; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0130 | 7253 |  |  | 6018 |  |  | -3699 | -3699 | -2464 | Critical Branch | Validation phase | 0 | 1235 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5768; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0230 | 7253 |  |  | 6018 |  |  | -3699 | -3699 | -2464 | Critical Branch | Validation phase | 0 | 1235 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5768; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0330 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 0 | 1269 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5491; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0430 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 0 | 1269 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5491; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0530 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 0 | 1269 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5491; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0630 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 0 | 1269 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5491; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0730 | 7212 |  |  | 6010 |  |  | -3565 | -3565 | -2363 | Critical Branch | Validation phase | 0 | 1202 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 5760; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0830 | 7212 |  |  | 6010 |  |  | -3565 | -3565 | -2363 | Critical Branch | Validation phase | 0 | 1202 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 5760; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0930 |  | 6932 | 838 |  | 6567 | 801 | -2566 | -2566 | 0 | Critical Branch | Validation phase | 0 | NA | 365 | 37 | 402 | 2566 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 131; AT: Reduction because NTC over thermal limit on border; CH: 6915; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1030 |  | 6932 | 838 |  | 6567 | 801 | -2566 | -2566 | 0 | Critical Branch | Validation phase | 0 | NA | 365 | 37 | 402 | 2566 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 131; AT: Reduction because NTC over thermal limit on border; CH: 6915; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1130 |  | 6932 | 838 |  | 6567 | 801 | -2566 | -2566 | 0 | Critical Branch | Validation phase | 0 | NA | 365 | 37 | 402 | 2566 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 131; AT: Reduction because NTC over thermal limit on border; CH: 6915; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1230 | 7050 |  |  | 6615 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 435 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1330 | 7050 |  |  | 6615 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 435 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1430 | 7050 |  |  | 6615 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 435 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1530 |  | 7078 | 755 |  | 6476 | 693 | -3843 | -3843 | 0 | Critical Branch | Validation phase | 0 | NA | 602 | 62 | 664 | 3843 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border; CH: 6829; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1630 |  | 7078 | 755 |  | 6476 | 693 | -3843 | -3843 | 0 | Critical Branch | Validation phase | 0 | NA | 602 | 62 | 664 | 3843 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border; CH: 6829; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1730 |  | 7078 | 755 |  | 6476 | 693 | -3843 | -3843 | 0 | Critical Branch | Validation phase | 0 | NA | 602 | 62 | 664 | 3843 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border; CH: 6829; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1830 |  | 7174 | 755 |  | 6515 | 687 | -4939 | -4939 | 0 | Critical Branch | Validation phase | 0 | NA | 659 | 68 | 727 | 4939 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border; CH: 6879; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1930 |  | 7174 | 755 |  | 6515 | 687 | -4939 | -4939 | 0 | Critical Branch | Validation phase | 0 | NA | 659 | 68 | 727 | 4939 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border; CH: 6879; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2030 |  | 7174 | 755 |  | 6515 | 687 | -4939 | -4939 | 0 | Critical Branch | Validation phase | 0 | NA | 659 | 68 | 727 | 4939 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border; CH: 6879; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2130 | 7669 |  |  | 6602 |  |  | -1688 | -1688 | -621 | Critical Branch | Validation phase | 0 | 1067 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6352; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2230 | 7669 |  |  | 6602 |  |  | -1688 | -1688 | -621 | Critical Branch | Validation phase | 0 | 1067 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6352; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2330 | 7069 |  |  | 6002 |  |  | -1087 | -1087 | -20 | Critical Branch | Validation phase | 0 | 1067 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5752; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250817 | August | 0030 | 7567 |  |  | 7050 |  |  | -1267 | -1267 | -756 | Critical Branch | Validation phase | 0 | 517 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6828; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0130 | 7567 |  |  | 7050 |  |  | -1267 | -1267 | -756 | Critical Branch | Validation phase | 0 | 517 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6828; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0230 | 7567 |  |  | 7050 |  |  | -1267 | -1267 | -756 | Critical Branch | Validation phase | 0 | 517 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6828; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0330 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250817 | August | 0430 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250817 | August | 0530 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250817 | August | 0630 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250817 | August | 0730 |  | 7117 | 1242 |  | 6689 | 1169 | -4520 | -4520 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 428 | 73 | 501 | 4520 | 1 | AT: 227; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0830 |  | 7117 | 1242 |  | 6689 | 1169 | -4520 | -4520 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 428 | 73 | 501 | 4520 | 1 | AT: 227; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0930 |  | 7078 | 844 |  | 6818 | 844 | -1324 | -1324 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 260 | 0 | 260 | 1324 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1030 |  | 7078 | 844 |  | 6818 | 844 | -1324 | -1324 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 260 | 0 | 260 | 1324 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1130 |  | 7078 | 844 |  | 6818 | 844 | -1324 | -1324 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 260 | 0 | 260 | 1324 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1230 |  | 6617 | 718 |  | 6361 | 691 | -295 | -295 | 0 | Critical Branch | Validation phase | 0 | NA | 256 | 27 | 283 | 295 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 6631; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250817 | August | 1330 |  | 6617 | 718 |  | 6361 | 691 | -295 | -295 | 0 | Critical Branch | Validation phase | 0 | NA | 256 | 27 | 283 | 295 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 6631; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250817 | August | 1430 |  | 6617 | 718 |  | 6361 | 691 | -295 | -295 | 0 | Critical Branch | Validation phase | 0 | NA | 256 | 27 | 283 | 295 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; CH: 6631; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250817 | August | 1530 |  | 7240 | 831 |  | 6858 | 821 | -5 | -5 | 0 | Critical Branch | Validation phase | 0 | NA | 382 | 10 | 392 | 5 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border; CH: 7293; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1630 |  | 7240 | 831 |  | 6858 | 821 | -5 | -5 | 0 | Critical Branch | Validation phase | 0 | NA | 382 | 10 | 392 | 5 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border; CH: 7293; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1730 |  | 7240 | 831 |  | 6858 | 821 | -5 | -5 | 0 | Critical Branch | Validation phase | 0 | NA | 382 | 10 | 392 | 5 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border; CH: 7293; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1830 |  | 7083 | 791 |  | 6820 | 791 | -2468 | -2468 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 263 | 0 | 263 | 2468 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1930 |  | 7083 | 791 |  | 6820 | 791 | -2468 | -2468 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 263 | 0 | 263 | 2468 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2030 |  | 7083 | 791 |  | 6820 | 791 | -2468 | -2468 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 263 | 0 | 263 | 2468 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2130 |  | 7143 | 818 |  | 6687 | 786 | -5023 | -5023 | 0 | Critical Branch | Validation phase | 0 | NA | 456 | 32 | 488 | 5023 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 7159; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2230 |  | 7143 | 818 |  | 6687 | 786 | -5023 | -5023 | 0 | Critical Branch | Validation phase | 0 | NA | 456 | 32 | 488 | 5023 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 7159; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2330 |  | 7143 | 818 |  | 6687 | 786 | -5023 | -5023 | 0 | Critical Branch | Validation phase | 0 | NA | 456 | 32 | 488 | 5023 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 7159; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0030 |  | 6822 | 1152 |  | 6055 | 1011 | -3312 | -3312 | 0 | Critical Branch | Validation phase | 0 | NA | 767 | 141 | 908 | 3312 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0130 |  | 6822 | 1152 |  | 6055 | 1011 | -3312 | -3312 | 0 | Critical Branch | Validation phase | 0 | NA | 767 | 141 | 908 | 3312 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0230 |  | 6822 | 1152 |  | 6055 | 1011 | -3312 | -3312 | 0 | Critical Branch | Validation phase | 0 | NA | 767 | 141 | 908 | 3312 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0330 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | 0 | NA | 358 | 98 | 456 | 1793 | 1 | AT: 203; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0430 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | 0 | NA | 358 | 98 | 456 | 1793 | 1 | AT: 203; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0530 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | 0 | NA | 358 | 98 | 456 | 1793 | 1 | AT: 203; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0630 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | 0 | NA | 358 | 98 | 456 | 1793 | 1 | AT: 203; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0730 |  | 6190 | 905 |  | 6047 | 879 | -2088 | -2088 | 0 | Critical Branch | Validation phase | 0 | NA | 143 | 26 | 169 | 2088 | 1 | AT: 183; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0830 |  | 6190 | 905 |  | 6047 | 879 | -2088 | -2088 | 0 | Critical Branch | Validation phase | 0 | NA | 143 | 26 | 169 | 2088 | 1 | AT: 183; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0930 | 5480 |  |  | 5250 |  |  | -4445 | -4445 | -4215 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250818 | August | 1030 | 5480 |  |  | 5250 |  |  | -4445 | -4445 | -4215 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250818 | August | 1130 | 5480 |  |  | 5250 |  |  | -4445 | -4445 | -4215 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250818 | August | 1230 | 6771 |  |  | 6141 |  |  | 95 | 95 | 630 | Adjustment reached | Validation phase | 0 | 630 | NA | NA | NA | 1165 | 1 | AT: 372; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250818 | August | 1330 | 6771 |  |  | 6141 |  |  | 95 | 95 | 630 | Adjustment reached | Validation phase | 0 | 630 | NA | NA | NA | 1165 | 1 | AT: 372; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250818 | August | 1430 | 6771 |  |  | 6141 |  |  | 95 | 95 | 630 | Adjustment reached | Validation phase | 0 | 630 | NA | NA | NA | 1165 | 1 | AT: 372; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250818 | August | 1530 |  | 7097 | 696 |  | 6104 | 603 | -4090 | -4090 | 0 | Critical Branch | Validation phase | 0 | NA | 993 | 93 | 1086 | 4090 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1630 |  | 7097 | 696 |  | 6104 | 603 | -4090 | -4090 | 0 | Critical Branch | Validation phase | 0 | NA | 993 | 93 | 1086 | 4090 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1730 |  | 7097 | 696 |  | 6104 | 603 | -4090 | -4090 | 0 | Critical Branch | Validation phase | 0 | NA | 993 | 93 | 1086 | 4090 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 138; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1830 |  | 6378 | 783 |  | 6047 | 746 | -4243 | -4243 | 0 | Critical Branch | Validation phase | 0 | NA | 331 | 37 | 368 | 4243 | 1 | AT: 227; AT: 131; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1930 |  | 6378 | 783 |  | 6047 | 746 | -4243 | -4243 | 0 | Critical Branch | Validation phase | 0 | NA | 331 | 37 | 368 | 4243 | 1 | AT: 227; AT: 131; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2030 |  | 6378 | 783 |  | 6047 | 746 | -4243 | -4243 | 0 | Critical Branch | Validation phase | 0 | NA | 331 | 37 | 368 | 4243 | 1 | AT: 227; AT: 131; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2130 |  | 6778 | 890 |  | 6047 | 804 | -4188 | -4188 | 0 | Critical Branch | Validation phase | 0 | NA | 731 | 86 | 817 | 4188 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2230 |  | 6778 | 890 |  | 6047 | 804 | -4188 | -4188 | 0 | Critical Branch | Validation phase | 0 | NA | 731 | 86 | 817 | 4188 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2330 |  | 6201 | 935 |  | 6055 | 910 | -3558 | -3558 | 0 | Critical Branch | Validation phase | 0 | NA | 146 | 25 | 171 | 3558 | 1 | AT: 196; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0030 |  | 6910 | 1072 |  | 6055 | 937 | -3443 | -3443 | 0 | Critical Branch | Validation phase | 0 | NA | 855 | 135 | 990 | 3443 | 1 | AT: 220; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0130 |  | 6910 | 1072 |  | 6055 | 937 | -3443 | -3443 | 0 | Critical Branch | Validation phase | 0 | NA | 855 | 135 | 990 | 3443 | 1 | AT: 220; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0230 |  | 6910 | 1072 |  | 6055 | 937 | -3443 | -3443 | 0 | Critical Branch | Validation phase | 0 | NA | 855 | 135 | 990 | 3443 | 1 | AT: 220; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0330 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | 0 | NA | 970 | 157 | 1127 | 2278 | 1 | AT: 224; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0430 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | 0 | NA | 970 | 157 | 1127 | 2278 | 1 | AT: 224; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0530 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | 0 | NA | 970 | 157 | 1127 | 2278 | 1 | AT: 224; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0630 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | 0 | NA | 970 | 157 | 1127 | 2278 | 1 | AT: 224; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0730 |  | 6545 | 852 |  | 6047 | 794 | -4066 | -4066 | 0 | Critical Branch | Validation phase | 0 | NA | 498 | 58 | 556 | 4066 | 1 | AT: 194; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0830 |  | 6545 | 852 |  | 6047 | 794 | -4066 | -4066 | 0 | Critical Branch | Validation phase | 0 | NA | 498 | 58 | 556 | 4066 | 1 | AT: 192; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0930 | 5480 |  |  | 5480 |  |  | -2326 | -2326 | -2326 | TTC Selection - LTTC | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1030 | 5480 |  |  | 5480 |  |  | -2326 | -2326 | -2326 | TTC Selection - LTTC | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1130 | 5480 |  |  | 5480 |  |  | -2326 | -2326 | -2326 | TTC Selection - LTTC | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1230 | 6312 |  |  | 6141 |  |  | -369 | -369 | -198 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 0 | 1 | AT: 345; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1330 | 6312 |  |  | 6141 |  |  | -369 | -369 | -198 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 0 | 1 | AT: 345; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1430 | 6312 |  |  | 6141 |  |  | -369 | -369 | -198 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 0 | 1 | AT: 345; AT: 140; CH: 5891; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1530 |  | 6221 | 631 |  | 6104 | 620 | -1843 | -1843 | 0 | Critical Branch | Validation phase | 0 | NA | 117 | 11 | 128 | 1843 | 1 | AT: 369; AT: 140; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1630 |  | 6221 | 631 |  | 6104 | 620 | -1843 | -1843 | 0 | Critical Branch | Validation phase | 0 | NA | 117 | 11 | 128 | 1843 | 1 | AT: 369; AT: 140; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1730 |  | 6221 | 631 |  | 6104 | 620 | -1843 | -1843 | 0 | Critical Branch | Validation phase | 0 | NA | 117 | 11 | 128 | 1843 | 1 | AT: 369; AT: 140; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1830 |  | 5441 | 667 |  | 5441 | 666 | -3463 | -3463 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 1 | 1 | 3463 | 1 | AT: 338; AT: 110; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1930 |  | 5441 | 667 |  | 5441 | 666 | -3463 | -3463 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 1 | 1 | 3463 | 1 | AT: 338; AT: 110; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 2030 |  | 5441 | 667 |  | 5441 | 666 | -3463 | -3463 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 1 | 1 | 3463 | 1 | AT: 338; AT: 110; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 2130 |  | 6066 | 744 |  | 6042 | 743 | -3398 | -3398 | 0 | Critical Branch | Validation phase | 0 | NA | 24 | 1 | 25 | 3398 | 1 | AT: 243; AT: 124; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 2230 |  | 6066 | 744 |  | 6042 | 743 | -3398 | -3398 | 0 | Critical Branch | Validation phase | 0 | NA | 24 | 1 | 25 | 3398 | 1 | AT: 243; AT: 124; CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 2330 |  | 5516 | 789 |  | 5516 | 789 | -2785 | -2785 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 0 | 0 | 2785 | 1 | AT: 227; AT: 143; CH: 6800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250820 | August | 0030 | 6695 |  |  | 6267 |  |  | -2276 | -2276 | -1848 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 392; AT: 160; CH: 6017; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0130 | 6695 |  |  | 6267 |  |  | -2276 | -2276 | -1848 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 392; AT: 160; CH: 6017; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0230 | 6695 |  |  | 6267 |  |  | -2276 | -2276 | -1848 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 392; AT: 160; CH: 6017; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0330 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | 0 | NA | 190 | 20 | 210 | 2788 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 6661; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0430 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | 0 | NA | 190 | 20 | 210 | 2788 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 6661; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0530 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | 0 | NA | 190 | 20 | 210 | 2788 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 6661; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0630 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | 0 | NA | 190 | 20 | 210 | 2788 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border; CH: 6661; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0730 | 6735 |  |  | 6314 |  |  | -2984 | -2984 | -2563 | Critical Branch | Validation phase | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 370; AT: 140; CH: 6064; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0830 | 6735 |  |  | 6314 |  |  | -2984 | -2984 | -2563 | Critical Branch | Validation phase | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 370; AT: 140; CH: 6064; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0930 | 5480 |  |  | 5250 |  |  | -5112 | -5112 | -4882 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1030 | 5480 |  |  | 5250 |  |  | -5112 | -5112 | -4882 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1130 | 5480 |  |  | 5250 |  |  | -5112 | -5112 | -4882 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1230 | 5480 |  |  | 5250 |  |  | -5207 | -5207 | -4977 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1330 | 5480 |  |  | 5250 |  |  | -5207 | -5207 | -4977 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1430 | 5480 |  |  | 5250 |  |  | -5207 | -5207 | -4977 | TTC Selection - LTTC | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 296; AT: 140; SI: 5000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1530 | 7355 |  |  | 6750 |  |  | -1555 | -1555 | -950 | Critical Branch | Validation phase | 0 | 605 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140; CH: 6537; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1630 | 7355 |  |  | 6787 |  |  | -1555 | -1555 | -987 | Critical Branch | Validation phase | 0 | 568 | NA | NA | NA | 0 | 1 | AT: 407; AT: 140; CH: 6537; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1730 | 7355 |  |  | 6787 |  |  | -1555 | -1555 | -987 | Critical Branch | Validation phase | 0 | 568 | NA | NA | NA | 0 | 1 | AT: 407; AT: 140; CH: 6537; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1830 |  | 6848 | 649 |  | 6545 | 628 | -2181 | -2181 | 0 | Critical Branch | Validation phase | 0 | NA | 303 | 21 | 324 | 2181 | 1 | AT: 410; AT: 140; CH: 6883; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1930 |  | 6848 | 649 |  | 6545 | 628 | -2181 | -2181 | 0 | Critical Branch | Validation phase | 0 | NA | 303 | 21 | 324 | 2181 | 1 | AT: 410; AT: 140; CH: 6883; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2030 |  | 6848 | 649 |  | 6545 | 628 | -2181 | -2181 | 0 | Critical Branch | Validation phase | 0 | NA | 303 | 21 | 324 | 2181 | 1 | AT: 410; AT: 140; CH: 6883; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2130 |  | 6553 | 614 |  | 6384 | 598 | -1908 | -1908 | 0 | Critical Branch | Validation phase | 0 | NA | 169 | 16 | 185 | 1908 | 1 | AT: 391; AT: 140; CH: 6655; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2230 |  | 6553 | 614 |  | 6384 | 598 | -1908 | -1908 | 0 | Critical Branch | Validation phase | 0 | NA | 169 | 16 | 185 | 1908 | 1 | AT: 391; AT: 140; CH: 6655; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2200; FR: Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2330 |  | 5993 | 639 |  | 5823 | 623 | -1285 | -1285 | 0 | Critical Branch | Validation phase | 0 | NA | 170 | 16 | 186 | 1285 | 1 | AT: 379; AT: 160; CH: 6054; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250821 | August | 0030 | 6624 |  |  | 5773 |  |  | -2108 | -2108 | -1257 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | CH: 5523; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 0130 | 6624 |  |  | 5773 |  |  | -2108 | -2108 | -1257 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | CH: 5523; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 0230 | 6624 |  |  | 5773 |  |  | -2108 | -2108 | -1257 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | CH: 5523; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 0330 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | CH: 6534; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0430 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | CH: 6534; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0530 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | CH: 6534; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0630 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 0 | 238 | NA | NA | NA | 0 | 1 | CH: 6534; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0730 | 5685 |  |  | 5493 |  |  | -1452 | -1452 | -1260 | Critical Branch | Validation phase | 0 | 192 | NA | NA | NA | 0 | 1 | CH: 5243; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 0830 | 5685 |  |  | 4750 |  |  | -1452 | -1452 | -517 | Critical Branch | Validation phase | 0 | 935 | NA | NA | NA | 0 | 1 | CH: 5243; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 0930 | 5708 |  |  | 4750 |  |  | -1719 | -1719 | -761 | Critical Branch | Validation phase | 0 | 958 | NA | NA | NA | 0 | 1 | CH: 4859; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1030 | 5708 |  |  | 4750 |  |  | -1719 | -1719 | -761 | Critical Branch | Validation phase | 0 | 958 | NA | NA | NA | 0 | 1 | CH: 4859; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1130 | 5708 |  |  | 4750 |  |  | -1719 | -1719 | -761 | Critical Branch | Validation phase | 0 | 958 | NA | NA | NA | 0 | 1 | CH: 4859; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1230 | 6277 |  |  | 4750 |  |  | -1119 | -1119 | 408 | Critical Branch | Validation phase | 0 | 1527 | NA | NA | NA | 1935 | 1 | CH: 5479; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1330 | 6277 |  |  | 4750 |  |  | -1119 | -1119 | 408 | Critical Branch | Validation phase | 0 | 1527 | NA | NA | NA | 1935 | 1 | CH: 5479; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1430 | 6277 |  |  | 4750 |  |  | -1119 | -1119 | 408 | Critical Branch | Validation phase | 0 | 1527 | NA | NA | NA | 1935 | 1 | CH: 5479; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1530 | 5673 |  |  | 4937 |  |  | -1328 | -1328 | -592 | Critical Branch | Validation phase | 0 | 736 | NA | NA | NA | 0 | 1 | CH: 4687; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 1630 | 5673 |  |  | 4937 |  |  | -1328 | -1328 | -592 | Critical Branch | Validation phase | 0 | 736 | NA | NA | NA | 0 | 1 | CH: 4687; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 1730 | 5673 |  |  | 4937 |  |  | -1328 | -1328 | -592 | Critical Branch | Validation phase | 0 | 736 | NA | NA | NA | 0 | 1 | CH: 4687; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 1830 |  | 5741 | 538 |  | 5590 | 524 | -2833 | -2833 | 0 | Critical Branch | Validation phase | 0 | NA | 151 | 14 | 165 | 2833 | 1 | CH: 5791; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 1930 |  | 5741 | 538 |  | 5590 | 524 | -2833 | -2833 | 0 | Critical Branch | Validation phase | 0 | NA | 151 | 14 | 165 | 2833 | 1 | CH: 5791; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 2030 |  | 5741 | 538 |  | 5590 | 524 | -2833 | -2833 | 0 | Critical Branch | Validation phase | 0 | NA | 151 | 14 | 165 | 2833 | 1 | CH: 5791; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 2130 | 5480 |  |  | 5480 |  |  | -1431 | -1431 | -1431 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250821 | August | 2230 | 5480 |  |  | 5480 |  |  | -1431 | -1431 | -1431 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250821 | August | 2330 | 4880 |  |  | 4880 |  |  | -824 | -824 | -824 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0030 | 5726 |  |  | 5726 |  |  | -1710 | -1710 | -1710 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0130 | 5726 |  |  | 5726 |  |  | -1710 | -1710 | -1710 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0230 | 5726 |  |  | 5726 |  |  | -1710 | -1710 | -1710 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0330 | 5930 |  |  | 5930 |  |  | -1807 | -1807 | -1807 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0430 | 5930 |  |  | 5930 |  |  | -1807 | -1807 | -1807 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0530 | 5930 |  |  | 5930 |  |  | -1807 | -1807 | -1807 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0630 | 5930 |  |  | 5930 |  |  | -1807 | -1807 | -1807 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250822 | August | 0730 | 5480 |  |  | 5288 |  |  | -2127 | -2127 | -1935 | TTC Selection - LTTC | Validation phase | 0 | 192 | NA | NA | NA | 0 | 1 | CH: 5038; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250822 | August | 0830 | 5480 |  |  | 4750 |  |  | -2127 | -2127 | -1397 | TTC Selection - LTTC | Validation phase | 0 | 730 | NA | NA | NA | 0 | 1 | CH: 5038; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 0930 | 5480 |  |  | 4750 |  |  | -2402 | -2402 | -1672 | TTC Selection - LTTC | Validation phase | 0 | 730 | NA | NA | NA | 0 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1030 | 5480 |  |  | 4750 |  |  | -2402 | -2402 | -1672 | TTC Selection - LTTC | Validation phase | 0 | 730 | NA | NA | NA | 0 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1130 | 5480 |  |  | 4750 |  |  | -2402 | -2402 | -1672 | TTC Selection - LTTC | Validation phase | 0 | 730 | NA | NA | NA | 0 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1230 | 6725 |  |  | 4750 |  |  | -832 | -832 | 1143 | Critical Branch | Validation phase | 0 | 1975 | NA | NA | NA | 3118 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1330 | 6725 |  |  | 4750 |  |  | -832 | -832 | 1143 | Critical Branch | Validation phase | 0 | 1975 | NA | NA | NA | 3118 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1430 | 6725 |  |  | 4750 |  |  | -832 | -832 | 1143 | Critical Branch | Validation phase | 0 | 1975 | NA | NA | NA | 3118 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1530 |  | 6081 | 701 |  | 5998 | 701 | -852 | -852 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 83 | 0 | 83 | 852 | 1
20250822 | August | 1630 |  | 6081 | 701 |  | 6081 | 701 | -852 | -852 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 852 | 0
20250822 | August | 1730 |  | 6081 | 701 |  | 6081 | 701 | -852 | -852 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 852 | 0
20250822 | August | 1830 |  | 6428 | 602 |  | 6428 | 602 | -3256 | -3256 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3256 | 0
20250822 | August | 1930 |  | 6428 | 602 |  | 6428 | 602 | -3256 | -3256 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3256 | 0
20250822 | August | 2030 |  | 6428 | 602 |  | 6428 | 602 | -3256 | -3256 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3256 | 0
20250822 | August | 2130 | 7478 |  |  | 6645 |  |  | -3358 | -3358 | -2525 | Critical Branch | Validation phase | 0 | 833 | NA | NA | NA | 0 | 1 | CH: 6395; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250822 | August | 2230 | 7478 |  |  | 6645 |  |  | -3358 | -3358 | -2525 | Critical Branch | Validation phase | 0 | 833 | NA | NA | NA | 0 | 1 | CH: 6395; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250822 | August | 2330 | 6878 |  |  | 6045 |  |  | -2751 | -2751 | -1918 | Critical Branch | Validation phase | 0 | 833 | NA | NA | NA | 0 | 1 | CH: 5795; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250823 | August | 0030 | 8919 |  |  | 7304 |  |  | -4484 | -4484 | -2875 | Critical Branch | Validation phase | 0 | 1615 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7071; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0130 | 8919 |  |  | 7304 |  |  | -4484 | -4484 | -2875 | Critical Branch | Validation phase | 0 | 1615 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7071; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0230 | 8919 |  |  | 7304 |  |  | -4484 | -4484 | -2875 | Critical Branch | Validation phase | 0 | 1615 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7071; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0330 | 8576 |  |  | 6938 |  |  | -4672 | -4672 | -3034 | Critical Branch | Validation phase | 0 | 1638 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6688; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0430 | 8576 |  |  | 6938 |  |  | -4672 | -4672 | -3034 | Critical Branch | Validation phase | 0 | 1638 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6688; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0530 | 8576 |  |  | 6938 |  |  | -4672 | -4672 | -3034 | Critical Branch | Validation phase | 0 | 1638 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6688; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0630 | 7476 |  |  | 5838 |  |  | -3533 | -3533 | -1895 | Critical Branch | Validation phase | 0 | 1638 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 5588; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0730 | 6920 |  |  | 6303 |  |  | -3002 | -3002 | -2385 | Critical Branch | Validation phase | 0 | 617 | NA | NA | NA | 0 | 1 | AT: 366; AT: 140; CH: 6053; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 0830 | 6920 |  |  | 6303 |  |  | -3002 | -3002 | -2385 | Critical Branch | Validation phase | 0 | 617 | NA | NA | NA | 0 | 1 | AT: 366; AT: 140; CH: 6053; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 0930 | 6808 |  |  | 6069 |  |  | -3181 | -3181 | -2442 | Critical Branch | Validation phase | 0 | 739 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 5819; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1030 | 6808 |  |  | 6069 |  |  | -3181 | -3181 | -2442 | Critical Branch | Validation phase | 0 | 739 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 5819; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1130 | 6808 |  |  | 6069 |  |  | -3181 | -3181 | -2442 | Critical Branch | Validation phase | 0 | 739 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 5819; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1230 | 6568 |  |  | 5924 |  |  | -1021 | -1021 | -377 | Critical Branch | Validation phase | 0 | 644 | NA | NA | NA | 0 | 1 | AT: 346; AT: 140; CH: 5674; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1330 | 6568 |  |  | 5924 |  |  | -1021 | -1021 | -377 | Critical Branch | Validation phase | 0 | 644 | NA | NA | NA | 0 | 1 | AT: 346; AT: 140; CH: 5674; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1430 | 6568 |  |  | 5924 |  |  | -1021 | -1021 | -377 | Critical Branch | Validation phase | 0 | 644 | NA | NA | NA | 0 | 1 | AT: 346; AT: 140; CH: 5674; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1530 | 7677 |  |  | 6436 |  |  | -3344 | -3344 | -2103 | Critical Branch | Validation phase | 0 | 1241 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6186; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1630 | 7677 |  |  | 6436 |  |  | -3344 | -3344 | -2103 | Critical Branch | Validation phase | 0 | 1241 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6186; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1730 | 8577 |  |  | 7336 |  |  | -4328 | -4328 | -3087 | Critical Branch | Validation phase | 0 | 1241 | NA | NA | NA | 0 | 1 | AT: 411; AT: 140; CH: 7086; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1830 | 8562 |  |  | 8561 |  |  | -4536 | -4536 | -4536 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140
20250823 | August | 1930 | 8562 |  |  | 8561 |  |  | -4536 | -4536 | -4536 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140
20250823 | August | 2030 | 8562 |  |  | 8561 |  |  | -4536 | -4536 | -4536 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140
20250823 | August | 2130 | 9009 |  |  | 8882 |  |  | -4949 | -4949 | -4822 | Critical Branch | Validation phase | 0 | 127 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 8632; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250823 | August | 2230 | 9009 |  |  | 8882 |  |  | -4949 | -4949 | -4822 | Critical Branch | Validation phase | 0 | 127 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 8632; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250823 | August | 2330 | 8409 |  |  | 8282 |  |  | -4342 | -4342 | -4215 | Critical Branch | Validation phase | 0 | 127 | NA | NA | NA | 0 | 1 | AT: 412; AT: 160; CH: 8032; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 0030 | 9262 |  |  | 8676 |  |  | -5051 | -5051 | -4469 | Critical Branch | Validation phase | 0 | 586 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8438; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0130 | 9262 |  |  | 8676 |  |  | -5051 | -5051 | -4469 | Critical Branch | Validation phase | 0 | 586 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8438; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0230 | 9262 |  |  | 8676 |  |  | -5051 | -5051 | -4469 | Critical Branch | Validation phase | 0 | 586 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8438; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0330 | 9159 |  |  | 8589 |  |  | -4980 | -4980 | -4413 | Critical Branch | Validation phase | 0 | 570 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8347; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0430 | 9159 |  |  | 8589 |  |  | -4980 | -4980 | -4413 | Critical Branch | Validation phase | 0 | 570 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8347; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0530 | 9159 |  |  | 8589 |  |  | -4980 | -4980 | -4413 | Critical Branch | Validation phase | 0 | 570 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8347; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0630 | 8959 |  |  | 8389 |  |  | -4764 | -4764 | -4197 | Critical Branch | Validation phase | 0 | 570 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8147; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0730 | 8117 |  |  | 7991 |  |  | -4154 | -4154 | -4028 | Critical Branch | Validation phase | 0 | 126 | NA | NA | NA | 0 | 1 | AT: 407; AT: 160; CH: 7741; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 0830 | 8117 |  |  | 7991 |  |  | -4154 | -4154 | -4028 | Critical Branch | Validation phase | 0 | 126 | NA | NA | NA | 0 | 1 | AT: 407; AT: 160; CH: 7741; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 0930 | 7688 |  |  | 7640 |  |  | -3833 | -3833 | -3785 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | AT: 384; AT: 160; CH: 7390; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1030 | 7688 |  |  | 7640 |  |  | -3833 | -3833 | -3785 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | AT: 384; AT: 160; CH: 7390; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1130 | 7688 |  |  | 7640 |  |  | -3833 | -3833 | -3785 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | AT: 384; AT: 160; CH: 7390; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1230 | 6808 |  |  | 6547 |  |  | -3150 | -3150 | -2889 | Critical Branch | Validation phase | 0 | 261 | NA | NA | NA | 0 | 1 | AT: 337; AT: 160; CH: 6297; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1330 | 6808 |  |  | 6547 |  |  | -3150 | -3150 | -2889 | Critical Branch | Validation phase | 0 | 261 | NA | NA | NA | 0 | 1 | AT: 337; AT: 160; CH: 6297; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1430 | 6808 |  |  | 6547 |  |  | -3150 | -3150 | -2889 | Critical Branch | Validation phase | 0 | 261 | NA | NA | NA | 0 | 1 | AT: 337; AT: 160; CH: 6297; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1530 | 7805 |  |  | 7522 |  |  | -3727 | -3727 | -3444 | Critical Branch | Validation phase | 0 | 283 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160; CH: 7272; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1630 | 7805 |  |  | 7522 |  |  | -3727 | -3727 | -3444 | Critical Branch | Validation phase | 0 | 283 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160; CH: 7272; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1730 | 7805 |  |  | 7522 |  |  | -3727 | -3727 | -3444 | Critical Branch | Validation phase | 0 | 283 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160; CH: 7272; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1830 | 7710 |  |  | 7662 |  |  | -4751 | -4751 | -4703 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | AT: 376; AT: 160; CH: 7412; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 1930 | 7710 |  |  | 7662 |  |  | -4751 | -4751 | -4703 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | AT: 376; AT: 160; CH: 7412; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2030 | 7710 |  |  | 7662 |  |  | -4751 | -4751 | -4703 | Critical Branch | Validation phase | 0 | 48 | NA | NA | NA | 0 | 1 | AT: 376; AT: 160; CH: 7412; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2130 | 7996 |  |  | 7943 |  |  | -4606 | -4606 | -4553 | Critical Branch | Validation phase | 0 | 53 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160; CH: 7693; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2230 | 7996 |  |  | 7943 |  |  | -4606 | -4606 | -4553 | Critical Branch | Validation phase | 0 | 53 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160; CH: 7693; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2330 | 7996 |  |  | 7943 |  |  | -4606 | -4606 | -4553 | Critical Branch | Validation phase | 0 | 53 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160; CH: 7693; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250825 | August | 0030 | 8711 |  |  | 7857 |  |  | -4060 | -4060 | -3206 | Critical Branch | Validation phase | 0 | 854 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7607; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250825 | August | 0130 | 8711 |  |  | 7857 |  |  | -4060 | -4060 | -3206 | Critical Branch | Validation phase | 0 | 854 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7607; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250825 | August | 0230 | 8711 |  |  | 7857 |  |  | -4060 | -4060 | -3206 | Critical Branch | Validation phase | 0 | 854 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7607; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250825 | August | 0330 | 8256 |  |  | 7540 |  |  | -2102 | -2102 | -1386 | Critical Branch | Validation phase | 0 | 716 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160; CH: 7290; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0430 | 8256 |  |  | 7540 |  |  | -2102 | -2102 | -1386 | Critical Branch | Validation phase | 0 | 716 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160; CH: 7290; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0530 | 8256 |  |  | 7540 |  |  | -2102 | -2102 | -1386 | Critical Branch | Validation phase | 0 | 716 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160; CH: 7290; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0630 | 8056 |  |  | 6250 |  |  | -1875 | -1875 | -69 | Critical Branch | Validation phase | 0 | 1806 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160; CH: 7090; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0730 | 7367 |  |  | 4750 |  |  | -2987 | -2987 | -370 | Critical Branch | Validation phase | 0 | 2617 | NA | NA | NA | 0 | 1 | AT: 176; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 0830 | 6967 |  |  | 4750 |  |  | -2545 | -2545 | -328 | Critical Branch | Validation phase | 0 | 2217 | NA | NA | NA | 0 | 1 | AT: 174; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 0930 | 6065 |  |  | 4750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1030 | 6065 |  |  | 4750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1130 | 6065 |  |  | 4750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1230 | 6427 |  |  | 4750 |  |  | 2363 | 362 | 3678 | Minimum Margin | Validation phase | 2001 | 1677 | NA | NA | NA | 6994 | 1 | AT: 160; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1330 | 6435 |  |  | 4750 |  |  | 2363 | 370 | 3678 | Minimum Margin | Validation phase | 1993 | 1685 | NA | NA | NA | 6986 | 1 | AT: 161; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1430 | 6382 |  |  | 4750 |  |  | 2363 | 317 | 3678 | Minimum Margin | Validation phase | 2046 | 1632 | NA | NA | NA | 7039 | 1 | AT: 159; AT: 70; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1530 | 8211 |  |  | 6250 |  |  | -3275 | -3275 | -1314 | Critical Branch | Smoothing ramp | 0 | 1961 | NA | NA | NA | 0 | 1 | AT: 200; AT: 70; CH: 7522; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 1630 | 8211 |  |  | 7750 |  |  | -3275 | -3275 | -2814 | Critical Branch | Smoothing ramp | 0 | 461 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; CH: 7522; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 1730 | 8361 |  |  | 7714 |  |  | -3433 | -3433 | -2788 | Critical Branch | Validation phase | 0 | 647 | NA | NA | NA | 0 | 1 | AT: 192; AT: 70; CH: 7672; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 1830 |  | 5851 | 493 |  | 5850 | 493 | -3676 | -3676 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3676 | 1 | AT: 153; AT: 70
20250825 | August | 1930 |  | 5851 | 493 |  | 5850 | 493 | -3676 | -3676 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3676 | 1 | AT: 153; AT: 70
20250825 | August | 2030 |  | 5851 | 493 |  | 5850 | 493 | -3676 | -3676 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3676 | 1 | AT: 153; AT: 70
20250825 | August | 2130 | 6868 |  |  | 6679 |  |  | -3547 | -3547 | -3358 | Critical Branch | Validation phase | 0 | 189 | NA | NA | NA | 0 | 1 | AT: 169; AT: 70; CH: 6429; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250825 | August | 2230 | 6868 |  |  | 6679 |  |  | -3547 | -3547 | -3358 | Critical Branch | Validation phase | 0 | 189 | NA | NA | NA | 0 | 1 | AT: 169; AT: 70; CH: 6429; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250825 | August | 2330 | 6278 |  |  | 6089 |  |  | -2947 | -2947 | -2758 | Critical Branch | Validation phase | 0 | 189 | NA | NA | NA | 0 | 1 | AT: 166; AT: 70; CH: 5839; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0030 | 7216 |  |  | 6868 |  |  | -2517 | -2517 | -2169 | Critical Branch | Validation phase | 0 | 348 | NA | NA | NA | 0 | 1 | CH: 6618; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0130 | 7216 |  |  | 6868 |  |  | -2517 | -2517 | -2169 | Critical Branch | Validation phase | 0 | 348 | NA | NA | NA | 0 | 1 | CH: 6618; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0230 | 7216 |  |  | 6868 |  |  | -2517 | -2517 | -2169 | Critical Branch | Validation phase | 0 | 348 | NA | NA | NA | 0 | 1 | CH: 6618; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0330 | 7298 |  |  | 6970 |  |  | -2233 | -2233 | -1905 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | CH: 6720; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0430 | 7298 |  |  | 6970 |  |  | -2233 | -2233 | -1905 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | CH: 6720; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0530 | 7298 |  |  | 6970 |  |  | -2233 | -2233 | -1905 | Critical Branch | Validation phase | 0 | 328 | NA | NA | NA | 0 | 1 | CH: 6720; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0630 | 7098 |  |  | 6250 |  |  | -2018 | -2018 | -1170 | Critical Branch | Smoothing ramp | 0 | 848 | NA | NA | NA | 0 | 1 | CH: 6520; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0730 |  | 5900 | 52 |  | 4661 | 49 | -3133 | -3133 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 1239 | 3 | 1242 | 3133 | 1 | CH: 5485; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 0830 |  | 5900 | 52 |  | 4661 | 49 | -3133 | -3133 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 1239 | 3 | 1242 | 3133 | 1 | CH: 5485; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 0930 | 6065 |  |  | 3750 |  |  | -5589 | -5589 | -3274 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1030 | 6065 |  |  | 3750 |  |  | -5589 | -5589 | -3274 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1130 | 6065 |  |  | 3750 |  |  | -5589 | -5589 | -3274 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1230 | 6065 |  |  | 4750 |  |  | -2942 | -2942 | -1627 | TTC Selection - LTTC | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1330 | 6065 |  |  | 4750 |  |  | -2942 | -2942 | -1627 | TTC Selection - LTTC | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1430 | 6065 |  |  | 4750 |  |  | -2942 | -2942 | -1627 | TTC Selection - LTTC | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1530 | 7738 |  |  | 6250 |  |  | -2794 | -2794 | -1306 | Critical Branch | Smoothing ramp | 0 | 1488 | NA | NA | NA | 0 | 1 | CH: 7261; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 1630 | 7738 |  |  | 7511 |  |  | -2794 | -2794 | -2567 | Critical Branch | Validation phase | 0 | 227 | NA | NA | NA | 0 | 1 | CH: 7261; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 1730 | 7888 |  |  | 7661 |  |  | -2957 | -2957 | -2730 | Critical Branch | Validation phase | 0 | 227 | NA | NA | NA | 0 | 1 | CH: 7411; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 1830 |  | 5913 | 498 |  | 5913 | 498 | -4160 | -4160 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4160 | 0
20250826 | August | 1930 |  | 5913 | 498 |  | 5913 | 498 | -4160 | -4160 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4160 | 0
20250826 | August | 2030 |  | 5913 | 498 |  | 5913 | 498 | -4160 | -4160 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4160 | 0
20250826 | August | 2130 | 6864 |  |  | 6553 |  |  | -3246 | -3246 | -2935 | Critical Branch | Validation phase | 0 | 311 | NA | NA | NA | 0 | 1 | CH: 6303; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 2230 | 6864 |  |  | 6553 |  |  | -3246 | -3246 | -2935 | Critical Branch | Validation phase | 0 | 311 | NA | NA | NA | 0 | 1 | CH: 6303; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 2330 | 6274 |  |  | 5963 |  |  | -2645 | -2645 | -2334 | Critical Branch | Validation phase | 0 | 311 | NA | NA | NA | 0 | 1 | CH: 5713; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0030 | 7773 |  |  | 7674 |  |  | -2897 | -2897 | -2798 | Critical Branch | Validation phase | 0 | 99 | NA | NA | NA | 0 | 1 | CH: 7424; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0130 | 7773 |  |  | 7674 |  |  | -2897 | -2897 | -2798 | Critical Branch | Validation phase | 0 | 99 | NA | NA | NA | 0 | 1 | CH: 7424; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0230 | 7773 |  |  | 7674 |  |  | -2897 | -2897 | -2798 | Critical Branch | Validation phase | 0 | 99 | NA | NA | NA | 0 | 1 | CH: 7424; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0330 | 7788 |  |  | 7662 |  |  | -2786 | -2786 | -2660 | Critical Branch | Validation phase | 0 | 126 | NA | NA | NA | 0 | 1 | CH: 7412; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0430 | 7788 |  |  | 7662 |  |  | -2786 | -2786 | -2660 | Critical Branch | Validation phase | 0 | 126 | NA | NA | NA | 0 | 1 | CH: 7412; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0530 | 7788 |  |  | 7662 |  |  | -2786 | -2786 | -2660 | Critical Branch | Validation phase | 0 | 126 | NA | NA | NA | 0 | 1 | CH: 7412; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0630 | 7588 |  |  | 6250 |  |  | -2573 | -2573 | -1235 | Critical Branch | Smoothing ramp | 0 | 1338 | NA | NA | NA | 0 | 1 | CH: 7212; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0730 | 6753 |  |  | 4750 |  |  | -4415 | -4415 | -2412 | Critical Branch | Validation phase | 0 | 2003 | NA | NA | NA | 0 | 1 | CH: 6262; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 0830 | 6753 |  |  | 4750 |  |  | -4415 | -4415 | -2412 | Critical Branch | Validation phase | 0 | 2003 | NA | NA | NA | 0 | 1 | CH: 6262; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 0930 | 6065 |  |  | 3750 |  |  | -5309 | -5309 | -2994 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1030 | 6065 |  |  | 3750 |  |  | -5309 | -5309 | -2994 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1130 | 6065 |  |  | 3750 |  |  | -5309 | -5309 | -2994 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1230 | 6145 |  |  | 4091 |  |  | 3165 | 80 | 5139 | Minimum Margin | Validation phase | 3085 | 2054 | NA | NA | NA | 10198 | 1 | SI: 3841; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1330 | 6145 |  |  | 4091 |  |  | 3165 | 80 | 5139 | Minimum Margin | Validation phase | 3085 | 2054 | NA | NA | NA | 10198 | 1 | SI: 3841; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1430 | 6145 |  |  | 4091 |  |  | 3165 | 80 | 5139 | Minimum Margin | Validation phase | 3085 | 2054 | NA | NA | NA | 10198 | 1 | SI: 3841; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1530 | 7812 |  |  | 5591 |  |  | -3406 | -3406 | -1185 | Critical Branch | Smoothing ramp | 0 | 2221 | NA | NA | NA | 0 | 1 | CH: 7518; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1630 | 7812 |  |  | 7091 |  |  | -3406 | -3406 | -2685 | Critical Branch | Smoothing ramp | 0 | 721 | NA | NA | NA | 0 | 1 | CH: 7518; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1730 | 7962 |  |  | 7914 |  |  | -3561 | -3561 | -3513 | Critical Branch | Smoothing ramp | 0 | 48 | NA | NA | NA | 0 | 1 | CH: 7668; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1830 |  | 6016 | 581 |  | 5963 | 576 | -4174 | -4174 | 0 | Critical Branch | Validation phase | 0 | NA | 53 | 5 | 58 | 4174 | 1 | CH: 6217; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1930 |  | 6016 | 581 |  | 5963 | 576 | -4174 | -4174 | 0 | Critical Branch | Validation phase | 0 | NA | 53 | 5 | 58 | 4174 | 1 | CH: 6217; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2030 |  | 6016 | 581 |  | 5963 | 576 | -4174 | -4174 | 0 | Critical Branch | Validation phase | 0 | NA | 53 | 5 | 58 | 4174 | 1 | CH: 6217; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2130 | 7488 |  |  | 7194 |  |  | -4963 | -4963 | -4669 | Critical Branch | Validation phase | 0 | 294 | NA | NA | NA | 0 | 1 | CH: 6944; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2230 | 7488 |  |  | 7194 |  |  | -4963 | -4963 | -4669 | Critical Branch | Validation phase | 0 | 294 | NA | NA | NA | 0 | 1 | CH: 6944; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2330 | 6898 |  |  | 6604 |  |  | -4368 | -4368 | -4074 | Critical Branch | Validation phase | 0 | 294 | NA | NA | NA | 0 | 1 | CH: 6354; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0030 | 8037 |  |  | 7632 |  |  | -4482 | -4482 | -4077 | Critical Branch | Validation phase | 0 | 405 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7382; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250828 | August | 0130 | 8037 |  |  | 7632 |  |  | -4482 | -4482 | -4077 | Critical Branch | Validation phase | 0 | 405 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7382; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250828 | August | 0230 | 8037 |  |  | 7632 |  |  | -4482 | -4482 | -4077 | Critical Branch | Validation phase | 0 | 405 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7382; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250828 | August | 0330 | 7835 |  |  | 7497 |  |  | -2737 | -2737 | -2399 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7247; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0430 | 7835 |  |  | 7497 |  |  | -2737 | -2737 | -2399 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7247; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0530 | 7835 |  |  | 7497 |  |  | -2737 | -2737 | -2399 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7247; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0630 | 7635 |  |  | 6250 |  |  | -2511 | -2511 | -1126 | Critical Branch | Smoothing ramp | 0 | 1385 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7047; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0730 | 6707 |  |  | 4750 |  |  | -4678 | -4678 | -2721 | Critical Branch | Validation phase | 0 | 1957 | NA | NA | NA | 0 | 1 | AT: 168; AT: 70; CH: 6201; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 0830 | 6707 |  |  | 4750 |  |  | -4678 | -4678 | -2721 | Critical Branch | Validation phase | 0 | 1957 | NA | NA | NA | 0 | 1 | AT: 168; AT: 70; CH: 6201; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; SI: 4500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 0930 | 6065 |  |  | 3750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1030 | 6065 |  |  | 3750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1130 | 6065 |  |  | 3750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 2315 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 3500; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1230 | 6065 |  |  | 4051 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 2014 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 3801; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1330 | 6065 |  |  | 4051 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 2014 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 3801; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1430 | 6065 |  |  | 4051 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 2014 | NA | NA | NA | 0 | 1 | AT: 151; AT: 70; SI: 3801; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1530 | 7472 |  |  | 5551 |  |  | -2589 | -2589 | -668 | Critical Branch | Smoothing ramp | 0 | 1921 | NA | NA | NA | 0 | 1 | AT: 189; AT: 70; CH: 6982; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1630 | 7472 |  |  | 7051 |  |  | -2589 | -2589 | -2168 | Critical Branch | Smoothing ramp | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 189; AT: 70; CH: 6982; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1730 | 7837 |  |  | 7597 |  |  | -2924 | -2924 | -2684 | Critical Branch | Validation phase | 0 | 240 | NA | NA | NA | 0 | 1 | AT: 384; AT: 140; CH: 7347; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1830 |  | 6632 | 733 |  | 6580 | 727 | -5553 | -5553 | 0 | Critical Branch | Validation phase | 0 | NA | 52 | 6 | 58 | 5553 | 1 | AT: 172; AT: 124; CH: 6831; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1930 |  | 6632 | 733 |  | 6580 | 727 | -5553 | -5553 | 0 | Critical Branch | Validation phase | 0 | NA | 52 | 6 | 58 | 5553 | 1 | AT: 172; AT: 124; CH: 6831; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2030 |  | 6632 | 733 |  | 6580 | 727 | -5553 | -5553 | 0 | Critical Branch | Validation phase | 0 | NA | 52 | 6 | 58 | 5553 | 1 | AT: 172; AT: 124; CH: 6831; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2130 | 7354 |  |  | 7028 |  |  | -4593 | -4593 | -4267 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 6778; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2230 | 7354 |  |  | 7028 |  |  | -4593 | -4593 | -4267 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 359; AT: 140; CH: 6778; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2330 | 6754 |  |  | 6428 |  |  | -3985 | -3985 | -3659 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 346; AT: 160; CH: 6178; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0030 | 7790 |  |  | 7372 |  |  | -2463 | -2463 | -2045 | Critical Branch | Validation phase | 0 | 418 | NA | NA | NA | 0 | 1 | CH: 7122; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0130 | 7790 |  |  | 7372 |  |  | -2463 | -2463 | -2045 | Critical Branch | Validation phase | 0 | 418 | NA | NA | NA | 0 | 1 | CH: 7122; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0230 | 7790 |  |  | 7372 |  |  | -2463 | -2463 | -2045 | Critical Branch | Validation phase | 0 | 418 | NA | NA | NA | 0 | 1 | CH: 7122; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0330 | 7687 |  |  | 7258 |  |  | -2256 | -2256 | -1827 | Critical Branch | Validation phase | 0 | 429 | NA | NA | NA | 0 | 1 | CH: 7008; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0430 | 7687 |  |  | 7258 |  |  | -2256 | -2256 | -1827 | Critical Branch | Validation phase | 0 | 429 | NA | NA | NA | 0 | 1 | CH: 7008; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0530 | 7687 |  |  | 7258 |  |  | -2256 | -2256 | -1827 | Critical Branch | Validation phase | 0 | 429 | NA | NA | NA | 0 | 1 | CH: 7008; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0630 | 7687 |  |  | 6288 |  |  | -2256 | -2256 | -857 | Critical Branch | Smoothing ramp | 0 | 1399 | NA | NA | NA | 0 | 1 | CH: 7008; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0730 | 5206 |  |  | 4788 |  |  | -2039 | -2039 | -1621 | Critical Branch | Validation phase | 0 | 418 | NA | NA | NA | 0 | 1 | CH: 4538; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0830 | 5206 |  |  | 4788 |  |  | -2039 | -2039 | -1621 | Critical Branch | Validation phase | 0 | 418 | NA | NA | NA | 0 | 1 | CH: 4538; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0930 | 6071 |  |  | 5558 |  |  | -1426 | -1426 | -913 | Critical Branch | Validation phase | 0 | 513 | NA | NA | NA | 0 | 1 | CH: 5308; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1030 | 6071 |  |  | 5558 |  |  | -1426 | -1426 | -913 | Critical Branch | Validation phase | 0 | 513 | NA | NA | NA | 0 | 1 | CH: 5308; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1130 | 6071 |  |  | 5558 |  |  | -1426 | -1426 | -913 | Critical Branch | Validation phase | 0 | 513 | NA | NA | NA | 0 | 1 | CH: 5308; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1230 | 5735 |  |  | 5398 |  |  | -2852 | -2852 | -2515 | Critical Branch | Validation phase | 0 | 337 | NA | NA | NA | 0 | 1 | CH: 5148; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1330 | 5735 |  |  | 5398 |  |  | -2852 | -2852 | -2515 | Critical Branch | Validation phase | 0 | 337 | NA | NA | NA | 0 | 1 | CH: 5148; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1430 | 5735 |  |  | 5398 |  |  | -2852 | -2852 | -2515 | Critical Branch | Validation phase | 0 | 337 | NA | NA | NA | 0 | 1 | CH: 5148; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1530 | 6787 |  |  | 6317 |  |  | -2266 | -2266 | -1796 | Critical Branch | Validation phase | 0 | 470 | NA | NA | NA | 0 | 1 | CH: 6067; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1630 | 6837 |  |  | 6367 |  |  | -2323 | -2323 | -1853 | Critical Branch | Validation phase | 0 | 470 | NA | NA | NA | 0 | 1 | CH: 6117; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1730 | 8637 |  |  | 7867 |  |  | -4291 | -4291 | -3521 | Critical Branch | Smoothing ramp | 0 | 770 | NA | NA | NA | 0 | 1 | CH: 7917; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1830 |  | 6303 | 513 |  | 6178 | 503 | -3766 | -3766 | 0 | Critical Branch | Validation phase | 0 | NA | 125 | 10 | 135 | 3766 | 1 | CH: 6329; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1930 |  | 6303 | 513 |  | 6178 | 503 | -3766 | -3766 | 0 | Critical Branch | Validation phase | 0 | NA | 125 | 10 | 135 | 3766 | 1 | CH: 6329; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2030 |  | 6303 | 513 |  | 6178 | 503 | -3766 | -3766 | 0 | Critical Branch | Validation phase | 0 | NA | 125 | 10 | 135 | 3766 | 1 | CH: 6329; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2130 | 7340 |  |  | 6998 |  |  | -2869 | -2869 | -2527 | Critical Branch | Validation phase | 0 | 342 | NA | NA | NA | 0 | 1 | CH: 6748; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2230 | 7340 |  |  | 6998 |  |  | -2869 | -2869 | -2527 | Critical Branch | Validation phase | 0 | 342 | NA | NA | NA | 0 | 1 | CH: 6748; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2330 | 6740 |  |  | 6398 |  |  | -2259 | -2259 | -1917 | Critical Branch | Validation phase | 0 | 342 | NA | NA | NA | 0 | 1 | CH: 6148; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0030 | 7819 |  |  | 7462 |  |  | -2969 | -2969 | -2612 | Critical Branch | Validation phase | 0 | 357 | NA | NA | NA | 0 | 1 | CH: 7212; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0130 | 7819 |  |  | 7462 |  |  | -2969 | -2969 | -2612 | Critical Branch | Validation phase | 0 | 357 | NA | NA | NA | 0 | 1 | CH: 7212; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0230 | 7819 |  |  | 7462 |  |  | -2969 | -2969 | -2612 | Critical Branch | Validation phase | 0 | 357 | NA | NA | NA | 0 | 1 | CH: 7212; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0330 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 0 | 371 | NA | NA | NA | 0 | 1 | CH: 6884; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0430 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 0 | 371 | NA | NA | NA | 0 | 1 | CH: 6884; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0530 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 0 | 371 | NA | NA | NA | 0 | 1 | CH: 6884; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0630 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 0 | 371 | NA | NA | NA | 0 | 1 | CH: 6884; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0730 | 7062 |  |  | 6666 |  |  | -2504 | -2504 | -2108 | Critical Branch | Validation phase | 0 | 396 | NA | NA | NA | 0 | 1 | CH: 6416; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0830 | 7062 |  |  | 6666 |  |  | -2504 | -2504 | -2108 | Critical Branch | Validation phase | 0 | 396 | NA | NA | NA | 0 | 1 | CH: 6416; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0930 | 7392 |  |  | 6960 |  |  | -2487 | -2487 | -2055 | Critical Branch | Validation phase | 0 | 432 | NA | NA | NA | 0 | 1 | CH: 6710; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1030 | 7392 |  |  | 6960 |  |  | -2487 | -2487 | -2055 | Critical Branch | Validation phase | 0 | 432 | NA | NA | NA | 0 | 1 | CH: 6710; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1130 | 7392 |  |  | 6960 |  |  | -2487 | -2487 | -2055 | Critical Branch | Validation phase | 0 | 432 | NA | NA | NA | 0 | 1 | CH: 6710; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1230 | 7655 |  |  | 7423 |  |  | -4355 | -4355 | -4123 | Critical Branch | Validation phase | 0 | 232 | NA | NA | NA | 0 | 1 | CH: 7173; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250830 | August | 1330 | 7655 |  |  | 7423 |  |  | -4355 | -4355 | -4123 | Critical Branch | Validation phase | 0 | 232 | NA | NA | NA | 0 | 1 | CH: 7173; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250830 | August | 1430 | 7655 |  |  | 7423 |  |  | -4355 | -4355 | -4123 | Critical Branch | Validation phase | 0 | 232 | NA | NA | NA | 0 | 1 | CH: 7173; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250830 | August | 1530 |  | 7303 | 594 |  | 7171 | 583 | -2696 | -2696 | 0 | Critical Branch | Validation phase | 0 | NA | 132 | 11 | 143 | 2696 | 1 | CH: 7423; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1630 |  | 7303 | 594 |  | 7171 | 583 | -2696 | -2696 | 0 | Critical Branch | Validation phase | 0 | NA | 132 | 11 | 143 | 2696 | 1 | CH: 7423; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1730 |  | 7303 | 594 |  | 7171 | 583 | -2696 | -2696 | 0 | Critical Branch | Validation phase | 0 | NA | 132 | 11 | 143 | 2696 | 1 | CH: 7423; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1830 |  | 6055 | 482 |  | 5946 | 473 | -3782 | -3782 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 109 | 9 | 118 | 3782 | 1 | CH: 6121; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1930 |  | 6055 | 482 |  | 5946 | 473 | -3782 | -3782 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 109 | 9 | 118 | 3782 | 1 | CH: 6121; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2030 |  | 6055 | 482 |  | 5946 | 473 | -3782 | -3782 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 109 | 9 | 118 | 3782 | 1 | CH: 6121; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2130 | 6577 |  |  | 6313 |  |  | -2686 | -2686 | -2422 | Critical Branch | Validation phase | 0 | 264 | NA | NA | NA | 0 | 1 | CH: 6063; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2230 | 6577 |  |  | 6313 |  |  | -2686 | -2686 | -2422 | Critical Branch | Validation phase | 0 | 264 | NA | NA | NA | 0 | 1 | CH: 6063; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2330 | 5977 |  |  | 5713 |  |  | -2072 | -2072 | -1808 | Critical Branch | Validation phase | 0 | 264 | NA | NA | NA | 0 | 1 | CH: 5463; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0030 | 7956 |  |  | 7667 |  |  | -2987 | -2987 | -2698 | Critical Branch | Validation phase | 0 | 289 | NA | NA | NA | 0 | 1 | CH: 7417; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0130 | 7956 |  |  | 7667 |  |  | -2987 | -2987 | -2698 | Critical Branch | Validation phase | 0 | 289 | NA | NA | NA | 0 | 1 | CH: 7417; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0230 | 7956 |  |  | 7667 |  |  | -2987 | -2987 | -2698 | Critical Branch | Validation phase | 0 | 289 | NA | NA | NA | 0 | 1 | CH: 7417; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0330 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | CH: 7131; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0430 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | CH: 7131; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0530 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | CH: 7131; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0630 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | CH: 7131; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0730 | 7592 |  |  | 7311 |  |  | -2274 | -2274 | -1993 | Critical Branch | Validation phase | 0 | 281 | NA | NA | NA | 0 | 1 | CH: 7061; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0830 | 7592 |  |  | 7311 |  |  | -2274 | -2274 | -1993 | Critical Branch | Validation phase | 0 | 281 | NA | NA | NA | 0 | 1 | CH: 7061; CH: Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0930 | 7225 |  |  | 6983 |  |  | -3886 | -3886 | -3644 | Critical Branch | Validation phase | 0 | 242 | NA | NA | NA | 0 | 1 | CH: 6733; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250831 | August | 1030 | 7225 |  |  | 6983 |  |  | -3886 | -3886 | -3644 | Critical Branch | Validation phase | 0 | 242 | NA | NA | NA | 0 | 1 | CH: 6733; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250831 | August | 1130 | 7225 |  |  | 6983 |  |  | -3886 | -3886 | -3644 | Critical Branch | Validation phase | 0 | 242 | NA | NA | NA | 0 | 1 | CH: 6733; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250831 | August | 1230 | 6649 |  |  | 6649 |  |  | -3177 | -3177 | -3177 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250831 | August | 1330 | 6649 |  |  | 6649 |  |  | -3177 | -3177 | -3177 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250831 | August | 1430 | 6649 |  |  | 6649 |  |  | -3177 | -3177 | -3177 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250831 | August | 1530 | 7667 |  |  | 7667 |  |  | -4116 | -4116 | -4116 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250831 | August | 1630 | 7667 |  |  | 7667 |  |  | -4116 | -4116 | -4116 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250831 | August | 1730 | 7667 |  |  | 7667 |  |  | -4116 | -4116 | -4116 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250831 | August | 1830 |  | 6118 | 559 |  | 6093 | 557 | -3604 | -3604 | 0 | Critical Branch | Validation phase | 0 | NA | 25 | 2 | 27 | 3604 | 1 | CH: 6270; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 1930 |  | 6118 | 559 |  | 6093 | 557 | -3604 | -3604 | 0 | Critical Branch | Validation phase | 0 | NA | 25 | 2 | 27 | 3604 | 1 | CH: 6270; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2030 |  | 6118 | 559 |  | 6093 | 557 | -3604 | -3604 | 0 | Critical Branch | Validation phase | 0 | NA | 25 | 2 | 27 | 3604 | 1 | CH: 6270; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2130 | 6383 |  |  | 6045 |  |  | -2441 | -2441 | -2103 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | CH: 5795; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2230 | 6383 |  |  | 6045 |  |  | -2441 | -2441 | -2103 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | CH: 5795; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2330 | 6383 |  |  | 6045 |  |  | -2441 | -2441 | -2103 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | CH: 5795; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0030 | 7991 |  |  | 7590 |  |  | -3206 | -3206 | -2805 | Critical Branch | Validation phase | 0 | 401 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160; CH: 7340; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0130 | 7991 |  |  | 7590 |  |  | -3206 | -3206 | -2805 | Critical Branch | Validation phase | 0 | 401 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160; CH: 7340; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0230 | 7991 |  |  | 7590 |  |  | -3206 | -3206 | -2805 | Critical Branch | Validation phase | 0 | 401 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160; CH: 7340; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0330 | 8090 |  |  | 7864 |  |  | -3147 | -3147 | -2921 | Critical Branch | Validation phase | 0 | 226 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7614; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0430 | 8090 |  |  | 7864 |  |  | -3147 | -3147 | -2921 | Critical Branch | Validation phase | 0 | 226 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7614; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0530 | 8090 |  |  | 7864 |  |  | -3147 | -3147 | -2921 | Critical Branch | Validation phase | 0 | 226 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7614; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0630 | 6890 |  |  | 6565 |  |  | -1914 | -1914 | -1589 | Critical Branch | Validation phase | 0 | 325 | NA | NA | NA | 0 | 1 | AT: 410; AT: 160; CH: 6414; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0730 | 5280 |  |  | 5065 |  |  | -2228 | -2228 | -2013 | TTC Selection - LTTC | Validation phase | 0 | 215 | NA | NA | NA | 0 | 1 | AT: 292; AT: 140; CH: 4815; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0830 | 5280 |  |  | 5065 |  |  | -2228 | -2228 | -2013 | TTC Selection - LTTC | Validation phase | 0 | 215 | NA | NA | NA | 0 | 1 | AT: 292; AT: 140; CH: 4815; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0930 | 6736 |  |  | 6565 |  |  | -2665 | -2665 | -2494 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6380; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 1030 | 6736 |  |  | 6630 |  |  | -2665 | -2665 | -2559 | Critical Branch | Validation phase | 0 | 106 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6380; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 1130 | 6736 |  |  | 6630 |  |  | -2665 | -2665 | -2559 | Critical Branch | Validation phase | 0 | 106 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6380; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 1230 | 6910 |  |  | 6424 |  |  | -2593 | -2593 | -2107 | Critical Branch | Validation phase | 0 | 486 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 6174; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250901 | September | 1330 | 6910 |  |  | 6424 |  |  | -2593 | -2593 | -2107 | Critical Branch | Validation phase | 0 | 486 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 6174; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250901 | September | 1430 | 6910 |  |  | 6424 |  |  | -2593 | -2593 | -2107 | Critical Branch | Validation phase | 0 | 486 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 6174; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250901 | September | 1530 | 6571 |  |  | 6571 |  |  | -2563 | -2563 | -2563 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 140
20250901 | September | 1630 | 6571 |  |  | 6571 |  |  | -2563 | -2563 | -2563 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 140
20250901 | September | 1730 | 6571 |  |  | 6571 |  |  | -2563 | -2563 | -2563 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 140
20250901 | September | 1830 |  | 4874 | 469 |  | 4874 | 469 | -2914 | -2914 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2914 | 1 | AT: 292; AT: 140
20250901 | September | 1930 |  | 4874 | 469 |  | 4874 | 469 | -2914 | -2914 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2914 | 1 | AT: 292; AT: 140
20250901 | September | 2030 |  | 4874 | 469 |  | 4874 | 469 | -2914 | -2914 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2914 | 1 | AT: 292; AT: 140
20250901 | September | 2130 | 6078 |  |  | 5805 |  |  | -2433 | -2433 | -2160 | Critical Branch | Validation phase | 0 | 273 | NA | NA | NA | 0 | 1 | AT: 341; AT: 140; CH: 5555; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 2230 | 6078 |  |  | 5805 |  |  | -2433 | -2433 | -2160 | Critical Branch | Validation phase | 0 | 273 | NA | NA | NA | 0 | 1 | AT: 341; AT: 140; CH: 5555; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 2330 | 5478 |  |  | 5205 |  |  | -1827 | -1827 | -1554 | Critical Branch | Validation phase | 0 | 273 | NA | NA | NA | 0 | 1 | AT: 325; AT: 160; CH: 4955; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0030 | 6081 |  |  | 5999 |  |  | -1499 | -1499 | -1417 | Critical Branch | Validation phase | 0 | 82 | NA | NA | NA | 0 | 1 | CH: 5749; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0130 | 6081 |  |  | 5999 |  |  | -1499 | -1499 | -1417 | Critical Branch | Validation phase | 0 | 82 | NA | NA | NA | 0 | 1 | CH: 5749; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0230 | 6081 |  |  | 5999 |  |  | -1499 | -1499 | -1417 | Critical Branch | Validation phase | 0 | 82 | NA | NA | NA | 0 | 1 | CH: 5749; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0330 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | CH: 5667; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0430 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | CH: 5667; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0530 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | CH: 5667; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0630 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 0 | 79 | NA | NA | NA | 0 | 1 | CH: 5667; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0730 | 5280 |  |  | 4616 |  |  | -2744 | -2744 | -2080 | TTC Selection - LTTC | Validation phase | 0 | 664 | NA | NA | NA | 0 | 1 | CH: 4366; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0830 | 5280 |  |  | 4616 |  |  | -2744 | -2744 | -2080 | TTC Selection - LTTC | Validation phase | 0 | 664 | NA | NA | NA | 0 | 1 | CH: 4366; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0930 | 6307 |  |  | 6116 |  |  | -1856 | -1856 | -1665 | Critical Branch | Smoothing ramp | 0 | 191 | NA | NA | NA | 0 | 1 | CH: 5892; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1030 | 6307 |  |  | 6142 |  |  | -1856 | -1856 | -1691 | Critical Branch | Validation phase | 0 | 165 | NA | NA | NA | 0 | 1 | CH: 5892; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1130 | 6307 |  |  | 6142 |  |  | -1856 | -1856 | -1691 | Critical Branch | Validation phase | 0 | 165 | NA | NA | NA | 0 | 1 | CH: 5892; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1230 | 6962 |  |  | 6318 |  |  | -2276 | -2276 | -1632 | Critical Branch | Validation phase | 0 | 644 | NA | NA | NA | 0 | 1 | CH: 6068; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250902 | September | 1330 | 6962 |  |  | 6318 |  |  | -2276 | -2276 | -1632 | Critical Branch | Validation phase | 0 | 644 | NA | NA | NA | 0 | 1 | CH: 6068; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250902 | September | 1430 | 6962 |  |  | 6318 |  |  | -2276 | -2276 | -1632 | Critical Branch | Validation phase | 0 | 644 | NA | NA | NA | 0 | 1 | CH: 6068; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250902 | September | 1530 | 6825 |  |  | 6309 |  |  | -2664 | -2664 | -2131 | Critical Branch | Validation phase | 0 | 516 | NA | NA | NA | 0 | 1 | CH: 6560; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 1900; FR: Testing of HVDC cables imported from Italy to France
20250902 | September | 1630 | 6825 |  |  | 6309 |  |  | -2664 | -2664 | -2131 | Critical Branch | Validation phase | 0 | 516 | NA | NA | NA | 0 | 1 | CH: 6560; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 1900; FR: Testing of HVDC cables imported from Italy to France
20250902 | September | 1730 | 6825 |  |  | 6780 |  |  | -2664 | -2664 | -2619 | Critical Branch | Smoothing ramp | 0 | 45 | NA | NA | NA | 0 | 1 | CH: 6560; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1830 |  | 4803 | 609 |  | 4803 | 609 | -3222 | -3222 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3222 | 0
20250902 | September | 1930 |  | 4803 | 609 |  | 4803 | 609 | -3222 | -3222 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3222 | 0
20250902 | September | 2030 |  | 4803 | 609 |  | 4803 | 609 | -3222 | -3222 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3222 | 0
20250902 | September | 2130 | 5280 |  |  | 5018 |  |  | -2378 | -2378 | -2116 | TTC Selection - LTTC | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | CH: 4768; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 2230 | 5280 |  |  | 5018 |  |  | -2378 | -2378 | -2116 | TTC Selection - LTTC | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | CH: 4768; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 2330 | 4680 |  |  | 4418 |  |  | -1770 | -1770 | -1508 | TTC Selection - LTTC | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | CH: 4168; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250903 | September | 0030 | 7458 |  |  | 6886 |  |  | -1708 | -1708 | -1138 | Critical Branch | Validation phase | 0 | 572 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6639; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250903 | September | 0130 | 7458 |  |  | 6886 |  |  | -1708 | -1708 | -1138 | Critical Branch | Validation phase | 0 | 572 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6639; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250903 | September | 0230 | 7458 |  |  | 6886 |  |  | -1708 | -1708 | -1138 | Critical Branch | Validation phase | 0 | 572 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6639; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250903 | September | 0330 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 0 | 519 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6958; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2646; FR: N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0430 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 0 | 519 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6958; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2646; FR: N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0530 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 0 | 519 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6958; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2646; FR: N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0630 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 0 | 519 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6958; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2646; FR: N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0730 | 7456 |  |  | 6813 |  |  | -2235 | -2235 | -1592 | Critical Branch | Validation phase | 0 | 643 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6563; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 0830 | 7456 |  |  | 6813 |  |  | -2235 | -2235 | -1592 | Critical Branch | Validation phase | 0 | 643 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6563; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 0930 | 7548 |  |  | 7485 |  |  | -2127 | -2127 | -2065 | Critical Branch | Validation phase | 0 | 63 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7237; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1030 | 7548 |  |  | 7485 |  |  | -2127 | -2127 | -2065 | Critical Branch | Validation phase | 0 | 63 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7237; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1130 | 7548 |  |  | 7485 |  |  | -2127 | -2127 | -2065 | Critical Branch | Validation phase | 0 | 63 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7237; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1230 | 7605 |  |  | 7448 |  |  | -734 | -734 | -577 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7198; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1330 | 7605 |  |  | 7448 |  |  | -734 | -734 | -577 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7198; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1430 | 7605 |  |  | 7448 |  |  | -734 | -734 | -577 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7198; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1530 | 7439 |  |  | 7287 |  |  | -755 | -755 | -603 | Critical Branch | Validation phase | 0 | 152 | NA | NA | NA | 0 | 1 | AT: 424; AT: 140; CH: 7037; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1630 | 7439 |  |  | 7287 |  |  | -755 | -755 | -603 | Critical Branch | Validation phase | 0 | 152 | NA | NA | NA | 0 | 1 | AT: 424; AT: 140; CH: 7037; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1730 | 7439 |  |  | 7287 |  |  | -755 | -755 | -603 | Critical Branch | Validation phase | 0 | 152 | NA | NA | NA | 0 | 1 | AT: 424; AT: 140; CH: 7037; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1830 |  | 6471 | 650 |  | 6263 | 630 | -871 | -871 | 0 | Critical Branch | Validation phase | 0 | NA | 208 | 20 | 228 | 871 | 1 | AT: 398; AT: 140; CH: 6500; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250903 | September | 1930 |  | 6471 | 650 |  | 6263 | 462 | -871 | -871 | 0 | Critical Branch | Validation phase | 0 | NA | 208 | 188 | 396 | 871 | 1 | AT: 398; AT: 140; CH: 6500; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; IT: 424; IT: Forecasted Security Violations
20250903 | September | 2030 |  | 6471 | 650 |  | 6263 | 462 | -871 | -871 | 0 | Critical Branch | Validation phase | 0 | NA | 208 | 188 | 396 | 871 | 1 | AT: 398; AT: 140; CH: 6500; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; IT: 424; IT: Forecasted Security Violations
20250903 | September | 2130 | 7606 |  |  | 7186 |  |  | -2101 | -2101 | -1681 | Critical Branch | Validation phase | 0 | 420 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6936; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 2230 | 7606 |  |  | 7186 |  |  | -2101 | -2101 | -1681 | Critical Branch | Validation phase | 0 | 420 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6936; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 2330 | 7006 |  |  | 6586 |  |  | -1489 | -1489 | -1069 | Critical Branch | Validation phase | 0 | 420 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6336; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250904 | September | 0030 | 7640 |  |  | 7277 |  |  | -2648 | -2648 | -2295 | Critical Branch | Validation phase | 0 | 363 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7221; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0130 | 7640 |  |  | 7277 |  |  | -2648 | -2648 | -2295 | Critical Branch | Validation phase | 0 | 363 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7221; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0230 | 7640 |  |  | 7277 |  |  | -2648 | -2648 | -2295 | Critical Branch | Validation phase | 0 | 363 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7221; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0330 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250904 | September | 0430 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250904 | September | 0530 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250904 | September | 0630 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250904 | September | 0730 | 7221 |  |  | 6791 |  |  | -1585 | -1585 | -1155 | Critical Branch | Validation phase | 0 | 430 | NA | NA | NA | 0 | 1 | AT: 410; AT: 140; CH: 6541; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250904 | September | 0830 | 7221 |  |  | 6298 |  |  | -1585 | -1585 | -748 | Critical Branch | Validation phase | 0 | 923 | NA | NA | NA | 0 | 1 | AT: 410; AT: 140; CH: 6541; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 1900; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0930 | 7571 |  |  | 6697 |  |  | -890 | -890 | -142 | Critical Branch | Validation phase | 0 | 874 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7185; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 1900; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1030 | 7571 |  |  | 6697 |  |  | -890 | -890 | -142 | Critical Branch | Validation phase | 0 | 874 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7185; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 1900; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1130 | 7571 |  |  | 7297 |  |  | -890 | -890 | -640 | Critical Branch | Validation phase | 0 | 274 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7185; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1230 | 7753 |  |  | 7384 |  |  | -2959 | -2959 | -2587 | Critical Branch | Validation phase | 0 | 369 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7339; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1330 | 7753 |  |  | 7384 |  |  | -2959 | -2959 | -2587 | Critical Branch | Validation phase | 0 | 369 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7339; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1430 | 7753 |  |  | 7384 |  |  | -2959 | -2959 | -2587 | Critical Branch | Validation phase | 0 | 369 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7339; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1530 | 7405 |  |  | 7405 |  |  | -2863 | -2863 | -2863 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250904 | September | 1630 | 7405 |  |  | 7405 |  |  | -2863 | -2863 | -2863 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250904 | September | 1730 | 7405 |  |  | 7405 |  |  | -2863 | -2863 | -2863 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250904 | September | 1830 |  | 6366 | 870 |  | 5724 | 789 | -1913 | -1913 | 0 | Critical Branch | Validation phase | 0 | NA | 642 | 81 | 723 | 1913 | 1 | AT: 194; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6047; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1930 |  | 6366 | 870 |  | 5724 | 789 | -1913 | -1913 | 0 | Critical Branch | Validation phase | 0 | NA | 642 | 81 | 723 | 1913 | 1 | AT: 194; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6047; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2030 |  | 6366 | 870 |  | 5724 | 789 | -1913 | -1913 | 0 | Critical Branch | Validation phase | 0 | NA | 642 | 81 | 723 | 1913 | 1 | AT: 194; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6047; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2130 | 7566 |  |  | 7134 |  |  | -3390 | -3390 | -2956 | Critical Branch | Validation phase | 0 | 432 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6923; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2230 | 7566 |  |  | 7134 |  |  | -3390 | -3390 | -2956 | Critical Branch | Validation phase | 0 | 432 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6923; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2330 | 6966 |  |  | 6573 |  |  | -2782 | -2782 | -2389 | Critical Branch | Validation phase | 0 | 393 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6323; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250905 | September | 0030 | 7747 |  |  | 7296 |  |  | -3005 | -3005 | -2571 | Critical Branch | Validation phase | 0 | 451 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7256; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0130 | 7747 |  |  | 7296 |  |  | -3005 | -3005 | -2571 | Critical Branch | Validation phase | 0 | 451 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7256; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0230 | 7747 |  |  | 7296 |  |  | -3005 | -3005 | -2571 | Critical Branch | Validation phase | 0 | 451 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7256; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0330 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 0 | 391 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7383; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0430 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 0 | 391 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7383; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0530 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 0 | 391 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7383; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0630 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 0 | 391 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7383; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0730 | 7313 |  |  | 7174 |  |  | -3927 | -3927 | -3788 | Critical Branch | Validation phase | 0 | 139 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 6924; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 0830 | 7313 |  |  | 7174 |  |  | -3927 | -3927 | -3788 | Critical Branch | Validation phase | 0 | 139 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 6924; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 0930 | 7286 |  |  | 6858 |  |  | -2583 | -2583 | -2155 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 6608; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1030 | 7286 |  |  | 6858 |  |  | -2583 | -2583 | -2155 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 6608; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1130 | 7286 |  |  | 6858 |  |  | -2583 | -2583 | -2155 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 6608; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1230 | 7192 |  |  | 6757 |  |  | -1169 | -1169 | -734 | Critical Branch | Validation phase | 0 | 435 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6507; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1330 | 7192 |  |  | 6757 |  |  | -1169 | -1169 | -734 | Critical Branch | Validation phase | 0 | 435 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6507; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1430 | 7192 |  |  | 6757 |  |  | -1169 | -1169 | -734 | Critical Branch | Validation phase | 0 | 435 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140; CH: 6507; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1530 | 7535 |  |  | 7190 |  |  | -2989 | -2989 | -2640 | Critical Branch | Validation phase | 0 | 345 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7012; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1630 | 7535 |  |  | 7190 |  |  | -2989 | -2989 | -2640 | Critical Branch | Validation phase | 0 | 345 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7012; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1730 | 7535 |  |  | 7190 |  |  | -2989 | -2989 | -2640 | Critical Branch | Validation phase | 0 | 345 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7012; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1830 |  | 7234 | 974 |  | 6732 | 947 | -4938 | -4938 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 502 | 27 | 529 | 4938 | 1 | AT: 223; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1930 |  | 7234 | 974 |  | 6732 | 947 | -4938 | -4938 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 502 | 27 | 529 | 4938 | 1 | AT: 223; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2030 |  | 7234 | 974 |  | 6732 | 947 | -4938 | -4938 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 502 | 27 | 529 | 4938 | 1 | AT: 223; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2130 | 7912 |  |  | 7295 |  |  | -4245 | -4245 | -3628 | Critical Branch | Validation phase | 0 | 617 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7182; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2230 | 7912 |  |  | 7295 |  |  | -4245 | -4245 | -3628 | Critical Branch | Validation phase | 0 | 617 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7182; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2330 | 7312 |  |  | 6832 |  |  | -3637 | -3637 | -3157 | Critical Branch | Validation phase | 0 | 480 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6582; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0030 | 7418 |  |  | 6639 |  |  | -2852 | -2852 | -2073 | Critical Branch | Validation phase | 0 | 779 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6389; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0130 | 7418 |  |  | 6639 |  |  | -2852 | -2852 | -2073 | Critical Branch | Validation phase | 0 | 779 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6389; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0230 | 7418 |  |  | 6639 |  |  | -2852 | -2852 | -2073 | Critical Branch | Validation phase | 0 | 779 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6389; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0330 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 0 | 762 | NA | NA | NA | 1176 | 1 | AT: 415; AT: 160; CH: 5839; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0430 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 0 | 762 | NA | NA | NA | 1176 | 1 | AT: 415; AT: 160; CH: 5839; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0530 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 0 | 762 | NA | NA | NA | 1176 | 1 | AT: 415; AT: 160; CH: 5839; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0630 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 0 | 762 | NA | NA | NA | 1176 | 1 | AT: 415; AT: 160; CH: 5839; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0730 | 6970 |  |  | 6406 |  |  | -2612 | -2612 | -2048 | Critical Branch | Validation phase | 0 | 564 | NA | NA | NA | 0 | 1 | AT: 395; AT: 140; CH: 6156; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0830 | 6970 |  |  | 6406 |  |  | -2612 | -2612 | -2048 | Critical Branch | Validation phase | 0 | 564 | NA | NA | NA | 0 | 1 | AT: 395; AT: 140; CH: 6156; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0930 | 7411 |  |  | 6498 |  |  | -2894 | -2894 | -1981 | Critical Branch | Validation phase | 0 | 913 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 6248; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1030 | 7411 |  |  | 6498 |  |  | -2894 | -2894 | -1981 | Critical Branch | Validation phase | 0 | 913 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 6248; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1130 | 7411 |  |  | 6498 |  |  | -2894 | -2894 | -1981 | Critical Branch | Validation phase | 0 | 913 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140; CH: 6248; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1230 | 6998 |  |  | 6954 |  |  | -3480 | -3480 | -3436 | Critical Branch | Validation phase | 0 | 44 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6704; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1330 | 6998 |  |  | 6954 |  |  | -3480 | -3480 | -3436 | Critical Branch | Validation phase | 0 | 44 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6704; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1430 | 6998 |  |  | 6954 |  |  | -3480 | -3480 | -3436 | Critical Branch | Validation phase | 0 | 44 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 6704; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1530 |  | 5978 | 577 |  | 5645 | 545 | -3398 | -3398 | 0 | Critical Branch | Validation phase | 0 | NA | 333 | 32 | 365 | 3398 | 1 | AT: 365; AT: 140; CH: 5919; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1630 |  | 5978 | 577 |  | 5645 | 545 | -3398 | -3398 | 0 | Critical Branch | Validation phase | 0 | NA | 333 | 32 | 365 | 3398 | 1 | AT: 365; AT: 140; CH: 5919; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1730 |  | 5978 | 577 |  | 5645 | 545 | -3398 | -3398 | 0 | Critical Branch | Validation phase | 0 | NA | 333 | 32 | 365 | 3398 | 1 | AT: 365; AT: 140; CH: 5919; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1830 |  | 5983 | 760 |  | 5385 | 684 | -3921 | -3921 | 0 | Critical Branch | Validation phase | 0 | NA | 598 | 76 | 674 | 3921 | 1 | AT: 182; AT: 127; CH: 6027; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1930 |  | 5983 | 760 |  | 5385 | 684 | -3921 | -3921 | 0 | Critical Branch | Validation phase | 0 | NA | 598 | 76 | 674 | 3921 | 1 | AT: 182; AT: 127; CH: 6027; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2030 |  | 5983 | 760 |  | 5385 | 684 | -3921 | -3921 | 0 | Critical Branch | Validation phase | 0 | NA | 598 | 76 | 674 | 3921 | 1 | AT: 182; AT: 127; CH: 6027; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2130 | 7040 |  |  | 6230 |  |  | -2694 | -2694 | -1884 | Critical Branch | Validation phase | 0 | 810 | NA | NA | NA | 0 | 1 | AT: 399; AT: 140; CH: 5980; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2230 | 7040 |  |  | 6230 |  |  | -2694 | -2694 | -1884 | Critical Branch | Validation phase | 0 | 810 | NA | NA | NA | 0 | 1 | AT: 399; AT: 140; CH: 5980; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2330 | 6440 |  |  | 5630 |  |  | -2091 | -2091 | -1281 | Critical Branch | Validation phase | 0 | 810 | NA | NA | NA | 0 | 1 | AT: 388; AT: 160; CH: 5380; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250907 | September | 0030 | 7851 |  |  | 7488 |  |  | -783 | -783 | -309 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 363 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0130 | 7851 |  |  | 7488 |  |  | -783 | -783 | -309 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 363 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0230 | 7851 |  |  | 7488 |  |  | -783 | -783 | -309 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 363 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0330 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7587; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0430 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7587; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0530 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7587; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0630 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7587; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0730 | 7922 |  |  | 7496 |  |  | -2380 | -2380 | -1972 | Critical Branch | Validation phase | 0 | 426 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7617; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0830 | 7922 |  |  | 6754 |  |  | -2380 | -2380 | -1231 | Critical Branch | Validation phase | 0 | 1168 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160; CH: 7617; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0930 | 5255 |  |  | 5254 |  |  | 1845 | 575 | 1271 | Minimum Margin | Minimum Margin | 1270 | 1 | NA | NA | NA | 1967 | 1 | AT: 310; AT: 160
20250907 | September | 1030 | 5255 |  |  | 5254 |  |  | 1845 | 575 | 1271 | Minimum Margin | Minimum Margin | 1270 | 1 | NA | NA | NA | 1967 | 1 | AT: 310; AT: 160
20250907 | September | 1130 | 5255 |  |  | 5254 |  |  | 1845 | 575 | 1271 | Minimum Margin | Minimum Margin | 1270 | 1 | NA | NA | NA | 1967 | 1 | AT: 310; AT: 160
20250907 | September | 1230 | 6162 |  |  | 6162 |  |  | -191 | -191 | -191 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250907 | September | 1330 | 6162 |  |  | 6162 |  |  | -191 | -191 | -191 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250907 | September | 1430 | 6162 |  |  | 6162 |  |  | -191 | -191 | -191 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250907 | September | 1530 |  | 6916 | 810 |  | 6709 | 810 | -2855 | -2855 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 207 | 0 | 207 | 2855 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 1630 |  | 6916 | 810 |  | 6709 | 810 | -2855 | -2855 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 207 | 0 | 207 | 2855 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 1730 |  | 7117 | 810 |  | 6920 | 810 | -3023 | -3023 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 197 | 0 | 197 | 3023 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 1830 |  | 6493 | 691 |  | 6493 | 691 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3208 | 1 | AT: 413; AT: 159
20250907 | September | 1930 |  | 6493 | 691 |  | 6493 | 691 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3208 | 1 | AT: 413; AT: 159
20250907 | September | 2030 |  | 6493 | 691 |  | 6493 | 691 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3208 | 1 | AT: 413; AT: 159
20250907 | September | 2130 | 7642 |  |  | 7604 |  |  | -2489 | -2489 | -2464 | Critical Branch | Critical Branch | 0 | 38 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250907 | September | 2230 | 7642 |  |  | 7604 |  |  | -2489 | -2489 | -2464 | Critical Branch | Critical Branch | 0 | 38 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250907 | September | 2330 | 7642 |  |  | 7604 |  |  | -2489 | -2489 | -2464 | Critical Branch | Critical Branch | 0 | 38 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0030 | 7203 |  |  | 7193 |  |  | -223 | -223 | -217 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0130 | 7203 |  |  | 7193 |  |  | -223 | -223 | -217 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0230 | 7203 |  |  | 7193 |  |  | -223 | -223 | -217 | Critical Branch | Critical Branch | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0330 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 0 | 28 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0430 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 0 | 28 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0530 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 0 | 28 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0630 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 0 | 28 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250908 | September | 0730 | 6580 |  |  | 6580 |  |  | -2512 | -2512 | -2512 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 361; AT: 140
20250908 | September | 0830 | 6580 |  |  | 6580 |  |  | -2512 | -2512 | -2512 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 361; AT: 140
20250908 | September | 0930 | 7762 |  |  | 7561 |  |  | -2627 | -2627 | -2419 | Critical Branch | Validation phase | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7496; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1030 | 7762 |  |  | 7561 |  |  | -2627 | -2627 | -2419 | Critical Branch | Validation phase | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7496; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1130 | 7762 |  |  | 7561 |  |  | -2627 | -2627 | -2419 | Critical Branch | Validation phase | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7496; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1230 | 7933 |  |  | 7602 |  |  | -1192 | -1192 | -893 | Critical Branch | Validation phase | 0 | 331 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7568; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1330 | 7933 |  |  | 7602 |  |  | -1192 | -1192 | -893 | Critical Branch | Validation phase | 0 | 331 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7568; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1430 | 7933 |  |  | 7602 |  |  | -1192 | -1192 | -893 | Critical Branch | Validation phase | 0 | 331 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7568; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1530 | 7783 |  |  | 7582 |  |  | -2823 | -2823 | -2625 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1630 | 7783 |  |  | 7582 |  |  | -2823 | -2823 | -2625 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1730 | 7783 |  |  | 7582 |  |  | -2823 | -2823 | -2625 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1830 |  | 6310 | 798 |  | 6300 | 660 | -562 | -562 | 0 | Critical Branch | Validation phase | 0 | NA | 10 | 138 | 148 | 562 | 1 | AT: 187; AT: 134; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 484; IT: Forecasted Security Violations
20250908 | September | 1930 |  | 6310 | 798 |  | 6300 | 660 | -562 | -562 | 0 | Critical Branch | Validation phase | 0 | NA | 10 | 138 | 148 | 562 | 1 | AT: 187; AT: 134; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 484; IT: Forecasted Security Violations
20250908 | September | 2030 |  | 6310 | 798 |  | 6300 | 660 | -562 | -562 | 0 | Critical Branch | Validation phase | 0 | NA | 10 | 138 | 148 | 562 | 1 | AT: 187; AT: 134; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 484; IT: Forecasted Security Violations
20250908 | September | 2130 | 6900 |  |  | 6900 |  |  | -1855 | -1855 | -1854 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; IT: 484; IT: Forecasted Security Violations
20250908 | September | 2230 | 6900 |  |  | 6900 |  |  | -1855 | -1855 | -1854 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250908 | September | 2330 | 6300 |  |  | 6300 |  |  | -1254 | -1254 | -1254 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 367; AT: 160
20250909 | September | 0030 | 7526 |  |  | 7496 |  |  | -947 | -947 | -929 | Critical Branch | Critical Branch | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250909 | September | 0130 | 7526 |  |  | 7496 |  |  | -947 | -947 | -929 | Critical Branch | Critical Branch | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250909 | September | 0230 | 7526 |  |  | 7496 |  |  | -947 | -947 | -929 | Critical Branch | Critical Branch | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250909 | September | 0330 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 0 | 385 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0430 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 0 | 385 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0530 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 0 | 385 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0630 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 0 | 385 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0730 |  | 6407 | 806 |  | 6407 | 806 | -4511 | -4511 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4511 | 1 | AT: 190; AT: 136
20250909 | September | 0830 |  | 6378 | 786 |  | 6378 | 786 | -4461 | -4461 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4461 | 1 | AT: 163; AT: 117
20250909 | September | 0930 | 7374 |  |  | 7373 |  |  | -469 | -469 | -468 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 353; AT: 120
20250909 | September | 1030 | 7374 |  |  | 7373 |  |  | -469 | -469 | -468 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 353; AT: 120
20250909 | September | 1130 | 7374 |  |  | 7373 |  |  | -469 | -469 | -468 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 353; AT: 120
20250909 | September | 1230 | 6849 |  |  | 6848 |  |  | -3137 | -3137 | -3136 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 326; AT: 120
20250909 | September | 1330 | 6849 |  |  | 6848 |  |  | -3137 | -3137 | -3136 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 326; AT: 120
20250909 | September | 1430 | 6849 |  |  | 6848 |  |  | -3137 | -3137 | -3136 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 326; AT: 120
20250909 | September | 1530 | 8035 |  |  | 7702 |  |  | -3590 | -3590 | -3262 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 333 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 1630 | 8035 |  |  | 7702 |  |  | -3590 | -3590 | -3262 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 333 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 1730 | 8035 |  |  | 7702 |  |  | -3590 | -3590 | -3262 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 333 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 1830 |  | 6476 | 799 |  | 6476 | 799 | -4564 | -4564 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4564 | 1 | AT: 165; AT: 119
20250909 | September | 1930 |  | 6476 | 799 |  | 6476 | 799 | -4564 | -4564 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 0 | 0 | 4564 | 1 | AT: 165; AT: 119; IT: 894; IT: Forecasted Security Violations
20250909 | September | 2030 |  | 6476 | 799 |  | 6476 | 799 | -4564 | -4564 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 0 | 0 | 4564 | 1 | AT: 165; AT: 119; IT: 894; IT: Forecasted Security Violations
20250909 | September | 2130 |  | 6706 | 655 |  | 6705 | 655 | -4005 | -4005 | 0 | Critical Branch | Validation phase | 0 | NA | 1 | 0 | 1 | 4005 | 1 | AT: 347; AT: 120; IT: 894; IT: Forecasted Security Violations
20250909 | September | 2230 |  | 6706 | 655 |  | 6705 | 655 | -4005 | -4005 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4005 | 1 | AT: 347; AT: 120
20250909 | September | 2330 |  | 6126 | 680 |  | 6126 | 680 | -3376 | -3376 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3376 | 1 | AT: 335; AT: 140
20250910 | September | 0030 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0130 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0230 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0330 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0430 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0530 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0630 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0730 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 0830 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 284; IT: Forecasted Security Violations
20250910 | September | 0930 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 284; IT: Forecasted Security Violations
20250910 | September | 1030 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 284; IT: Forecasted Security Violations
20250910 | September | 1130 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2; IT: 284; IT: Forecasted Security Violations
20250910 | September | 1230 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1330 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1430 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1530 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1630 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1730 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1830 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1930 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2030 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2130 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2230 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | CH: 7340; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2330 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 6740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250911 | September | 0030 | 8153 |  |  | 7541 |  |  | -951 | -951 | -265 | Critical Branch | Validation phase | 0 | 612 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7557; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0130 | 8153 |  |  | 7541 |  |  | -951 | -951 | -265 | Critical Branch | Validation phase | 0 | 612 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7557; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0230 | 8153 |  |  | 7541 |  |  | -951 | -951 | -265 | Critical Branch | Validation phase | 0 | 612 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7557; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0330 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7630; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0430 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7630; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0530 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7630; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0630 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7630; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0730 | 8195 |  |  | 7603 |  |  | -1587 | -1587 | -909 | Critical Branch | Validation phase | 0 | 592 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7613; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0830 | 8195 |  |  | 7603 |  |  | -1587 | -1587 | -909 | Critical Branch | Validation phase | 0 | 592 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7613; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0930 | 7327 |  |  | 7327 |  |  | -2277 | -2277 | -2276 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 351; AT: 120
20250911 | September | 1030 | 7327 |  |  | 7327 |  |  | -2277 | -2277 | -2276 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 351; AT: 120
20250911 | September | 1130 | 7327 |  |  | 7327 |  |  | -2277 | -2277 | -2276 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 351; AT: 120
20250911 | September | 1230 | 7409 |  |  | 7397 |  |  | -1496 | -1496 | -1484 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 355; AT: 120; CH: 7147; CH: Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20250911 | September | 1330 | 7409 |  |  | 7397 |  |  | -1496 | -1496 | -1484 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 355; AT: 120; CH: 7147; CH: Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20250911 | September | 1430 | 7409 |  |  | 7397 |  |  | -1496 | -1496 | -1484 | Critical Branch | Validation phase | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 355; AT: 120; CH: 7147; CH: Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20250911 | September | 1530 | 7839 |  |  | 7363 |  |  | -3097 | -3097 | -2577 | Critical Branch | Validation phase | 0 | 476 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7207; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1630 | 7839 |  |  | 7363 |  |  | -3097 | -3097 | -2577 | Critical Branch | Validation phase | 0 | 476 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7207; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1730 | 7839 |  |  | 7363 |  |  | -3097 | -3097 | -2577 | Critical Branch | Validation phase | 0 | 476 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7207; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1830 | 8375 |  |  | 7498 |  |  | -2884 | -2884 | -2033 | Critical Branch | Validation phase | 0 | 877 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7430; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1930 | 8375 |  |  | 7498 |  |  | -2884 | -2884 | -2033 | Critical Branch | Validation phase | 0 | 877 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7430; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2030 | 8375 |  |  | 7498 |  |  | -2884 | -2884 | -2033 | Critical Branch | Validation phase | 0 | 877 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7430; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2130 | 8380 |  |  | 7584 |  |  | -1906 | -1906 | -1019 | Critical Branch | Validation phase | 0 | 796 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7580; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2230 | 8380 |  |  | 7584 |  |  | -1906 | -1906 | -1019 | Critical Branch | Validation phase | 0 | 796 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 7580; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2330 | 7780 |  |  | 7210 |  |  | -1300 | -1300 | -733 | Critical Branch | Validation phase | 0 | 570 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6980; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0030 | 7568 |  |  | 7367 |  |  | -2274 | -2274 | -2080 | Critical Branch | Validation phase | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7253; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0130 | 7568 |  |  | 7367 |  |  | -2274 | -2274 | -2080 | Critical Branch | Validation phase | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7253; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0230 | 7568 |  |  | 7367 |  |  | -2274 | -2274 | -2080 | Critical Branch | Validation phase | 0 | 201 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7253; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0330 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0430 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0530 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0630 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7365; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0730 | 6954 |  |  | 6954 |  |  | -2532 | -2532 | -2532 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 332; AT: 120
20250912 | September | 0830 | 6954 |  |  | 6954 |  |  | -2532 | -2532 | -2532 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 332; AT: 120
20250912 | September | 0930 | 7763 |  |  | 7546 |  |  | -1773 | -1773 | -1566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 217 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1030 | 7763 |  |  | 7546 |  |  | -1773 | -1773 | -1566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 217 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1130 | 7763 |  |  | 7546 |  |  | -1773 | -1773 | -1566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 217 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1230 | 7379 |  |  | 7239 |  |  | -1110 | -1110 | -973 | Critical Branch | Validation phase | 0 | 140 | NA | NA | NA | 0 | 1 | AT: 364; AT: 120; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1330 | 7379 |  |  | 7239 |  |  | -1110 | -1110 | -973 | Critical Branch | Validation phase | 0 | 140 | NA | NA | NA | 0 | 1 | AT: 364; AT: 120; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1430 | 7379 |  |  | 7239 |  |  | -1110 | -1110 | -973 | Critical Branch | Validation phase | 0 | 140 | NA | NA | NA | 0 | 1 | AT: 364; AT: 120; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1530 | 7775 |  |  | 7463 |  |  | -1488 | -1488 | -1190 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 312 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1630 | 7775 |  |  | 7463 |  |  | -1488 | -1488 | -1190 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 312 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1730 | 7835 |  |  | 7090 |  |  | -1554 | -1554 | -805 | Critical Branch | Critical Branch | 0 | 745 | NA | NA | NA | 0 | 1 | AT: 403; AT: 140
20250912 | September | 1830 |  | 5166 | 502 |  | 5165 | 502 | -2503 | -2503 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2503 | 1 | AT: 311; AT: 140
20250912 | September | 1930 |  | 5366 | 502 |  | 5365 | 502 | -2729 | -2729 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2729 | 1 | AT: 314; AT: 140
20250912 | September | 2030 |  | 5366 | 502 |  | 5365 | 502 | -2729 | -2729 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2729 | 1 | AT: 314; AT: 140
20250912 | September | 2130 | 6799 |  |  | 6710 |  |  | -2346 | -2346 | -2257 | Critical Branch | Validation phase | 0 | 89 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140; CH: 6460; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250912 | September | 2230 | 6799 |  |  | 6710 |  |  | -2346 | -2346 | -2257 | Critical Branch | Validation phase | 0 | 89 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140; CH: 6460; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250912 | September | 2330 | 6199 |  |  | 6110 |  |  | -1737 | -1737 | -1648 | Critical Branch | Validation phase | 0 | 89 | NA | NA | NA | 0 | 1 | AT: 361; AT: 160; CH: 5860; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0030 | 6413 |  |  | 6412 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160
20250913 | September | 0130 | 6413 |  |  | 6412 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160
20250913 | September | 0230 | 6413 |  |  | 6412 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160
20250913 | September | 0330 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6744; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0430 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6744; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0530 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6744; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0630 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6744; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0730 | 6545 |  |  | 6439 |  |  | -1772 | -1772 | -1666 | Critical Branch | Validation phase | 0 | 106 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140; CH: 6189; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0830 | 6545 |  |  | 6439 |  |  | -1772 | -1772 | -1666 | Critical Branch | Validation phase | 0 | 106 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140; CH: 6189; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0930 | 7666 |  |  | 7427 |  |  | -5189 | -5189 | -4952 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 239 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1030 | 7666 |  |  | 7427 |  |  | -5189 | -5189 | -4952 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 239 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1130 | 7666 |  |  | 7427 |  |  | -5189 | -5189 | -4952 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 239 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1230 | 6567 |  |  | 6567 |  |  | -3716 | -3716 | -3716 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 140
20250913 | September | 1330 | 6567 |  |  | 6567 |  |  | -3716 | -3716 | -3716 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 140
20250913 | September | 1430 | 6567 |  |  | 6567 |  |  | -3716 | -3716 | -3716 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 140
20250913 | September | 1530 | 7696 |  |  | 7443 |  |  | -2068 | -2068 | -1831 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 253 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1630 | 7696 |  |  | 7443 |  |  | -2068 | -2068 | -1831 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 253 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1730 | 7696 |  |  | 7370 |  |  | -2068 | -2068 | -1758 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 420; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1830 |  | 5416 | 526 |  | 5416 | 526 | -2882 | -2882 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2882 | 1 | AT: 328; AT: 140
20250913 | September | 1930 |  | 5616 | 526 |  | 5616 | 526 | -3111 | -3111 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3111 | 1 | AT: 331; AT: 140
20250913 | September | 2030 |  | 5616 | 526 |  | 5616 | 526 | -3111 | -3111 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3111 | 1 | AT: 331; AT: 140
20250913 | September | 2130 | 6798 |  |  | 6737 |  |  | -1935 | -1935 | -1874 | Critical Branch | Validation phase | 0 | 61 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140; CH: 6487; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 2230 | 6798 |  |  | 6737 |  |  | -1935 | -1935 | -1874 | Critical Branch | Validation phase | 0 | 61 | NA | NA | NA | 0 | 1 | AT: 374; AT: 140; CH: 6487; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 2330 | 6198 |  |  | 6137 |  |  | -1324 | -1324 | -1263 | Critical Branch | Validation phase | 0 | 61 | NA | NA | NA | 0 | 1 | AT: 361; AT: 160; CH: 5887; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0030 | 7509 |  |  | 7395 |  |  | 239 | 239 | 105 | Adjustment reached | Validation phase | 0 | 114 | NA | NA | NA | -29 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7168; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0130 | 7509 |  |  | 7395 |  |  | 239 | 239 | 105 | Adjustment reached | Validation phase | 0 | 114 | NA | NA | NA | -29 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7168; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0230 | 7509 |  |  | 7395 |  |  | 239 | 239 | 105 | Adjustment reached | Validation phase | 0 | 114 | NA | NA | NA | -29 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7168; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0330 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7184; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0430 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7184; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0530 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7184; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0630 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7184; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0730 | 7384 |  |  | 7274 |  |  | -1964 | -1964 | -1867 | Critical Branch | Validation phase | 0 | 110 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7054; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0830 | 7384 |  |  | 7274 |  |  | -1964 | -1964 | -1867 | Critical Branch | Validation phase | 0 | 110 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7054; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0930 | 7430 |  |  | 7383 |  |  | -2392 | -2392 | -2360 | Critical Branch | Validation phase | 0 | 47 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7170; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 1030 | 7430 |  |  | 7383 |  |  | -2392 | -2392 | -2360 | Critical Branch | Validation phase | 0 | 47 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7170; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 1130 | 7430 |  |  | 7383 |  |  | -2392 | -2392 | -2360 | Critical Branch | Validation phase | 0 | 47 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7170; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 1230 | 6684 |  |  | 6684 |  |  | -3837 | -3837 | -3836 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160
20250914 | September | 1330 | 6684 |  |  | 6684 |  |  | -3837 | -3837 | -3836 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160
20250914 | September | 1430 | 6684 |  |  | 6684 |  |  | -3837 | -3837 | -3836 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 404; AT: 160
20250914 | September | 1530 | 6850 |  |  | 6850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250914 | September | 1630 | 6850 |  |  | 6850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250914 | September | 1730 | 6850 |  |  | 6850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250914 | September | 1830 | 6241 |  |  | 6241 |  |  | -2755 | -2755 | -2755 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 375; AT: 160
20250914 | September | 1930 | 6441 |  |  | 6441 |  |  | -2968 | -2968 | -2968 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 376; AT: 160
20250914 | September | 2030 | 6441 |  |  | 6441 |  |  | -2968 | -2968 | -2968 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 376; AT: 160
20250914 | September | 2130 | 6620 |  |  | 6619 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 160
20250914 | September | 2230 | 6620 |  |  | 6619 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 160
20250914 | September | 2330 | 6620 |  |  | 6619 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 160
20250915 | September | 0030 | 6641 |  |  | 6380 |  |  | -1185 | -1185 | 0 | Critical Branch | Validation phase | 0 | 261 | NA | NA | NA | 1185 | 1 | AT: 389; AT: 160; CH: 6130; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0130 | 6641 |  |  | 6380 |  |  | -1185 | -1185 | 0 | Critical Branch | Validation phase | 0 | 261 | NA | NA | NA | 1185 | 1 | AT: 389; AT: 160; CH: 6130; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0230 | 6641 |  |  | 6380 |  |  | -1185 | -1185 | 0 | Critical Branch | Validation phase | 0 | 261 | NA | NA | NA | 1185 | 1 | AT: 389; AT: 160; CH: 6130; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0330 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 1181 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6663; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0430 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 1181 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6663; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0530 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 1181 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6663; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0630 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 1181 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6663; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0730 | 6490 |  |  | 6418 |  |  | -1834 | -1834 | 0 | Critical Branch | Validation phase | 0 | 72 | NA | NA | NA | 1834 | 1 | AT: 356; AT: 140; CH: 6168; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0830 | 6490 |  |  | 6418 |  |  | -1834 | -1834 | 0 | Critical Branch | Validation phase | 0 | 72 | NA | NA | NA | 1834 | 1 | AT: 356; AT: 140; CH: 6168; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0930 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1030 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1130 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1230 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1330 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1430 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1530 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1630 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1730 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1830 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1930 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2030 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2130 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2230 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2330 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250916 | September | 0030 | 6859 |  |  | 6737 |  |  | -1516 | -1516 | -1394 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 402; AT: 160; CH: 6487; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0130 | 6859 |  |  | 6737 |  |  | -1516 | -1516 | -1394 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 402; AT: 160; CH: 6487; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0230 | 6859 |  |  | 6737 |  |  | -1516 | -1516 | -1394 | Critical Branch | Validation phase | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 402; AT: 160; CH: 6487; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0330 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 0 | 160 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6662; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0430 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 0 | 160 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6662; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0530 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 0 | 160 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6662; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0630 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 0 | 160 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6662; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0730 | 7252 |  |  | 7149 |  |  | -2431 | -2431 | -2328 | Critical Branch | Validation phase | 0 | 103 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140; CH: 6899; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0830 | 7252 |  |  | 7149 |  |  | -2431 | -2431 | -2328 | Critical Branch | Validation phase | 0 | 103 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140; CH: 6899; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0930 | 7239 |  |  | 7212 |  |  | -732 | -732 | -705 | Critical Branch | Validation phase | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140; CH: 6962; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250916 | September | 1030 | 7239 |  |  | 7212 |  |  | -732 | -732 | -705 | Critical Branch | Validation phase | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140; CH: 6962; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250916 | September | 1130 | 7239 |  |  | 7212 |  |  | -732 | -732 | -705 | Critical Branch | Validation phase | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 400; AT: 140; CH: 6962; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250916 | September | 1230 | 6641 |  |  | 6641 |  |  | -4124 | -4124 | -4124 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 365; AT: 140
20250916 | September | 1330 | 6641 |  |  | 6641 |  |  | -4124 | -4124 | -4124 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 365; AT: 140
20250916 | September | 1430 | 6641 |  |  | 6641 |  |  | -4124 | -4124 | -4124 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 365; AT: 140
20250916 | September | 1530 | 7635 |  |  | 7496 |  |  | -998 | -998 | -853 | Critical Branch | Validation phase | 0 | 139 | NA | NA | NA | 0 | 1 | AT: 424; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1630 | 7635 |  |  | 7496 |  |  | -998 | -998 | -853 | Critical Branch | Validation phase | 0 | 139 | NA | NA | NA | 0 | 1 | AT: 424; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1730 | 7635 |  |  | 7496 |  |  | -998 | -998 | -853 | Critical Branch | Validation phase | 0 | 139 | NA | NA | NA | 0 | 1 | AT: 424; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1830 |  | 7107 | 672 |  | 6950 | 672 | -3133 | -3133 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 157 | 0 | 157 | 3133 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1930 |  | 7107 | 672 |  | 6950 | 672 | -3133 | -3133 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 157 | 0 | 157 | 3133 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2030 |  | 7107 | 672 |  | 6950 | 672 | -3133 | -3133 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 157 | 0 | 157 | 3133 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2130 | 7422 |  |  | 7340 |  |  | -2332 | -2332 | -2249 | Critical Branch | Validation phase | 0 | 82 | NA | NA | NA | 0 | 1 | AT: 411; AT: 140; CH: 7137; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2230 | 7422 |  |  | 7340 |  |  | -2332 | -2332 | -2249 | Critical Branch | Validation phase | 0 | 82 | NA | NA | NA | 0 | 1 | AT: 411; AT: 140; CH: 7137; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2330 | 6822 |  |  | 6787 |  |  | -1721 | -1721 | -1686 | Critical Branch | Validation phase | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 400; AT: 160; CH: 6537; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0030 | 7028 |  |  | 6876 |  |  | -1444 | -1444 | -1292 | Critical Branch | Validation phase | 0 | 152 | NA | NA | NA | 0 | 1 | CH: 6626; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0130 | 7028 |  |  | 6876 |  |  | -1444 | -1444 | -1292 | Critical Branch | Validation phase | 0 | 152 | NA | NA | NA | 0 | 1 | CH: 6626; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0230 | 7028 |  |  | 6876 |  |  | -1444 | -1444 | -1292 | Critical Branch | Validation phase | 0 | 152 | NA | NA | NA | 0 | 1 | CH: 6626; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0330 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 0 | 183 | NA | NA | NA | 0 | 1 | CH: 6261; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0430 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 0 | 183 | NA | NA | NA | 0 | 1 | CH: 6261; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0530 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 0 | 183 | NA | NA | NA | 0 | 1 | CH: 6261; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0630 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 0 | 183 | NA | NA | NA | 0 | 1 | CH: 6261; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0730 | 6664 |  |  | 6631 |  |  | -2209 | -2209 | -2176 | Critical Branch | Validation phase | 0 | 33 | NA | NA | NA | 0 | 1 | CH: 6381; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0830 | 6664 |  |  | 6631 |  |  | -2209 | -2209 | -2176 | Critical Branch | Validation phase | 0 | 33 | NA | NA | NA | 0 | 1 | CH: 6381; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0930 | 7169 |  |  | 7169 |  |  | -3527 | -3527 | -3527 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1030 | 7169 |  |  | 7169 |  |  | -3527 | -3527 | -3527 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1130 | 7169 |  |  | 7169 |  |  | -3527 | -3527 | -3527 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1230 | 7002 |  |  | 7002 |  |  | -4163 | -4163 | -4163 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1330 | 7002 |  |  | 7002 |  |  | -4163 | -4163 | -4163 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1430 | 7002 |  |  | 7002 |  |  | -4163 | -4163 | -4163 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1530 | 6984 |  |  | 6984 |  |  | -1936 | -1936 | -1936 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1630 | 6984 |  |  | 6984 |  |  | -1936 | -1936 | -1936 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1730 | 6984 |  |  | 6984 |  |  | -1936 | -1936 | -1936 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250917 | September | 1830 |  | 6116 | 573 |  | 6116 | 573 | -2951 | -2951 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2951 | 0
20250917 | September | 1930 |  | 6116 | 573 |  | 6116 | 573 | -2951 | -2951 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2951 | 0
20250917 | September | 2030 |  | 6116 | 573 |  | 6116 | 573 | -2951 | -2951 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2951 | 0
20250917 | September | 2130 | 6469 |  |  | 6402 |  |  | -1310 | -1310 | -1243 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | CH: 6152; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 2230 | 6469 |  |  | 6402 |  |  | -1310 | -1310 | -1243 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | CH: 6152; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 2330 | 5869 |  |  | 5802 |  |  | -697 | -697 | -630 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | CH: 5552; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0030 | 6761 |  |  | 6531 |  |  | -1576 | -1576 | -1346 | Critical Branch | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 396; AT: 160; CH: 6281; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0130 | 6761 |  |  | 6531 |  |  | -1576 | -1576 | -1346 | Critical Branch | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 396; AT: 160; CH: 6281; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0230 | 6761 |  |  | 6531 |  |  | -1576 | -1576 | -1346 | Critical Branch | Validation phase | 0 | 230 | NA | NA | NA | 0 | 1 | AT: 396; AT: 160; CH: 6281; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0330 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160; CH: 6486; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0430 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160; CH: 6486; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0530 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160; CH: 6486; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0630 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 0 | 157 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160; CH: 6486; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0730 | 5663 |  |  | 5663 |  |  | -1841 | -1841 | -1841 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 320; AT: 140
20250918 | September | 0830 | 5663 |  |  | 5663 |  |  | -1841 | -1841 | -1841 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 320; AT: 140
20250918 | September | 0930 | 7031 |  |  | 7010 |  |  | -1912 | -1912 | -1893 | Critical Branch | Validation phase | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 405; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1030 | 7031 |  |  | 7010 |  |  | -1912 | -1912 | -1893 | Critical Branch | Validation phase | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 405; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1130 | 7031 |  |  | 7010 |  |  | -1912 | -1912 | -1893 | Critical Branch | Validation phase | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 405; AT: 140; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1230 | 7452 |  |  | 7029 |  |  | -2408 | -2408 | -1986 | Critical Branch | Validation phase | 0 | 423 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6811; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1330 | 7452 |  |  | 7029 |  |  | -2408 | -2408 | -1986 | Critical Branch | Validation phase | 0 | 423 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6811; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1430 | 7452 |  |  | 7029 |  |  | -2408 | -2408 | -1986 | Critical Branch | Validation phase | 0 | 423 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6811; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1530 | 7019 |  |  | 6985 |  |  | -2172 | -2172 | -2138 | Critical Branch | Validation phase | 0 | 34 | NA | NA | NA | 0 | 1 | AT: 404; AT: 140; CH: 6740; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1630 | 7019 |  |  | 6985 |  |  | -2172 | -2172 | -2138 | Critical Branch | Validation phase | 0 | 34 | NA | NA | NA | 0 | 1 | AT: 404; AT: 140; CH: 6740; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1730 | 7319 |  |  | 7005 |  |  | -2502 | -2502 | -2195 | Critical Branch | Validation phase | 0 | 314 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140; CH: 7040; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 1830 |  | 5071 | 467 |  | 5071 | 467 | -2721 | -2721 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2721 | 1 | AT: 296; AT: 140
20250918 | September | 1930 |  | 5071 | 467 |  | 5071 | 467 | -2721 | -2721 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2721 | 1 | AT: 296; AT: 140
20250918 | September | 2030 |  | 5071 | 467 |  | 5071 | 467 | -2721 | -2721 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2721 | 1 | AT: 296; AT: 140
20250918 | September | 2130 | 6903 |  |  | 6581 |  |  | -2143 | -2143 | -1821 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; CH: 6331; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 2230 | 6903 |  |  | 6581 |  |  | -2143 | -2143 | -1821 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; CH: 6331; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 2330 | 6303 |  |  | 5981 |  |  | -1532 | -1532 | -1210 | Critical Branch | Validation phase | 0 | 322 | NA | NA | NA | 0 | 1 | AT: 367; AT: 160; CH: 5731; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0030 | 7163 |  |  | 6587 |  |  | -3457 | -3457 | -2881 | Critical Branch | Validation phase | 0 | 576 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6337; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0130 | 7163 |  |  | 6587 |  |  | -3457 | -3457 | -2881 | Critical Branch | Validation phase | 0 | 576 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6337; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0230 | 7163 |  |  | 6587 |  |  | -3457 | -3457 | -2881 | Critical Branch | Validation phase | 0 | 576 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6337; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0330 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | AT: 407; AT: 160; CH: 6502; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0430 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | AT: 407; AT: 160; CH: 6502; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0530 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | AT: 407; AT: 160; CH: 6502; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0630 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | AT: 407; AT: 160; CH: 6502; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0730 | 5557 |  |  | 5556 |  |  | -3420 | -3420 | -3419 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 313; AT: 140
20250919 | September | 0830 | 5557 |  |  | 5556 |  |  | -3420 | -3420 | -3419 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 313; AT: 140
20250919 | September | 0930 | 6352 |  |  | 6352 |  |  | -2360 | -2360 | -2360 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 363; AT: 140
20250919 | September | 1030 | 6352 |  |  | 6352 |  |  | -2360 | -2360 | -2360 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 363; AT: 140
20250919 | September | 1130 | 6352 |  |  | 6352 |  |  | -2360 | -2360 | -2360 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 363; AT: 140
20250919 | September | 1230 | 6121 |  |  | 5803 |  |  | -4297 | -4297 | -3979 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 348; AT: 140; CH: 5553; CH: Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250919 | September | 1330 | 6121 |  |  | 5803 |  |  | -4297 | -4297 | -3979 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 348; AT: 140; CH: 5553; CH: Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250919 | September | 1430 | 6121 |  |  | 5803 |  |  | -4297 | -4297 | -3979 | Critical Branch | Validation phase | 0 | 318 | NA | NA | NA | 0 | 1 | AT: 348; AT: 140; CH: 5553; CH: Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250919 | September | 1530 | 7170 |  |  | 6872 |  |  | -2979 | -2979 | -2681 | Critical Branch | Validation phase | 0 | 298 | NA | NA | NA | 0 | 1 | AT: 413; AT: 140; CH: 6622; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1630 | 7170 |  |  | 6872 |  |  | -2979 | -2979 | -2681 | Critical Branch | Validation phase | 0 | 298 | NA | NA | NA | 0 | 1 | AT: 413; AT: 140; CH: 6622; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1730 | 7470 |  |  | 7005 |  |  | -3314 | -3314 | -2849 | Critical Branch | Smoothing ramp | 0 | 465 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 6922; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1830 | 7650 |  |  | 5505 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2145 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 5255; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1930 | 7650 |  |  | 5505 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2145 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 5255; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2030 | 7650 |  |  | 5505 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2145 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 5255; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2130 | 7650 |  |  | 6581 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1069 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6331; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2230 | 7650 |  |  | 6581 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1069 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 6331; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2330 | 7050 |  |  | 5981 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1069 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160; CH: 5731; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0030 | 6903 |  |  | 6013 |  |  | -1829 | -1829 | -939 | Critical Branch | Validation phase | 0 | 890 | NA | NA | NA | 0 | 1 | CH: 5763; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0130 | 6903 |  |  | 6013 |  |  | -1829 | -1829 | -939 | Critical Branch | Validation phase | 0 | 890 | NA | NA | NA | 0 | 1 | CH: 5763; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0230 | 6903 |  |  | 6013 |  |  | -1829 | -1829 | -939 | Critical Branch | Validation phase | 0 | 890 | NA | NA | NA | 0 | 1 | CH: 5763; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0330 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 0 | 828 | NA | NA | NA | 0 | 1 | CH: 5726; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0430 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 0 | 828 | NA | NA | NA | 0 | 1 | CH: 5726; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0530 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 0 | 828 | NA | NA | NA | 0 | 1 | CH: 5726; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0630 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 0 | 828 | NA | NA | NA | 0 | 1 | CH: 5726; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0730 | 6657 |  |  | 5792 |  |  | -2001 | -2001 | -1136 | Critical Branch | Validation phase | 0 | 865 | NA | NA | NA | 0 | 1 | CH: 5542; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0830 | 6657 |  |  | 5792 |  |  | -2001 | -2001 | -1136 | Critical Branch | Validation phase | 0 | 865 | NA | NA | NA | 0 | 1 | CH: 5542; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0930 | 6528 |  |  | 6528 |  |  | -3255 | -3255 | -3255 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250920 | September | 1030 | 6528 |  |  | 6528 |  |  | -3255 | -3255 | -3255 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250920 | September | 1130 | 6528 |  |  | 6528 |  |  | -3255 | -3255 | -3255 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250920 | September | 1230 | 6528 |  |  | 6528 |  |  | -119 | -119 | -119 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250920 | September | 1330 | 6528 |  |  | 6528 |  |  | -119 | -119 | -119 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250920 | September | 1430 | 6528 |  |  | 6528 |  |  | -119 | -119 | -119 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250920 | September | 1530 | 7217 |  |  | 6639 |  |  | -2026 | -2026 | -1448 | Critical Branch | Validation phase | 0 | 578 | NA | NA | NA | 0 | 1 | CH: 6389; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250920 | September | 1630 | 7217 |  |  | 6639 |  |  | -2026 | -2026 | -1448 | Critical Branch | Validation phase | 0 | 578 | NA | NA | NA | 0 | 1 | CH: 6389; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250920 | September | 1730 | 7517 |  |  | 5798 |  |  | -2348 | -2348 | -629 | Critical Branch | Smoothing ramp | 0 | 1719 | NA | NA | NA | 0 | 1 | CH: 6689; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 1830 | 5480 |  |  | 4298 |  |  | -2511 | -2511 | -1329 | TTC Selection - LTTC | Validation phase | 0 | 1182 | NA | NA | NA | 0 | 1 | CH: 4048; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 1930 | 5480 |  |  | 4298 |  |  | -2511 | -2511 | -1329 | TTC Selection - LTTC | Validation phase | 0 | 1182 | NA | NA | NA | 0 | 1 | CH: 4048; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2030 | 5480 |  |  | 4298 |  |  | -2511 | -2511 | -1329 | TTC Selection - LTTC | Validation phase | 0 | 1182 | NA | NA | NA | 0 | 1 | CH: 4048; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2130 | 6491 |  |  | 5798 |  |  | -1397 | -1397 | -704 | Critical Branch | Smoothing ramp | 0 | 693 | NA | NA | NA | 0 | 1 | CH: 5877; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2230 | 6491 |  |  | 6127 |  |  | -1397 | -1397 | -1033 | Critical Branch | Validation phase | 0 | 364 | NA | NA | NA | 0 | 1 | CH: 5877; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2330 | 5891 |  |  | 5527 |  |  | -788 | -788 | -424 | Critical Branch | Validation phase | 0 | 364 | NA | NA | NA | 0 | 1 | CH: 5277; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250921 | September | 0030 | 8275 |  |  | 7029 |  |  | -1193 | -1193 | 0 | Critical Branch | Validation phase | 0 | 1246 | NA | NA | NA | 1193 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6779; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0130 | 8275 |  |  | 7029 |  |  | -1193 | -1193 | 0 | Critical Branch | Validation phase | 0 | 1246 | NA | NA | NA | 1193 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6779; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0230 | 8275 |  |  | 7029 |  |  | -1193 | -1193 | 0 | Critical Branch | Validation phase | 0 | 1246 | NA | NA | NA | 1193 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6779; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0330 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 0 | 1412 | NA | NA | NA | 5364 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6670; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0430 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 0 | 1412 | NA | NA | NA | 5364 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6670; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0530 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 0 | 1412 | NA | NA | NA | 5364 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6670; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0630 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 0 | 1412 | NA | NA | NA | 5364 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6670; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0730 | 8429 |  |  | 7050 |  |  | -5825 | -5825 | 0 | Critical Branch | Validation phase | 0 | 1379 | NA | NA | NA | 5825 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6943; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0830 | 8429 |  |  | 7050 |  |  | -5825 | -5825 | 0 | Critical Branch | Validation phase | 0 | 1379 | NA | NA | NA | 5825 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6943; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0930 | 8114 |  |  | 6905 |  |  | -4185 | -4185 | 0 | Critical Branch | Validation phase | 0 | 1209 | NA | NA | NA | 4185 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6655; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1030 | 8114 |  |  | 6905 |  |  | -4185 | -4185 | 0 | Critical Branch | Validation phase | 0 | 1209 | NA | NA | NA | 4185 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6655; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1130 | 8114 |  |  | 6905 |  |  | -4185 | -4185 | 0 | Critical Branch | Validation phase | 0 | 1209 | NA | NA | NA | 4185 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6655; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1230 | 6018 |  |  | 6984 |  |  | -2573 | -2573 | 0 | Critical Branch | Critical Branch | 0 | -966 | NA | NA | NA | 2573 | 1 | AT: 349; AT: 160
20250921 | September | 1330 | 6018 |  |  | 6984 |  |  | -2573 | -2573 | 0 | Critical Branch | Critical Branch | 0 | -966 | NA | NA | NA | 2573 | 1 | AT: 349; AT: 160
20250921 | September | 1430 | 6018 |  |  | 6984 |  |  | -2573 | -2573 | 0 | Critical Branch | Critical Branch | 0 | -966 | NA | NA | NA | 2573 | 1 | AT: 349; AT: 160
20250921 | September | 1530 | 7602 |  |  | 7050 |  |  | -3976 | -3976 | 0 | Critical Branch | Validation phase | 0 | 552 | NA | NA | NA | 3976 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6803; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1630 | 7602 |  |  | 7050 |  |  | -3976 | -3976 | 0 | Critical Branch | Validation phase | 0 | 552 | NA | NA | NA | 3976 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6803; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1730 | 7802 |  |  | 7043 |  |  | -4179 | -4179 | 0 | Critical Branch | Validation phase | 0 | 759 | NA | NA | NA | 4179 | 1 | AT: 393; AT: 160; CH: 6803; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250921 | September | 1830 | 5395 |  |  | 7135 |  |  | -2668 | -2668 | 0 | Critical Branch | Critical Branch | 0 | -1740 | NA | NA | NA | 2668 | 1 | AT: 300; AT: 160
20250921 | September | 1930 | 5395 |  |  | 7135 |  |  | -2668 | -2668 | 0 | Critical Branch | Critical Branch | 0 | -1740 | NA | NA | NA | 2668 | 1 | AT: 300; AT: 160
20250921 | September | 2030 | 5395 |  |  | 7135 |  |  | -2668 | -2668 | 0 | Critical Branch | Critical Branch | 0 | -1740 | NA | NA | NA | 2668 | 1 | AT: 300; AT: 160
20250921 | September | 2130 | 7576 |  |  | 6687 |  |  | -3139 | -3139 | 0 | Critical Branch | Validation phase | 0 | 889 | NA | NA | NA | 3139 | 1 | AT: 393; AT: 160; CH: 6437; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250921 | September | 2230 | 7576 |  |  | 6687 |  |  | -3139 | -3139 | 0 | Critical Branch | Validation phase | 0 | 889 | NA | NA | NA | 3139 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6437; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 2330 | 7576 |  |  | 6687 |  |  | -3139 | -3139 | 0 | Critical Branch | Validation phase | 0 | 889 | NA | NA | NA | 3139 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6437; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 0030 | 7363 |  |  | 7163 |  |  | -2390 | -2390 | -2190 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6913; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 0130 | 7363 |  |  | 7163 |  |  | -2390 | -2390 | -2190 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6913; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 0230 | 7363 |  |  | 7163 |  |  | -2390 | -2390 | -2190 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6913; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 0330 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250922 | September | 0430 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250922 | September | 0530 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250922 | September | 0630 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250922 | September | 0730 | 6792 |  |  | 6791 |  |  | -1972 | -1972 | -1971 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 363; AT: 140
20250922 | September | 0830 | 5792 |  |  | 5792 |  |  | -861 | -861 | -861 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 354; AT: 140
20250922 | September | 0930 | 7378 |  |  | 6839 |  |  | -2195 | -2195 | -1671 | Critical Branch | Validation phase | 0 | 539 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6907; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1030 | 7378 |  |  | 6839 |  |  | -2195 | -2195 | -1671 | Critical Branch | Validation phase | 0 | 539 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6907; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1130 | 7378 |  |  | 6839 |  |  | -2195 | -2195 | -1671 | Critical Branch | Validation phase | 0 | 539 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 6907; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1230 | 7526 |  |  | 6897 |  |  | -2226 | -2226 | -1603 | Critical Branch | Validation phase | 0 | 629 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7019; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1330 | 7526 |  |  | 6897 |  |  | -2226 | -2226 | -1603 | Critical Branch | Validation phase | 0 | 629 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7019; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1430 | 7526 |  |  | 6897 |  |  | -2226 | -2226 | -1603 | Critical Branch | Validation phase | 0 | 629 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7019; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1530 | 6062 |  |  | 6062 |  |  | -956 | -956 | -956 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 375; AT: 140
20250922 | September | 1630 | 7062 |  |  | 7062 |  |  | -2047 | -2047 | -2047 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 382; AT: 140
20250922 | September | 1730 | 7062 |  |  | 7062 |  |  | -2047 | -2047 | -2047 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 382; AT: 140
20250922 | September | 1830 | 6474 |  |  | 6133 |  |  | -2758 | -2758 | -2417 | Critical Branch | Validation phase | 0 | 341 | NA | NA | NA | 0 | 1 | AT: 347; AT: 140; CH: 5883; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 1930 | 6474 |  |  | 6133 |  |  | -2758 | -2758 | -2417 | Critical Branch | Validation phase | 0 | 341 | NA | NA | NA | 0 | 1 | AT: 347; AT: 140; CH: 5883; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2030 | 6474 |  |  | 6133 |  |  | -2758 | -2758 | -2417 | Critical Branch | Validation phase | 0 | 341 | NA | NA | NA | 0 | 1 | AT: 347; AT: 140; CH: 5883; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2130 | 6727 |  |  | 5995 |  |  | -1790 | -1790 | -1058 | Critical Branch | Validation phase | 0 | 732 | NA | NA | NA | 0 | 1 | AT: 362; AT: 140; CH: 5745; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2230 | 6727 |  |  | 5995 |  |  | -1790 | -1790 | -1058 | Critical Branch | Validation phase | 0 | 732 | NA | NA | NA | 0 | 1 | AT: 362; AT: 140; CH: 5745; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2330 | 6127 |  |  | 5395 |  |  | -1179 | -1179 | -447 | Critical Branch | Validation phase | 0 | 732 | NA | NA | NA | 0 | 1 | AT: 348; AT: 160; CH: 5145; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250923 | September | 0030 | 7509 |  |  | 7098 |  |  | -1874 | -1874 | -1463 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6848; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0130 | 7509 |  |  | 7098 |  |  | -1874 | -1874 | -1463 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6848; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0230 | 7509 |  |  | 7098 |  |  | -1874 | -1874 | -1463 | Critical Branch | Validation phase | 0 | 411 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6848; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0330 | 8029 |  |  | 7416 |  |  | -2361 | -2361 | -1754 | Critical Branch | Validation phase | 0 | 613 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7180; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0430 | 8029 |  |  | 7416 |  |  | -2361 | -2361 | -1754 | Critical Branch | Validation phase | 0 | 613 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7180; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0530 | 8029 |  |  | 7416 |  |  | -2361 | -2361 | -1754 | Critical Branch | Validation phase | 0 | 613 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7180; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0630 | 8029 |  |  | 6809 |  |  | -2361 | -2361 | -1149 | Critical Branch | Validation phase | 0 | 1220 | NA | NA | NA | 0 | 1 | AT: 410; AT: 160; CH: 7180; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250923 | September | 0730 |  | 5302 | 101 |  | 5131 | 98 | -2382 | -2382 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 171 | 3 | 174 | 2382 | 1 | AT: 298; AT: 71; CH: 5209; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 0830 |  | 5302 | 101 |  | 5131 | 98 | -2382 | -2382 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 171 | 3 | 174 | 2382 | 1 | AT: 298; AT: 71; CH: 5209; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 0930 | 7192 |  |  | 6809 |  |  | -2131 | -2131 | -1750 | Critical Branch | Critical Branch | 0 | 383 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250923 | September | 1030 | 7192 |  |  | 7191 |  |  | -2131 | -2131 | -2130 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140
20250923 | September | 1130 | 7192 |  |  | 7191 |  |  | -2131 | -2131 | -2130 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 389; AT: 140
20250923 | September | 1230 | 7646 |  |  | 7317 |  |  | -2087 | -2087 | -1758 | Critical Branch | Validation phase | 0 | 329 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 7067; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 1330 | 7646 |  |  | 7317 |  |  | -2087 | -2087 | -1758 | Critical Branch | Validation phase | 0 | 329 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 7067; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 1430 | 7646 |  |  | 7317 |  |  | -2087 | -2087 | -1758 | Critical Branch | Validation phase | 0 | 329 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140; CH: 7067; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 1530 | 7220 |  |  | 7220 |  |  | -902 | -902 | -902 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140
20250923 | September | 1630 | 7220 |  |  | 7220 |  |  | -902 | -902 | -902 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140
20250923 | September | 1730 | 7220 |  |  | 6789 |  |  | -902 | -902 | -473 | Critical Branch | Critical Branch | 0 | 431 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250923 | September | 1830 |  | 5091 | 610 |  | 4820 | 560 | -2573 | -2573 | 0 | Critical Branch | Validation phase | 0 | NA | 271 | 50 | 321 | 2573 | 1 | AT: 209; AT: 100; CH: 5310; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; IT: 403; IT: Forecasted Security Violations
20250923 | September | 1930 |  | 5091 | 610 |  | 4820 | 560 | -2573 | -2573 | 0 | Critical Branch | Validation phase | 0 | NA | 271 | 50 | 321 | 2573 | 1 | AT: 209; AT: 100; CH: 5310; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; IT: 403; IT: Forecasted Security Violations
20250923 | September | 2030 |  | 5091 | 610 |  | 4820 | 560 | -2573 | -2573 | 0 | Critical Branch | Validation phase | 0 | NA | 271 | 50 | 321 | 2573 | 1 | AT: 209; AT: 100; CH: 5310; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; IT: 403; IT: Forecasted Security Violations
20250923 | September | 2130 | 6757 |  |  | 6757 |  |  | -1892 | -1892 | -1892 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 364; AT: 140
20250923 | September | 2230 | 6757 |  |  | 6757 |  |  | -1892 | -1892 | -1892 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 364; AT: 140
20250923 | September | 2330 | 6157 |  |  | 6157 |  |  | -1282 | -1282 | -1282 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 350; AT: 160
20250924 | September | 0030 | 7522 |  |  | 7360 |  |  | -2047 | -2047 | -1889 | Critical Branch | Validation phase | 0 | 162 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7121; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 0130 | 7522 |  |  | 7360 |  |  | -2047 | -2047 | -1889 | Critical Branch | Validation phase | 0 | 162 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7121; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 0230 | 7522 |  |  | 7360 |  |  | -2047 | -2047 | -1889 | Critical Branch | Validation phase | 0 | 162 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7121; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 0330 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250924 | September | 0430 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250924 | September | 0530 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250924 | September | 0630 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 160
20250924 | September | 0730 | 5630 |  |  | 5629 |  |  | -1833 | -1833 | -1833 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 298; AT: 140
20250924 | September | 0830 | 5630 |  |  | 5629 |  |  | -1833 | -1833 | -1833 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 298; AT: 140
20250924 | September | 0930 | 7052 |  |  | 7000 |  |  | -1788 | -1788 | -1736 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6750; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 1030 | 7052 |  |  | 7000 |  |  | -1788 | -1788 | -1736 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6750; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 1130 | 7052 |  |  | 7000 |  |  | -1788 | -1788 | -1736 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140; CH: 6750; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 1230 | 8058 |  |  | 7771 |  |  | -1484 | -1484 | -1108 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7748; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250924 | September | 1330 | 8058 |  |  | 7771 |  |  | -1484 | -1484 | -1108 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7748; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250924 | September | 1430 | 8058 |  |  | 7771 |  |  | -1484 | -1484 | -1108 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7748; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250924 | September | 1530 | 7032 |  |  | 7032 |  |  | -1782 | -1782 | -1782 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250924 | September | 1630 | 7032 |  |  | 7032 |  |  | -1782 | -1782 | -1782 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250924 | September | 1730 | 7032 |  |  | 7032 |  |  | -1782 | -1782 | -1782 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250924 | September | 1830 |  | 6141 | 562 |  | 6140 | 562 | -2460 | -2460 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2460 | 1 | AT: 356; AT: 140
20250924 | September | 1930 |  | 6141 | 562 |  | 6140 | 562 | -2460 | -2460 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2460 | 1 | AT: 356; AT: 140
20250924 | September | 2030 |  | 6141 | 562 |  | 6140 | 562 | -2460 | -2460 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2460 | 1 | AT: 356; AT: 140
20250924 | September | 2130 | 7397 |  |  | 7396 |  |  | -1806 | -1806 | -1805 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250924 | September | 2230 | 7397 |  |  | 7396 |  |  | -1806 | -1806 | -1805 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140
20250924 | September | 2330 | 6797 |  |  | 6797 |  |  | -1194 | -1194 | -1194 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 390; AT: 160
20250925 | September | 0030 | 7358 |  |  | 7200 |  |  | -1491 | -1491 | -1333 | Critical Branch | Validation phase | 0 | 158 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0130 | 7358 |  |  | 7200 |  |  | -1491 | -1491 | -1333 | Critical Branch | Validation phase | 0 | 158 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0230 | 7358 |  |  | 7200 |  |  | -1491 | -1491 | -1333 | Critical Branch | Validation phase | 0 | 158 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0330 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 0 | 96 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0430 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 0 | 96 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0530 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 0 | 96 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0630 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 0 | 96 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0730 | 6822 |  |  | 6822 |  |  | -2213 | -2213 | -2213 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 368; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0830 | 6822 |  |  | 6822 |  |  | -2213 | -2213 | -2213 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 368; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0930 | 7043 |  |  | 6572 |  |  | -1901 | -1901 | -1407 | Critical Branch | Validation phase | 0 | 471 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 1900; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1
20250925 | September | 1030 | 7043 |  |  | 6572 |  |  | -1901 | -1901 | -1407 | Critical Branch | Validation phase | 0 | 471 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 1900; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1
20250925 | September | 1130 | 7043 |  |  | 6572 |  |  | -1901 | -1901 | -1407 | Critical Branch | Validation phase | 0 | 471 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 1900; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1
20250925 | September | 1230 | 7121 |  |  | 7121 |  |  | -1846 | -1846 | -1846 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 1330 | 7121 |  |  | 7121 |  |  | -1846 | -1846 | -1846 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 1430 | 7121 |  |  | 7121 |  |  | -1846 | -1846 | -1846 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 1530 | 8033 |  |  | 7656 |  |  | -1290 | -1290 | -853 | Critical Branch | Validation phase | 0 | 377 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1630 | 8033 |  |  | 7656 |  |  | -1290 | -1290 | -853 | Critical Branch | Validation phase | 0 | 377 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1730 | 8033 |  |  | 7656 |  |  | -1290 | -1290 | -853 | Critical Branch | Validation phase | 0 | 377 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1830 |  | 7495 | 723 |  | 7085 | 699 | -3568 | -3568 | 0 | Critical Branch | Validation phase | 0 | NA | 410 | 24 | 434 | 3568 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1930 |  | 7495 | 723 |  | 7085 | 699 | -3568 | -3568 | 0 | Critical Branch | Validation phase | 0 | NA | 410 | 24 | 434 | 3568 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2030 |  | 7495 | 723 |  | 7085 | 699 | -3568 | -3568 | 0 | Critical Branch | Validation phase | 0 | NA | 410 | 24 | 434 | 3568 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2130 | 8172 |  |  | 7656 |  |  | -960 | -960 | -395 | Critical Branch | Validation phase | 0 | 516 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2230 | 8172 |  |  | 7656 |  |  | -960 | -960 | -395 | Critical Branch | Validation phase | 0 | 516 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 7550; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2330 | 7572 |  |  | 7200 |  |  | -348 | -348 | 24 | Critical Branch | Validation phase | 0 | 372 | NA | NA | NA | 396 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 6950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2500; FR: Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250926 | September | 0030 | 8298 |  |  | 8182 |  |  | -1345 | -1345 | -1245 | Critical Branch | Validation phase | 0 | 116 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7997; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250926 | September | 0130 | 8298 |  |  | 8182 |  |  | -1345 | -1345 | -1245 | Critical Branch | Validation phase | 0 | 116 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7997; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250926 | September | 0230 | 8298 |  |  | 8182 |  |  | -1345 | -1345 | -1245 | Critical Branch | Validation phase | 0 | 116 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7997; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250926 | September | 0330 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 0 | 51 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250926 | September | 0430 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 0 | 51 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250926 | September | 0530 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 0 | 51 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250926 | September | 0630 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 0 | 51 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250926 | September | 0730 | 7913 |  |  | 7906 |  |  | -2396 | -2396 | -2390 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 0830 | 7713 |  |  | 7706 |  |  | -2172 | -2172 | -2166 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 0930 | 7938 |  |  | 7918 |  |  | -2150 | -2150 | -2132 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 1030 | 7938 |  |  | 7918 |  |  | -2150 | -2150 | -2132 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 1130 | 7938 |  |  | 7918 |  |  | -2150 | -2150 | -2132 | Critical Branch | Critical Branch | 0 | 20 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 1230 | 8058 |  |  | 8031 |  |  | -1355 | -1355 | -1331 | Critical Branch | Critical Branch | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 1330 | 8058 |  |  | 8031 |  |  | -1355 | -1355 | -1331 | Critical Branch | Critical Branch | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 1430 | 8058 |  |  | 7684 |  |  | -1355 | -1355 | -984 | Critical Branch | Critical Branch | 0 | 374 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250926 | September | 1530 | 6184 |  |  | 6184 |  |  | 200 | 104 | 96 | Minimum Margin | Minimum Margin | 96 | 0 | NA | NA | NA | 88 | 1 | AT: 340; AT: 140
20250926 | September | 1630 | 7530 |  |  | 7530 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 349; AT: 140
20250926 | September | 1730 | 7530 |  |  | 7530 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 349; AT: 140
20250926 | September | 1830 |  | 8838 | 716 |  | 8606 | 716 | -3871 | -3871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 232 | 0 | 232 | 3871 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250926 | September | 1930 |  | 8838 | 716 |  | 8606 | 716 | -3871 | -3871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 232 | 0 | 232 | 3871 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250926 | September | 2030 |  | 8838 | 716 |  | 8606 | 716 | -3871 | -3871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 232 | 0 | 232 | 3871 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250926 | September | 2130 | 9058 |  |  | 9058 |  |  | -2998 | -2998 | -2998 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250926 | September | 2230 | 9058 |  |  | 9058 |  |  | -2998 | -2998 | -2998 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250926 | September | 2330 | 8458 |  |  | 8458 |  |  | -2380 | -2380 | -2380 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250927 | September | 0030 | 9209 |  |  | 8446 |  |  | -934 | -934 | -171 | Critical Branch | Validation phase | 0 | 763 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8196; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 0130 | 9209 |  |  | 8446 |  |  | -934 | -934 | -171 | Critical Branch | Validation phase | 0 | 763 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8196; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 0230 | 9209 |  |  | 8446 |  |  | -934 | -934 | -171 | Critical Branch | Validation phase | 0 | 763 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8196; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 0330 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 0 | 485 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8321; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0430 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 0 | 485 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8321; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0530 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 0 | 485 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8321; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0630 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 0 | 485 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8321; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0730 | 8766 |  |  | 8398 |  |  | -982 | -982 | -614 | Critical Branch | Validation phase | 0 | 368 | NA | NA | NA | 0 | 1 | AT: 410; AT: 140; CH: 8148; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0830 | 7966 |  |  | 7598 |  |  | -102 | -102 | 266 | Critical Branch | Validation phase | 0 | 368 | NA | NA | NA | 634 | 1 | AT: 409; AT: 140; CH: 7348; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0930 | 8053 |  |  | 7284 |  |  | -2656 | -2656 | -1887 | Critical Branch | Validation phase | 0 | 769 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 7034; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1030 | 8053 |  |  | 7284 |  |  | -2656 | -2656 | -1887 | Critical Branch | Validation phase | 0 | 769 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 7034; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1130 | 8053 |  |  | 7284 |  |  | -2656 | -2656 | -1887 | Critical Branch | Validation phase | 0 | 769 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140; CH: 7034; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1230 | 7550 |  |  | 7331 |  |  | -1824 | -1824 | -1605 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140; CH: 7081; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1330 | 7550 |  |  | 7331 |  |  | -1824 | -1824 | -1605 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140; CH: 7081; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1430 | 7550 |  |  | 7331 |  |  | -1824 | -1824 | -1605 | Critical Branch | Validation phase | 0 | 219 | NA | NA | NA | 0 | 1 | AT: 386; AT: 140; CH: 7081; CH: Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1530 | 8257 |  |  | 7819 |  |  | -5633 | -5633 | -5195 | Critical Branch | Validation phase | 0 | 438 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 7569; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250927 | September | 1630 | 8257 |  |  | 7819 |  |  | -5633 | -5633 | -5195 | Critical Branch | Validation phase | 0 | 438 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 7569; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250927 | September | 1730 | 9057 |  |  | 8619 |  |  | -6428 | -6428 | -5990 | Critical Branch | Validation phase | 0 | 438 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140; CH: 8369; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250927 | September | 1830 |  | 8537 | 928 |  | 8239 | 907 | -2445 | -2445 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 298 | 21 | 319 | 2445 | 1 | AT: 213; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 1930 |  | 8537 | 928 |  | 8239 | 907 | -2445 | -2445 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 298 | 21 | 319 | 2445 | 1 | AT: 213; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2030 |  | 8537 | 928 |  | 8239 | 907 | -2445 | -2445 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 298 | 21 | 319 | 2445 | 1 | AT: 213; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2130 | 9217 |  |  | 8295 |  |  | -2545 | -2545 | -1623 | Critical Branch | Validation phase | 0 | 922 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8045; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2230 | 9217 |  |  | 8295 |  |  | -2545 | -2545 | -1623 | Critical Branch | Validation phase | 0 | 922 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8045; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3800; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2330 | 8617 |  |  | 7695 |  |  | -1935 | -1935 | -1013 | Critical Branch | Validation phase | 0 | 922 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 7445; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250928 | September | 0030 | 9346 |  |  | 8626 |  |  | -1418 | -1418 | -701 | Critical Branch | Validation phase | 0 | 720 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8591; CH: Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0130 | 9346 |  |  | 8626 |  |  | -1418 | -1418 | -701 | Critical Branch | Validation phase | 0 | 720 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8591; CH: Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0230 | 9346 |  |  | 8626 |  |  | -1418 | -1418 | -701 | Critical Branch | Validation phase | 0 | 720 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8591; CH: Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0330 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8282; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0430 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8282; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0530 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8282; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0630 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8282; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0730 | 8078 |  |  | 8077 |  |  | -6816 | -6816 | -6816 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 395; AT: 160
20250928 | September | 0830 | 8078 |  |  | 7750 |  |  | -6816 | -6816 | -6485 | Critical Branch | Critical Branch | 0 | 328 | NA | NA | NA | 0 | 1 | AT: 380; AT: 160
20250928 | September | 0930 | 6280 |  |  | 6250 |  |  | -6797 | -6797 | -6767 | TTC Selection - LTTC | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 301; AT: 160; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250928 | September | 1030 | 6280 |  |  | 6250 |  |  | -6797 | -6797 | -6767 | TTC Selection - LTTC | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 301; AT: 160; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250928 | September | 1130 | 6280 |  |  | 6250 |  |  | -6797 | -6797 | -6767 | TTC Selection - LTTC | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 301; AT: 160; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250928 | September | 1230 | 6280 |  |  | 6279 |  |  | -5763 | -5763 | -5762 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 301; AT: 160
20250928 | September | 1330 | 6280 |  |  | 6279 |  |  | -5763 | -5763 | -5762 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 301; AT: 160
20250928 | September | 1430 | 6280 |  |  | 6279 |  |  | -5763 | -5763 | -5762 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 301; AT: 160
20250928 | September | 1530 |  | 6956 | 601 |  | 6956 | 601 | -5043 | -5043 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5043 | 1 | AT: 361; AT: 160
20250928 | September | 1630 |  | 6956 | 601 |  | 6956 | 601 | -5043 | -5043 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5043 | 1 | AT: 361; AT: 160
20250928 | September | 1730 |  | 6956 | 601 |  | 6956 | 601 | -5043 | -5043 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5043 | 1 | AT: 361; AT: 160
20250928 | September | 1830 |  | 9142 | 801 |  | 8360 | 781 | -5355 | -5355 | 0 | Critical Branch | Validation phase | 0 | NA | 782 | 20 | 802 | 5355 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 9201; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 1930 |  | 9142 | 801 |  | 8360 | 781 | -5355 | -5355 | 0 | Critical Branch | Validation phase | 0 | NA | 782 | 20 | 802 | 5355 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 9201; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2030 |  | 9142 | 801 |  | 8360 | 781 | -5355 | -5355 | 0 | Critical Branch | Validation phase | 0 | NA | 782 | 20 | 802 | 5355 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; CH: 9201; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2130 | 9661 |  |  | 8842 |  |  | -2755 | -2755 | -1945 | Critical Branch | Validation phase | 0 | 819 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 9029; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2230 | 9661 |  |  | 8842 |  |  | -2755 | -2755 | -1945 | Critical Branch | Validation phase | 0 | 819 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 9029; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2330 | 9661 |  |  | 8842 |  |  | -2755 | -2755 | -1945 | Critical Branch | Validation phase | 0 | 819 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 9029; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0030 | 9061 |  |  | 8433 |  |  | -2324 | -2324 | -1696 | Critical Branch | Validation phase | 0 | 628 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0130 | 9061 |  |  | 8433 |  |  | -2324 | -2324 | -1696 | Critical Branch | Validation phase | 0 | 628 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0230 | 9061 |  |  | 8433 |  |  | -2324 | -2324 | -1696 | Critical Branch | Validation phase | 0 | 628 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0330 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 0 | 766 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0430 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 0 | 766 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0530 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 0 | 766 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0630 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 0 | 766 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0730 |  | 7848 | 610 |  | 7848 | 610 | -2298 | -2298 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 0 | 0 | 2298 | 1 | AT: 391; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 0830 |  | 7848 | 610 |  | 7848 | 610 | -2298 | -2298 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 0 | 0 | 2298 | 1 | AT: 391; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 0930 | 8490 |  |  | 8490 |  |  | -3441 | -3441 | -3441 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 1030 | 8490 |  |  | 8490 |  |  | -3441 | -3441 | -3441 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 1130 | 8490 |  |  | 8490 |  |  | -3441 | -3441 | -3441 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 1230 | 9367 |  |  | 8806 |  |  | -2313 | -2313 | -1797 | Critical Branch | Validation phase | 0 | 561 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1330 | 9367 |  |  | 8806 |  |  | -2313 | -2313 | -1797 | Critical Branch | Validation phase | 0 | 561 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1430 | 9367 |  |  | 8806 |  |  | -2313 | -2313 | -1797 | Critical Branch | Validation phase | 0 | 561 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1530 |  | 8141 | 629 |  | 8061 | 629 | -2209 | -2209 | 0 | Critical Branch | Validation phase | 0 | NA | 80 | 0 | 80 | 2209 | 1 | AT: 406; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1630 |  | 8141 | 629 |  | 8061 | 629 | -2209 | -2209 | 0 | Critical Branch | Validation phase | 0 | NA | 80 | 0 | 80 | 2209 | 1 | AT: 406; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1730 |  | 8141 | 629 |  | 8061 | 629 | -2209 | -2209 | 0 | Critical Branch | Validation phase | 0 | NA | 80 | 0 | 80 | 2209 | 1 | AT: 406; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1830 |  | 7939 | 897 |  | 7743 | 882 | -3533 | -3533 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 196 | 15 | 211 | 3533 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1930 |  | 7939 | 897 |  | 7743 | 882 | -3533 | -3533 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 196 | 15 | 211 | 3533 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 2030 |  | 7939 | 897 |  | 7743 | 882 | -3533 | -3533 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 196 | 15 | 211 | 3533 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 2130 | 8366 |  |  | 8366 |  |  | -1576 | -1576 | -1576 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 2230 | 8366 |  |  | 8366 |  |  | -1576 | -1576 | -1576 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 2330 | 7766 |  |  | 7766 |  |  | -966 | -966 | -965 | Critical Branch | Validation phase | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 379; AT: 160; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0030 | 9072 |  |  | 8433 |  |  | -3400 | -3400 | -2761 | Critical Branch | Validation phase | 0 | 639 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 0130 | 9072 |  |  | 8433 |  |  | -3400 | -3400 | -2761 | Critical Branch | Validation phase | 0 | 639 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 0230 | 9072 |  |  | 8433 |  |  | -3400 | -3400 | -2761 | Critical Branch | Validation phase | 0 | 639 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 0330 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 0 | 204 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0430 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 0 | 204 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0530 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 0 | 204 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0630 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 0 | 204 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; CH: 8200; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0730 |  | 6841 | 684 |  | 6841 | 683 | -5646 | -5646 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 1 | 1 | 5646 | 1 | AT: 344; AT: 115; CH: 8800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0830 |  | 6841 | 664 |  | 6841 | 664 | -5615 | -5615 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 0 | 0 | 5615 | 1 | AT: 292; AT: 99; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0930 | 9241 |  |  | 8746 |  |  | -2853 | -2853 | -2354 | Critical Branch | Validation phase | 0 | 495 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1030 | 9241 |  |  | 8746 |  |  | -2853 | -2853 | -2354 | Critical Branch | Validation phase | 0 | 495 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1130 | 9241 |  |  | 8746 |  |  | -2853 | -2853 | -2354 | Critical Branch | Validation phase | 0 | 495 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1230 | 9612 |  |  | 8746 |  |  | -6332 | -6332 | -5379 | Critical Branch | Validation phase | 0 | 866 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1330 | 9612 |  |  | 8746 |  |  | -6332 | -6332 | -5379 | Critical Branch | Validation phase | 0 | 866 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1430 | 9612 |  |  | 8746 |  |  | -6332 | -6332 | -5379 | Critical Branch | Validation phase | 0 | 866 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1530 |  | 7903 | 770 |  | 7727 | 765 | -3609 | -3609 | 0 | Critical Branch | Validation phase | 0 | NA | 176 | 5 | 181 | 3609 | 1 | AT: 356; AT: 116; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1630 |  | 7903 | 770 |  | 7727 | 498 | -3609 | -3609 | 0 | Critical Branch | Validation phase | 0 | NA | 176 | 272 | 448 | 3609 | 1 | AT: 356; AT: 116; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1730 |  | 7903 | 770 |  | 7727 | 235 | -3609 | -3609 | 0 | Critical Branch | Validation phase | 0 | NA | 176 | 535 | 711 | 3609 | 1 | AT: 356; AT: 116; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV; IT: 153; IT: Forecasted Security Violations
20250930 | September | 1830 |  | 7528 | 733 |  | 7528 | 235 | -5528 | -5528 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 498 | 498 | 5528 | 1 | AT: 184; AT: 110; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 153; IT: Forecasted Security Violations
20250930 | September | 1930 |  | 7528 | 733 |  | 7528 | 235 | -5528 | -5528 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 498 | 498 | 5528 | 1 | AT: 184; AT: 110; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 153; IT: Forecasted Security Violations
20250930 | September | 2030 |  | 7528 | 733 |  | 7528 | 235 | -5528 | -5528 | 0 | Critical Branch | Validation phase | 0 | NA | 0 | 498 | 498 | 5528 | 1 | AT: 184; AT: 110; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 153; IT: Forecasted Security Violations
20250930 | September | 2130 |  | 8446 | 658 |  | 8181 | 184 | -5193 | -5193 | 0 | Critical Branch | Validation phase | 0 | NA | 265 | 474 | 739 | 5193 | 1 | AT: 365; AT: 119; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV; IT: 153; IT: Forecasted Security Violations
20250930 | September | 2230 |  | 8446 | 658 |  | 8181 | 417 | -5193 | -5193 | 0 | Critical Branch | Validation phase | 0 | NA | 265 | 241 | 506 | 5193 | 1 | AT: 365; AT: 119; CH: 8740; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 3600; FR: Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 2330 |  | 7866 | 683 |  | 7865 | 610 | -4560 | -4560 | 0 | Critical Branch | Validation phase | 0 | NA | 1 | 73 | 74 | 4560 | 1 | AT: 355; AT: 139; CH: 8140; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.

## DA 70% Reduction
DA 70% reduction results
|  |  | TTC Adjustment |  |  | ANTC |  | LimitedBy
BD | Month | TS | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | Adjustment | 70% reduction | % reduction | Category
20250702 | July | 1230 | 6684 |  |  | 890 | 469 | Minimum Margin | 421 | 47.3% | [500-1000] MW
20250702 | July | 1330 | 6426 |  |  | 890 | 211 | Minimum Margin | 679 | 76.29% | [500-1000] MW
20250702 | July | 1430 | 6383 |  |  | 890 | 168 | Minimum Margin | 722 | 81.12% | [500-1000] MW
20250704 | July | 1230 | 7075 |  |  | 7348 | 345 | Minimum Margin | 7003 | 95.3% | above 1000 MW
20250704 | July | 1330 | 7071 |  |  | 7348 | 341 | Minimum Margin | 7007 | 95.36% | above 1000 MW
20250704 | July | 1430 | 7049 |  |  | 7348 | 319 | Minimum Margin | 7029 | 95.66% | above 1000 MW
20250710 | July | 1530 | 8128 |  |  | 1562 | 168 | Minimum Margin | 1394 | 89.24% | above 1000 MW
20250710 | July | 1630 | 7962 |  |  | 1562 | 2 | Minimum Margin | 1560 | 99.87% | above 1000 MW
20250710 | July | 1730 | 7960 |  |  | 1562 | 0 | Critical Branch | 1562 | 100% | above 1000 MW
20250724 | July | 0930 | 8513 |  |  | 2489 | 0 | Critical Branch | 2489 | 100% | above 1000 MW
20250724 | July | 1030 | 8513 |  |  | 2489 | 0 | Critical Branch | 2489 | 100% | above 1000 MW
20250724 | July | 1130 | 8725 |  |  | 2489 | 212 | Minimum Margin | 2277 | 91.48% | above 1000 MW
20250724 | July | 1230 | 7199 |  |  | 2962 | 58 | Minimum Margin | 2904 | 98.04% | above 1000 MW
20250724 | July | 1330 | 7199 |  |  | 2962 | 58 | Minimum Margin | 2904 | 98.04% | above 1000 MW
20250724 | July | 1430 | 7199 |  |  | 2962 | 58 | Minimum Margin | 2904 | 98.04% | above 1000 MW
20250725 | July | 1230 | 6790 |  |  | 4626 | 60 | Minimum Margin | 4566 | 98.7% | above 1000 MW
20250725 | July | 1330 | 6790 |  |  | 4626 | 60 | Minimum Margin | 4566 | 98.7% | above 1000 MW
20250725 | July | 1430 | 6790 |  |  | 4626 | 60 | Minimum Margin | 4566 | 98.7% | above 1000 MW
20250725 | July | 1530 | 7975 |  |  | 4168 | 87 | Minimum Margin | 4081 | 97.91% | above 1000 MW
20250725 | July | 1630 | 7975 |  |  | 4168 | 87 | Minimum Margin | 4081 | 97.91% | above 1000 MW
20250725 | July | 1730 | 7975 |  |  | 4168 | 87 | Minimum Margin | 4081 | 97.91% | above 1000 MW
20250728 | July | 0930 | 7977 |  |  | 4119 | 280 | Minimum Margin | 3839 | 93.2% | above 1000 MW
20250728 | July | 1030 | 7977 |  |  | 4119 | 280 | Minimum Margin | 3839 | 93.2% | above 1000 MW
20250728 | July | 1130 | 7977 |  |  | 4119 | 280 | Minimum Margin | 3839 | 93.2% | above 1000 MW
20250811 | August | 0930 | 5378 |  |  | 2680 | 432 | Minimum Margin | 2248 | 83.88% | above 1000 MW
20250811 | August | 1030 | 5378 |  |  | 2680 | 432 | Minimum Margin | 2248 | 83.88% | above 1000 MW
20250811 | August | 1130 | 5378 |  |  | 2680 | 432 | Minimum Margin | 2248 | 83.88% | above 1000 MW
20250825 | August | 1230 | 6427 |  |  | 2363 | 362 | Minimum Margin | 2001 | 84.68% | above 1000 MW
20250825 | August | 1330 | 6435 |  |  | 2363 | 370 | Minimum Margin | 1993 | 84.34% | above 1000 MW
20250825 | August | 1430 | 6382 |  |  | 2363 | 317 | Minimum Margin | 2046 | 86.58% | above 1000 MW
20250827 | August | 1230 | 6145 |  |  | 3165 | 80 | Minimum Margin | 3085 | 97.47% | above 1000 MW
20250827 | August | 1330 | 6145 |  |  | 3165 | 80 | Minimum Margin | 3085 | 97.47% | above 1000 MW
20250827 | August | 1430 | 6145 |  |  | 3165 | 80 | Minimum Margin | 3085 | 97.47% | above 1000 MW
20250907 | September | 0930 | 5255 |  |  | 1845 | 575 | Minimum Margin | 1270 | 68.83% | above 1000 MW
20250907 | September | 1030 | 5255 |  |  | 1845 | 575 | Minimum Margin | 1270 | 68.83% | above 1000 MW
20250907 | September | 1130 | 5255 |  |  | 1845 | 575 | Minimum Margin | 1270 | 68.83% | above 1000 MW
20250926 | September | 1530 | 6184 |  |  | 200 | 104 | Minimum Margin | 96 | 48% | below 500 MW

## DA TTC Validation
DA Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | ANTC |  |  | LimitedBy |  | TTC Validation Reduction |  |  | Reason for TTC Reduction |  | Reason for TTC Reduction AT |  | Reason for TTC Reduction CH |  | Reason for TTC Reduction FR |  | Reason for TTC Reduction IT |  | Reason for TTC Reduction SI
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | Smoothing | Reason | Bilateral | Reason | MNII | Reason | Bilateral | Reason | MNII | Reason | MNII | Reason
20250701 | July | 0030 | 8326 |  |  | 7816 |  |  | -1564 | -1564 | -1054 | Critical Branch | Validation phase | 510 | NA | 0 |  |  |  |  | 7506 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250701 | July | 0130 | 8326 |  |  | 7816 |  |  | -1564 | -1564 | -1054 | Critical Branch | Validation phase | 510 | NA | 0 |  |  |  |  | 7506 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250701 | July | 0230 | 8326 |  |  | 7816 |  |  | -1564 | -1564 | -1054 | Critical Branch | Validation phase | 510 | NA | 0 |  |  |  |  | 7506 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250701 | July | 0330 | 8611 |  |  | 8493 |  |  | -1504 | -1504 | -1386 | Critical Branch | Validation phase | 118 | NA | 0 |  |  |  |  | 8183 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0430 | 8611 |  |  | 8493 |  |  | -1504 | -1504 | -1386 | Critical Branch | Validation phase | 118 | NA | 0 |  |  |  |  | 8183 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0530 | 8611 |  |  | 8493 |  |  | -1504 | -1504 | -1386 | Critical Branch | Validation phase | 118 | NA | 0 |  |  |  |  | 8183 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0630 | 8411 |  |  | 8293 |  |  | -1283 | -1283 | -1165 | Critical Branch | Validation phase | 118 | NA | 0 |  |  |  |  | 7983 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0730 | 8206 |  |  | 8158 |  |  | -5053 | -5053 | -5005 | Critical Branch | Validation phase | 48 | NA | 0 |  |  |  |  | 7843 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 0830 | 8206 |  |  | 7990 |  |  | -5053 | -5053 | -4837 | Critical Branch | Smoothing ramp | 216 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7843 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 1130 | 6490 |  |  | 6441 |  |  | -70 | -70 | -21 | TTC Selection - LTTC | Smoothing ramp | 49 | NA | 0 | Smoothing | Smoothing ramp
20250701 | July | 1230 | 6490 |  |  | 4941 |  |  | -169 | -169 | 1380 | TTC Selection - LTTC | Validation phase | 1549 | NA | 2929 |  |  |  |  | 4626 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA
20250701 | July | 1330 | 6490 |  |  | 4941 |  |  | -169 | -169 | 1380 | TTC Selection - LTTC | Validation phase | 1549 | NA | 2929 |  |  |  |  | 4626 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA
20250701 | July | 1430 | 6490 |  |  | 4941 |  |  | -169 | -169 | 1380 | TTC Selection - LTTC | Validation phase | 1549 | NA | 2929 |  |  |  |  | 4626 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA
20250701 | July | 1530 |  | 6570 | 564 |  | 6216 | 564 | 77 | 77 | 0 | Adjustment reached | Smoothing ramp | NA | 354 | -77 | Smoothing | Smoothing ramp
20250701 | July | 1830 |  | 7763 | 620 |  | 7712 | 616 | -1898 | -1898 | 0 | Critical Branch | Validation phase | NA | 55 | 1898 |  |  |  |  | 7722 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 1930 |  | 7763 | 620 |  | 7712 | 616 | -1898 | -1898 | 0 | Critical Branch | Validation phase | NA | 55 | 1898 |  |  |  |  | 7722 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2030 |  | 7763 | 620 |  | 7712 | 616 | -1898 | -1898 | 0 | Critical Branch | Validation phase | NA | 55 | 1898 |  |  |  |  | 7722 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2130 |  | 7611 | 625 |  | 7578 | 622 | -1834 | -1834 | 0 | Critical Branch | Validation phase | NA | 36 | 1834 |  |  |  |  | 7565 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2230 |  | 7611 | 625 |  | 7578 | 622 | -1834 | -1834 | 0 | Critical Branch | Validation phase | NA | 36 | 1834 |  |  |  |  | 7565 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250701 | July | 2330 |  | 7046 | 650 |  | 7033 | 649 | -1205 | -1205 | 0 | Critical Branch | Validation phase | NA | 14 | 1205 |  |  |  |  | 6985 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250702 | July | 0030 | 7084 |  |  | 7084 |  |  | -3447 | -3447 | -3446 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 187 |  | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0130 | 7084 |  |  | 7084 |  |  | -3447 | -3447 | -3446 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 187 |  | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0230 | 7084 |  |  | 7084 |  |  | -3447 | -3447 | -3446 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 187 |  | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0330 | 8923 |  |  | 8299 |  |  | -4881 | -4881 | -4257 | Critical Branch | Validation phase | 624 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0430 | 8923 |  |  | 8299 |  |  | -4881 | -4881 | -4257 | Critical Branch | Validation phase | 624 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0530 | 8923 |  |  | 8000 |  |  | -4881 | -4881 | -3959 | Critical Branch | Validation phase | 923 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0630 | 8723 |  |  | 6500 |  |  | -4673 | -4673 | -2456 | Critical Branch | Validation phase | 2223 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0730 | 7335 |  |  | 5000 |  |  | -1788 | -1788 | 547 | Critical Branch | Validation phase | 2335 | NA | 2882 |  |  | 190 |  | 4685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0830 | 7335 |  |  | 5000 |  |  | -1788 | -1788 | 547 | Critical Branch | Validation phase | 2335 | NA | 2882 |  |  | 176 |  | 4685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 0930 | 5315 |  |  | 5000 |  |  | -84 | -84 | 231 | TTC Selection - LTTC | Validation phase | 315 | NA | 546 |  |  | 164 |  | 4685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1030 | 5315 |  |  | 5000 |  |  | -84 | -84 | 231 | TTC Selection - LTTC | Validation phase | 315 | NA | 546 |  |  | 164 |  | 4685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1130 | 5315 |  |  | 5000 |  |  | -84 | -84 | 231 | TTC Selection - LTTC | Validation phase | 315 | NA | 546 |  |  | 164 |  | 4685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1230 | 6684 |  |  | 5500 |  |  | 890 | 469 | 1605 | Minimum Margin | Validation phase | 1184 | NA | 2741 |  |  | 178 |  | 5185 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250702 | July | 1330 | 6426 |  |  | 5500 |  |  | 890 | 211 | 1605 | Minimum Margin | Validation phase | 926 | NA | 2999 |  |  | 173 |  | 5185 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250702 | July | 1430 | 6383 |  |  | 5500 |  |  | 890 | 168 | 1605 | Minimum Margin | Validation phase | 883 | NA | 3042 |  |  | 172 |  | 5185 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250702 | July | 1530 | 6215 |  |  | 5500 |  |  | -621 | -621 | 94 | TTC Selection - LTTC | Validation phase | 715 | NA | 809 |  |  | 169 |  | 5185 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1630 | 6215 |  |  | 5500 |  |  | -621 | -621 | 94 | TTC Selection - LTTC | Validation phase | 715 | NA | 809 |  |  | 169 |  | 5185 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1730 | 6515 |  |  | 6000 |  |  | -940 | -940 | -425 | TTC Selection - LTTC | Validation phase | 515 | NA | 0 |  |  | 171 |  | 5685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1830 |  | 8103 | 700 |  | 5715 | 565 | -2249 | -2249 | 0 | Critical Branch | Validation phase | NA | 2523 | 2249 |  |  | 197 |  | 5685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 1930 |  | 8103 | 700 |  | 5715 | 32 | -2249 | -2249 | 0 | Critical Branch | Validation phase | NA | 3056 | 2249 |  |  | 206 |  | 5685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 870 | Forecasted Security Violations
20250702 | July | 2030 |  | 8103 | 700 |  | 5715 | 32 | -2249 | -2249 | 0 | Critical Branch | Validation phase | NA | 3056 | 2249 |  |  | 206 |  | 5685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 870 | Forecasted Security Violations
20250702 | July | 2130 |  | 8376 | 715 |  | 5706 | 32 | -6111 | -6111 | 0 | Critical Branch | Validation phase | NA | 3353 | 6111 |  |  | 210 | Reduction because NTC over thermal limit on border | 5685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 870 | Forecasted Security Violations
20250702 | July | 2230 |  | 8376 | 715 |  | 6706 | 577 | -6111 | -6111 | 0 | Critical Branch | Validation phase | NA | 1808 | 6111 |  |  | 210 | Reduction because NTC over thermal limit on border | 6685 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250702 | July | 2330 |  | 7806 | 740 |  | 7804 | 740 | -5498 | -5498 | 0 | Critical Branch | Validation phase | NA | 2 | 5498 |  |  | 210 | Reduction because NTC over thermal limit on border | 7990 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250703 | July | 0030 | 8972 |  |  | 8920 |  |  | -1700 | -1700 | -1648 | Critical Branch | Validation phase | 52 | NA | 0 |  |  |  |  | 8610 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250703 | July | 0130 | 8972 |  |  | 8920 |  |  | -1700 | -1700 | -1648 | Critical Branch | Validation phase | 52 | NA | 0 |  |  |  |  | 8610 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250703 | July | 0230 | 8972 |  |  | 8920 |  |  | -1700 | -1700 | -1648 | Critical Branch | Validation phase | 52 | NA | 0 |  |  |  |  | 8610 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250703 | July | 0730 | 8485 |  |  | 7907 |  |  | -1743 | -1743 | -1165 | Critical Branch | Validation phase | 578 | NA | 0 |  |  |  |  | 7592 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 0830 | 8485 |  |  | 7907 |  |  | -1743 | -1743 | -1165 | Critical Branch | Validation phase | 578 | NA | 0 |  |  |  |  | 7592 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 0930 | 7530 |  |  | 6692 |  |  | -3717 | -3717 | -2879 | Critical Branch | Validation phase | 838 | NA | 0 |  |  |  |  | 6377 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1030 | 7530 |  |  | 6692 |  |  | -3717 | -3717 | -2879 | Critical Branch | Validation phase | 838 | NA | 0 |  |  |  |  | 6377 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1130 | 7530 |  |  | 6692 |  |  | -3717 | -3717 | -2879 | Critical Branch | Validation phase | 838 | NA | 0 |  |  |  |  | 6377 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1230 | 8371 |  |  | 7065 |  |  | -646 | -646 | 660 | Critical Branch | Validation phase | 1306 | NA | 1966 |  |  |  |  | 6750 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1330 | 8371 |  |  | 7065 |  |  | -646 | -646 | 660 | Critical Branch | Validation phase | 1306 | NA | 1966 |  |  |  |  | 6750 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1430 | 8371 |  |  | 7065 |  |  | -646 | -646 | 660 | Critical Branch | Validation phase | 1306 | NA | 1966 |  |  |  |  | 6750 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1530 | 8678 |  |  | 7847 |  |  | -1197 | -1197 | -366 | Critical Branch | Validation phase | 831 | NA | 0 |  |  |  |  | 7532 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1630 | 8678 |  |  | 7847 |  |  | -1197 | -1197 | -366 | Critical Branch | Validation phase | 831 | NA | 0 |  |  |  |  | 7532 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1730 | 8678 |  |  | 7847 |  |  | -1197 | -1197 | -366 | Critical Branch | Validation phase | 831 | NA | 0 |  |  |  |  | 7532 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250703 | July | 1830 |  | 8780 | 693 |  | 8780 | 556 | -2553 | -2553 | 0 | Critical Branch | Smoothing ramp | NA | 137 | 2553 | Smoothing | Smoothing ramp
20250703 | July | 2230 |  | 8764 | 702 |  | 8764 | 563 | -5778 | -5778 | 0 | Critical Branch | Smoothing ramp | NA | 139 | 5778 | Smoothing | Smoothing ramp
20250704 | July | 0030 | 8382 |  |  | 8023 |  |  | -3583 | -3583 | -3224 | Critical Branch | Validation phase | 359 | NA | 0 |  |  | 411 |  | 7713 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0130 | 8382 |  |  | 8023 |  |  | -3583 | -3583 | -3224 | Critical Branch | Validation phase | 359 | NA | 0 |  |  | 411 |  | 7713 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0230 | 8382 |  |  | 8023 |  |  | -3583 | -3583 | -3224 | Critical Branch | Validation phase | 359 | NA | 0 |  |  | 411 |  | 7713 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0330 | 8424 |  |  | 7680 |  |  | -4785 | -4785 | -4041 | Critical Branch | Validation phase | 744 | NA | 0 |  |  | 413 |  | 7370 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0430 | 8424 |  |  | 7680 |  |  | -4785 | -4785 | -4041 | Critical Branch | Validation phase | 744 | NA | 0 |  |  | 413 |  | 7370 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0530 | 8424 |  |  | 7680 |  |  | -4785 | -4785 | -4041 | Critical Branch | Validation phase | 744 | NA | 0 |  |  | 413 |  | 7370 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0630 | 8224 |  |  | 7480 |  |  | -4580 | -4580 | -3836 | Critical Branch | Validation phase | 744 | NA | 0 |  |  | 413 |  | 7170 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250704 | July | 0730 | 8343 |  |  | 7347 |  |  | -4371 | -4371 | -3375 | Critical Branch | Validation phase | 996 | NA | 0 |  |  | 400 |  | 7032 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0830 | 8343 |  |  | 7347 |  |  | -4371 | -4371 | -3375 | Critical Branch | Validation phase | 996 | NA | 0 |  |  | 400 |  | 7032 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 0930 | 7021 |  |  | 6640 |  |  | -3512 | -3512 | -3131 | Critical Branch | Validation phase | 381 | NA | 0 |  |  | 343 |  | 6325 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1030 | 7021 |  |  | 6640 |  |  | -3512 | -3512 | -3131 | Critical Branch | Validation phase | 381 | NA | 0 |  |  | 343 |  | 6325 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1130 | 7021 |  |  | 6403 |  |  | -3512 | -3512 | -2893 | Critical Branch | Validation phase | 618 | NA | 0 |  |  | 343 |  | 6325 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1230 | 7075 |  |  | 4903 |  |  | 7348 | 345 | 9175 | Minimum Margin | Validation phase | 2172 | NA | 18005 |  |  | 346 |  | 4588 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250704 | July | 1330 | 7071 |  |  | 4903 |  |  | 7348 | 341 | 9175 | Minimum Margin | Validation phase | 2168 | NA | 18009 |  |  | 346 |  | 4588 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250704 | July | 1430 | 7049 |  |  | 4903 |  |  | 7348 | 319 | 9175 | Minimum Margin | Validation phase | 2146 | NA | 18031 |  |  | 345 |  | 4588 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250704 | July | 1530 | 7819 |  |  | 6092 |  |  | -663 | -663 | 1064 | Critical Branch | Validation phase | 1727 | NA | 2791 |  |  | 378 |  | 5777 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1630 | 7819 |  |  | 6092 |  |  | -663 | -663 | 1064 | Critical Branch | Validation phase | 1727 | NA | 2791 |  |  | 378 |  | 5777 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1730 | 7819 |  |  | 6092 |  |  | -663 | -663 | 1064 | Critical Branch | Validation phase | 1727 | NA | 2791 |  |  | 378 |  | 5777 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1830 |  | 8571 | 678 |  | 7333 | 482 | -2320 | -2320 | 0 | Critical Branch | Validation phase | NA | 1434 | 2320 |  |  | 425 | Reduction because NTC over thermal limit on border | 8526 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 1930 |  | 8571 | 678 |  | 8353 | 244 | -2320 | -2320 | 0 | Critical Branch | Validation phase | NA | 652 | 2320 |  |  | 425 | Reduction because NTC over thermal limit on border | 8526 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 2030 |  | 8571 | 678 |  | 8353 | 244 | -2320 | -2320 | 0 | Critical Branch | Validation phase | NA | 652 | 2320 |  |  | 425 | Reduction because NTC over thermal limit on border | 8526 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250704 | July | 2130 |  | 8519 | 683 |  | 8517 | 244 | -2730 | -2730 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 441 | 2730 |  |  | 425 | Reduction because NTC over thermal limit on border
20250704 | July | 2230 |  | 8519 | 683 |  | 8517 | 496 | -2730 | -2730 | 0 | Critical Branch | Critical Branch | NA | 189 | 2730 |  |  | 425 | Reduction because NTC over thermal limit on border
20250704 | July | 2330 |  | 7939 | 708 |  | 7938 | 690 | -2084 | -2084 | 0 | Critical Branch | Critical Branch | NA | 19 | 2084 |  |  | 415
20250705 | July | 0030 | 9031 |  |  | 9005 |  |  | -5384 | -5384 | -5351 | Critical Branch | Critical Branch | 26 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0130 | 9031 |  |  | 9005 |  |  | -5384 | -5384 | -5351 | Critical Branch | Critical Branch | 26 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0230 | 9031 |  |  | 9005 |  |  | -5384 | -5384 | -5351 | Critical Branch | Critical Branch | 26 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0330 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 32 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0430 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 32 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0530 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 32 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0630 | 9151 |  |  | 9119 |  |  | -5495 | -5495 | -5456 | Critical Branch | Critical Branch | 32 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250705 | July | 0730 | 8707 |  |  | 8574 |  |  | -5369 | -5369 | -5236 | Critical Branch | Validation phase | 133 | NA | 0 |  |  | 410 |  | 8259 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 0830 | 8707 |  |  | 8379 |  |  | -5369 | -5369 | -5036 | Critical Branch | Validation phase | 328 | NA | 0 |  |  | 394 |  | 8259 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 0930 | 6880 |  |  | 6879 |  |  | -3721 | -3721 | -3720 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 332
20250705 | July | 1030 | 6880 |  |  | 6879 |  |  | -3721 | -3721 | -3720 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 332
20250705 | July | 1130 | 6880 |  |  | 6879 |  |  | -3721 | -3721 | -3720 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 332
20250705 | July | 1230 | 6880 |  |  | 6879 |  |  | -10 | -10 | -9 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 332
20250705 | July | 1330 | 6880 |  |  | 6879 |  |  | -10 | -10 | -9 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 332
20250705 | July | 1430 | 6880 |  |  | 6879 |  |  | -10 | -10 | -9 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 332
20250705 | July | 1530 | 7032 |  |  | 7032 |  |  | -3626 | -3626 | -3626 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 339
20250705 | July | 1630 | 7032 |  |  | 7032 |  |  | -3626 | -3626 | -3626 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 339
20250705 | July | 1730 | 7032 |  |  | 7032 |  |  | -3626 | -3626 | -3626 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 339
20250705 | July | 1830 |  | 8443 | 693 |  | 8245 | 681 | -2402 | -2402 | 0 | Critical Branch | Validation phase | NA | 210 | 2402 |  |  | 412 |  | 8416 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 1930 |  | 8443 | 693 |  | 8294 | 681 | -2402 | -2402 | 0 | Critical Branch | Validation phase | NA | 161 | 2402 |  |  | 423 |  | 8416 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 2030 |  | 8443 | 693 |  | 8294 | 681 | -2402 | -2402 | 0 | Critical Branch | Validation phase | NA | 161 | 2402 |  |  | 423 |  | 8416 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250705 | July | 2130 | 9087 |  |  | 9063 |  |  | -5088 | -5088 | -5065 | Critical Branch | Validation phase | 24 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8749 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250705 | July | 2230 | 9087 |  |  | 9063 |  |  | -5088 | -5088 | -5065 | Critical Branch | Validation phase | 24 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8749 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250705 | July | 2330 | 8487 |  |  | 8463 |  |  | -4479 | -4479 | -4456 | Critical Branch | Validation phase | 24 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8154 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250706 | July | 0030 | 8740 |  |  | 8727 |  |  | -2253 | -2253 | -2241 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0130 | 8740 |  |  | 8727 |  |  | -2253 | -2253 | -2241 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0230 | 8740 |  |  | 8727 |  |  | -2253 | -2253 | -2241 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0330 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0430 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0530 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0630 | 8534 |  |  | 8530 |  |  | -793 | -793 | -789 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 0730 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250706 | July | 0830 | 8450 |  |  | 8071 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 379 | NA | 0 |  |  | 395
20250706 | July | 0930 | 6572 |  |  | 6571 |  |  | -367 | -367 | -366 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 330
20250706 | July | 1030 | 6572 |  |  | 6000 |  |  | -367 | -367 | 205 | Critical Branch | Validation phase | 572 | NA | 777 |  |  | 330 | [5 empty] | 5690 | Secure Value
20250706 | July | 1130 | 6572 |  |  | 6000 |  |  | -367 | -367 | 205 | Critical Branch | Validation phase | 572 | NA | 777 |  |  | 330 | [5 empty] | 5690 | Secure Value
20250706 | July | 1230 | 6280 |  |  | 5282 |  |  | -2875 | -2875 | -1877 | TTC Selection - LTTC | Validation phase | 998 | NA | 0 |  |  | 317 |  | 4972 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 5690 | Secure Value
20250706 | July | 1330 | 6280 |  |  | 5282 |  |  | -2875 | -2875 | -1877 | TTC Selection - LTTC | Validation phase | 998 | NA | 0 |  |  | 317 |  | 4972 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 5690 | Secure Value
20250706 | July | 1430 | 6280 |  |  | 5282 |  |  | -2875 | -2875 | -1877 | TTC Selection - LTTC | Validation phase | 998 | NA | 0 |  |  | 317 |  | 4972 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 5690 | Secure Value
20250706 | July | 1530 | 6437 |  |  | 6000 |  |  | -2307 | -2307 | -1870 | Critical Branch | Validation phase | 437 | NA | 0 |  |  | 324 | [5 empty] | 5690 | Secure Value
20250706 | July | 1630 | 6437 |  |  | 6000 |  |  | -2307 | -2307 | -1870 | Critical Branch | Validation phase | 437 | NA | 0 |  |  | 324 | [5 empty] | 5690 | Secure Value
20250706 | July | 1730 | 6437 |  |  | 6437 |  |  | -2307 | -2307 | -2307 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 324
20250706 | July | 1830 | 8923 |  |  | 7937 |  |  | -1659 | -1659 | -690 | Critical Branch | Validation phase | 986 | NA | 0 |  |  | 385 |  | 8523 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250706 | July | 1930 | 8923 |  |  | 8816 |  |  | -1659 | -1659 | -1558 | Critical Branch | Validation phase | 107 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8523 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250706 | July | 2030 | 8923 |  |  | 8816 |  |  | -1659 | -1659 | -1558 | Critical Branch | Validation phase | 107 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8523 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250706 | July | 2130 | 8682 |  |  | 8672 |  |  | -1531 | -1531 | -1524 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 2230 | 8682 |  |  | 8672 |  |  | -1531 | -1531 | -1524 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250706 | July | 2330 | 8682 |  |  | 8672 |  |  | -1531 | -1531 | -1524 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250707 | July | 0030 | 8016 |  |  | 8016 |  |  | -2085 | -2085 | -2085 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 395
20250707 | July | 0130 | 8016 |  |  | 8016 |  |  | -2085 | -2085 | -2085 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 395
20250707 | July | 0230 | 8016 |  |  | 8016 |  |  | -2085 | -2085 | -2085 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 395
20250707 | July | 0330 | 8411 |  |  | 8411 |  |  | -1954 | -1954 | -1953 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250707 | July | 0430 | 8411 |  |  | 8411 |  |  | -1954 | -1954 | -1953 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250707 | July | 0530 | 8411 |  |  | 8411 |  |  | -1954 | -1954 | -1953 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250707 | July | 0630 | 8211 |  |  | 8072 |  |  | -1715 | -1715 | -1576 | Critical Branch | Critical Branch | 139 | NA | 0 |  |  | 413
20250707 | July | 0730 | 6993 |  |  | 6572 |  |  | -2513 | -2513 | -2163 | Critical Branch | Validation phase | 421 | NA | 0 |  |  | 342 |  |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250707 | July | 0830 | 5693 |  |  | 5693 |  |  | -1332 | -1332 | -1332 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 327
20250707 | July | 0930 | 7718 |  |  | 7089 |  |  | -1709 | -1709 | -1080 | Critical Branch | Validation phase | 629 | NA | 0 |  |  | 399 |  | 6774 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250707 | July | 1030 | 7718 |  |  | 7089 |  |  | -1709 | -1709 | -1080 | Critical Branch | Validation phase | 629 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6774 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250707 | July | 1130 | 7718 |  |  | 7089 |  |  | -1709 | -1709 | -1080 | Critical Branch | Validation phase | 629 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6774 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250707 | July | 1230 | 7118 |  |  | 7118 |  |  | -3383 | -3383 | -3383 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 400
20250707 | July | 1330 | 7118 |  |  | 7118 |  |  | -3383 | -3383 | -3383 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 400
20250707 | July | 1430 | 7118 |  |  | 7118 |  |  | -3383 | -3383 | -3383 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 400
20250707 | July | 1530 | 7713 |  |  | 7707 |  |  | -4375 | -4375 | -4371 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250707 | July | 1630 | 7713 |  |  | 7707 |  |  | -4375 | -4375 | -4371 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250707 | July | 1730 | 7713 |  |  | 7707 |  |  | -4375 | -4375 | -4371 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250707 | July | 1830 |  | 6768 | 637 |  | 6767 | 637 | -2640 | -2640 | 0 | Critical Branch | Critical Branch | NA | 1 | 2640 |  |  | 402
20250707 | July | 1930 |  | 6768 | 637 |  | 6767 | 637 | -2640 | -2640 | 0 | Critical Branch | Critical Branch | NA | 1 | 2640 |  |  | 402
20250707 | July | 2030 |  | 6768 | 637 |  | 6767 | 637 | -2640 | -2640 | 0 | Critical Branch | Critical Branch | NA | 1 | 2640 |  |  | 402
20250707 | July | 2130 |  | 6847 | 660 |  | 6847 | 660 | -2085 | -2085 | 0 | Critical Branch | Critical Branch | NA | 0 | 2085 |  |  | 407
20250707 | July | 2230 |  | 6847 | 660 |  | 6847 | 660 | -2085 | -2085 | 0 | Critical Branch | Critical Branch | NA | 0 | 2085 |  |  | 407
20250707 | July | 2330 |  | 6267 | 685 |  | 6266 | 685 | -1463 | -1463 | 0 | Critical Branch | Critical Branch | NA | 1 | 1463 |  |  | 394
20250708 | July | 0030 | 7586 |  |  | 7563 |  |  | -4254 | -4254 | -4240 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0130 | 7586 |  |  | 7563 |  |  | -4254 | -4254 | -4240 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0230 | 7586 |  |  | 7563 |  |  | -4254 | -4254 | -4240 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0330 | 7466 |  |  | 7449 |  |  | -3932 | -3932 | -3921 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0430 | 7466 |  |  | 7449 |  |  | -3932 | -3932 | -3921 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0530 | 7466 |  |  | 7449 |  |  | -3932 | -3932 | -3921 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0630 | 7266 |  |  | 7248 |  |  | -3724 | -3724 | -3714 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250708 | July | 0730 | 7108 |  |  | 7107 |  |  | -4452 | -4452 | -4452 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 399
20250708 | July | 0830 | 7108 |  |  | 7107 |  |  | -4452 | -4452 | -4452 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 399
20250708 | July | 0930 | 6028 |  |  | 6027 |  |  | -1279 | -1279 | -1278 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 344
20250708 | July | 1030 | 6028 |  |  | 6027 |  |  | -1279 | -1279 | -1278 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 344
20250708 | July | 1130 | 6028 |  |  | 6027 |  |  | -1279 | -1279 | -1278 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 344
20250708 | July | 1230 | 6944 |  |  | 6944 |  |  | -1793 | -1793 | -1793 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20250708 | July | 1330 | 6729 |  |  | 6729 |  |  | -1643 | -1643 | -1643 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 196
20250708 | July | 1430 | 6729 |  |  | 6729 |  |  | -1643 | -1643 | -1643 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 196
20250708 | July | 1530 | 6207 |  |  | 6206 |  |  | -1233 | -1233 | -1233 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 184
20250708 | July | 1630 | 6207 |  |  | 6206 |  |  | -1233 | -1233 | -1233 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 184
20250708 | July | 1730 | 6422 |  |  | 6421 |  |  | -1386 | -1386 | -1385 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 364
20250708 | July | 1830 |  | 5470 | 515 |  | 5469 | 515 | -1793 | -1793 | 0 | Critical Branch | Critical Branch | NA | 1 | 1793 |  |  | 332
20250708 | July | 1930 |  | 5470 | 515 |  | 5469 | 515 | -1793 | -1793 | 0 | Critical Branch | Critical Branch | NA | 1 | 1793 |  |  | 332
20250708 | July | 2030 |  | 5470 | 515 |  | 5469 | 515 | -1793 | -1793 | 0 | Critical Branch | Critical Branch | NA | 1 | 1793 |  |  | 332
20250708 | July | 2130 | 5838 |  |  | 5838 |  |  | -1823 | -1823 | -1822 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 329
20250708 | July | 2230 | 5838 |  |  | 5838 |  |  | -1823 | -1823 | -1822 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 329
20250708 | July | 2330 | 5238 |  |  | 5238 |  |  | -1217 | -1217 | -1217 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 312
20250709 | July | 0030 | 7638 |  |  | 7585 |  |  | -4577 | -4577 | -4534 | Critical Branch | Validation phase | 53 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7300 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 0130 | 7638 |  |  | 7585 |  |  | -4577 | -4577 | -4534 | Critical Branch | Validation phase | 53 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7300 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 0230 | 7638 |  |  | 7585 |  |  | -4577 | -4577 | -4534 | Critical Branch | Validation phase | 53 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7300 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 0330 | 7228 |  |  | 7224 |  |  | -2065 | -2065 | -2063 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250709 | July | 0430 | 7228 |  |  | 7224 |  |  | -2065 | -2065 | -2063 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250709 | July | 0530 | 7228 |  |  | 7224 |  |  | -2065 | -2065 | -2063 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250709 | July | 0630 | 7028 |  |  | 7024 |  |  | -1852 | -1852 | -1850 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250709 | July | 0730 | 6861 |  |  | 6861 |  |  | -1648 | -1648 | -1647 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 387
20250709 | July | 0830 | 6861 |  |  | 6861 |  |  | -1648 | -1648 | -1647 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 387
20250709 | July | 0930 | 7554 |  |  | 7538 |  |  | -1599 | -1599 | -1583 | Critical Branch | Validation phase | 16 | NA | 0 |  |  | 422 |  | 7223 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 1030 | 7554 |  |  | 7538 |  |  | -1599 | -1599 | -1583 | Critical Branch | Validation phase | 16 | NA | 0 |  |  | 422 |  | 7223 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 1130 | 7554 |  |  | 7538 |  |  | -1599 | -1599 | -1583 | Critical Branch | Validation phase | 16 | NA | 0 |  |  | 422 |  | 7223 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250709 | July | 1230 | 7880 |  |  | 7866 |  |  | -4338 | -4338 | -4319 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250709 | July | 1330 | 7880 |  |  | 7866 |  |  | -4338 | -4338 | -4319 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250709 | July | 1430 | 7880 |  |  | 7866 |  |  | -4338 | -4338 | -4319 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250709 | July | 1530 | 6956 |  |  | 6956 |  |  | -1720 | -1720 | -1720 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 392
20250709 | July | 1630 | 6956 |  |  | 6956 |  |  | -1720 | -1720 | -1720 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 392
20250709 | July | 1730 | 6956 |  |  | 6956 |  |  | -1720 | -1720 | -1720 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 392
20250709 | July | 1830 | 7215 |  |  | 7215 |  |  | -4588 | -4588 | -4588 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 398
20250709 | July | 1930 | 7215 |  |  | 7215 |  |  | -4588 | -4588 | -4588 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 398
20250709 | July | 2030 | 7215 |  |  | 7215 |  |  | -4588 | -4588 | -4588 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 398
20250709 | July | 2130 | 7054 |  |  | 7054 |  |  | -4188 | -4188 | -4188 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 390
20250709 | July | 2230 | 7054 |  |  | 7054 |  |  | -4188 | -4188 | -4188 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 390
20250709 | July | 2330 | 6454 |  |  | 6453 |  |  | -3585 | -3585 | -3585 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 377
20250710 | July | 0030 | 8169 |  |  | 7913 |  |  | -4228 | -4228 | -3973 | Critical Branch | Validation phase | 256 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7741 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 2544 | Planned outage Venaus Villarodin 400kV
20250710 | July | 0130 | 8169 |  |  | 7913 |  |  | -4228 | -4228 | -3973 | Critical Branch | Validation phase | 256 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7741 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 2544 | Planned outage Venaus Villarodin 400kV
20250710 | July | 0230 | 8169 |  |  | 7913 |  |  | -4228 | -4228 | -3973 | Critical Branch | Validation phase | 256 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7741 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 2544 | Planned outage Venaus Villarodin 400kV
20250710 | July | 0330 | 7766 |  |  | 7733 |  |  | -3723 | -3723 | -3684 | Critical Branch | Critical Branch | 33 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250710 | July | 0430 | 7766 |  |  | 7733 |  |  | -3723 | -3723 | -3684 | Critical Branch | Critical Branch | 33 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250710 | July | 0530 | 7766 |  |  | 7733 |  |  | -3723 | -3723 | -3684 | Critical Branch | Critical Branch | 33 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250710 | July | 0630 | 7566 |  |  | 7532 |  |  | -3517 | -3517 | -3477 | Critical Branch | Critical Branch | 34 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250710 | July | 0730 | 6976 |  |  | 6976 |  |  | -1915 | -1915 | -1915 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 393
20250710 | July | 0830 | 6976 |  |  | 6976 |  |  | -1915 | -1915 | -1915 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 393
20250710 | July | 0930 | 7243 |  |  | 7242 |  |  | -3426 | -3426 | -3425 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 406
20250710 | July | 1030 | 7243 |  |  | 7242 |  |  | -3426 | -3426 | -3425 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 406
20250710 | July | 1130 | 7243 |  |  | 7242 |  |  | -3426 | -3426 | -3425 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 406
20250710 | July | 1230 | 7834 |  |  | 7822 |  |  | -3300 | -3300 | -3293 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250710 | July | 1330 | 7834 |  |  | 7822 |  |  | -3300 | -3300 | -3293 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250710 | July | 1430 | 7834 |  |  | 7822 |  |  | -3300 | -3300 | -3293 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250710 | July | 1530 | 8128 |  |  | 7910 |  |  | 1562 | 168 | 1586 | Minimum Margin | TTC Validation phase - bilateral reduction | 218 | NA | 3004 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250710 | July | 1630 | 7962 |  |  | 7813 |  |  | 1562 | 2 | 1691 | Minimum Margin | TTC Validation phase - bilateral reduction | 149 | NA | 3380 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250710 | July | 1730 | 7960 |  |  | 7811 |  |  | 1562 | 0 | 1693 | Critical Branch | TTC Validation phase - bilateral reduction | 149 | NA | 3386 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250710 | July | 1830 | 7399 |  |  | 7399 |  |  | -4791 | -4791 | -4791 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 407
20250710 | July | 1930 | 7399 |  |  | 7399 |  |  | -4791 | -4791 | -4791 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 407
20250710 | July | 2030 | 7399 |  |  | 7399 |  |  | -4791 | -4791 | -4791 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 407
20250710 | July | 2130 | 7777 |  |  | 7776 |  |  | -5208 | -5208 | -5207 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250710 | July | 2230 | 7777 |  |  | 7776 |  |  | -5208 | -5208 | -5207 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250710 | July | 2330 | 7177 |  |  | 7176 |  |  | -4606 | -4606 | -4605 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250711 | July | 0030 | 7724 |  |  | 7688 |  |  | -4672 | -4672 | -4649 | Critical Branch | Critical Branch | 36 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250711 | July | 0130 | 7724 |  |  | 7688 |  |  | -4672 | -4672 | -4649 | Critical Branch | Critical Branch | 36 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250711 | July | 0230 | 7724 |  |  | 7688 |  |  | -4672 | -4672 | -4649 | Critical Branch | Critical Branch | 36 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250711 | July | 0330 | 8023 |  |  | 7944 |  |  | -4460 | -4460 | -4402 | Critical Branch | Validation phase | 79 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7747 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0430 | 8023 |  |  | 7944 |  |  | -4460 | -4460 | -4402 | Critical Branch | Validation phase | 79 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7747 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0530 | 8023 |  |  | 7944 |  |  | -4460 | -4460 | -4402 | Critical Branch | Validation phase | 79 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7747 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0630 | 7823 |  |  | 7743 |  |  | -4249 | -4249 | -4190 | Critical Branch | Validation phase | 80 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7547 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250711 | July | 0730 | 6817 |  |  | 6817 |  |  | -4534 | -4534 | -4534 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 378
20250711 | July | 0830 | 6817 |  |  | 6817 |  |  | -4534 | -4534 | -4534 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 378
20250711 | July | 0930 | 7880 |  |  | 7108 |  |  | -3326 | -3326 | -2554 | Critical Branch | Validation phase | 772 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6858 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2544 | Planned outage Venaus Villarodin 400kV
20250711 | July | 1030 | 7880 |  |  | 7108 |  |  | -3326 | -3326 | -2554 | Critical Branch | Validation phase | 772 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6858 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2544 | Planned outage Venaus Villarodin 400kV
20250711 | July | 1130 | 7880 |  |  | 7108 |  |  | -3326 | -3326 | -2554 | Critical Branch | Validation phase | 772 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6858 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2544 | Planned outage Venaus Villarodin 400kV
20250711 | July | 1230 | 7827 |  |  | 7813 |  |  | -4228 | -4228 | -4219 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250711 | July | 1330 | 7827 |  |  | 7813 |  |  | -4228 | -4228 | -4219 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250711 | July | 1430 | 7827 |  |  | 7813 |  |  | -4228 | -4228 | -4219 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250711 | July | 1530 | 7518 |  |  | 7518 |  |  | -3592 | -3592 | -3592 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20250711 | July | 1630 | 7518 |  |  | 7518 |  |  | -3592 | -3592 | -3592 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20250711 | July | 1730 | 7518 |  |  | 7518 |  |  | -3592 | -3592 | -3592 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20250711 | July | 1830 |  | 6047 | 562 |  | 6046 | 562 | -4196 | -4196 | 0 | Critical Branch | Critical Branch | NA | 1 | 4196 |  |  | 353
20250711 | July | 1930 |  | 6047 | 562 |  | 6046 | 562 | -4196 | -4196 | 0 | Critical Branch | Critical Branch | NA | 1 | 4196 |  |  | 353
20250711 | July | 2030 |  | 6047 | 562 |  | 6046 | 562 | -4196 | -4196 | 0 | Critical Branch | Critical Branch | NA | 1 | 4196 |  |  | 353
20250711 | July | 2130 | 7035 |  |  | 7035 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 383
20250711 | July | 2230 | 7035 |  |  | 7035 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 383
20250711 | July | 2330 | 6435 |  |  | 6435 |  |  | -3889 | -3889 | -3889 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 370
20250712 | July | 0030 | 7639 |  |  | 7488 |  |  | -3394 | -3394 | -3250 | Critical Branch | Validation phase | 151 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7197 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250712 | July | 0130 | 7639 |  |  | 7488 |  |  | -3394 | -3394 | -3250 | Critical Branch | Validation phase | 151 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7197 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250712 | July | 0230 | 7639 |  |  | 7488 |  |  | -3394 | -3394 | -3250 | Critical Branch | Validation phase | 151 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7197 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250712 | July | 0330 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 191 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7361 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0430 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 191 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7361 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0530 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 191 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7361 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0630 | 7834 |  |  | 7643 |  |  | -3425 | -3425 | -3245 | Critical Branch | Validation phase | 191 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7361 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0730 | 7580 |  |  | 7537 |  |  | -3151 | -3151 | -3108 | Critical Branch | Validation phase | 43 | NA | 0 |  |  | 416 |  | 7222 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0830 | 7580 |  |  | 7537 |  |  | -3151 | -3151 | -3108 | Critical Branch | Validation phase | 43 | NA | 0 |  |  | 416 |  | 7222 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 0930 | 7444 |  |  | 7302 |  |  | -2601 | -2601 | -2459 | Critical Branch | Validation phase | 142 | NA | 0 |  |  | 409 |  | 6987 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 1030 | 7444 |  |  | 7302 |  |  | -2601 | -2601 | -2459 | Critical Branch | Validation phase | 142 | NA | 0 |  |  | 409 |  | 6987 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 1130 | 7444 |  |  | 7302 |  |  | -2601 | -2601 | -2459 | Critical Branch | Validation phase | 142 | NA | 0 |  |  | 409 |  | 6987 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 1230 | 7775 |  |  | 7774 |  |  | -4106 | -4106 | -4104 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250712 | July | 1330 | 7775 |  |  | 7774 |  |  | -4106 | -4106 | -4104 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250712 | July | 1430 | 7775 |  |  | 7774 |  |  | -4106 | -4106 | -4104 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250712 | July | 1530 |  | 7190 | 672 |  | 7189 | 672 | -4598 | -4598 | 0 | Critical Branch | Critical Branch | NA | 1 | 4598 |  |  | 425
20250712 | July | 1630 |  | 7190 | 672 |  | 7189 | 672 | -4598 | -4598 | 0 | Critical Branch | Critical Branch | NA | 1 | 4598 |  |  | 425
20250712 | July | 1730 |  | 7190 | 672 |  | 7189 | 672 | -4598 | -4598 | 0 | Critical Branch | Critical Branch | NA | 1 | 4598 |  |  | 425
20250712 | July | 1830 |  | 6657 | 637 |  | 6656 | 637 | -3472 | -3472 | 0 | Critical Branch | Critical Branch | NA | 1 | 3472 |  |  | 396
20250712 | July | 1930 |  | 6657 | 637 |  | 6656 | 637 | -3472 | -3472 | 0 | Critical Branch | Critical Branch | NA | 1 | 3472 |  |  | 396
20250712 | July | 2030 |  | 6657 | 637 |  | 6656 | 637 | -3472 | -3472 | 0 | Critical Branch | Critical Branch | NA | 1 | 3472 |  |  | 396
20250712 | July | 2130 | 6889 |  |  | 6834 |  |  | -3205 | -3205 | -3150 | Critical Branch | Validation phase | 55 | NA | 0 |  |  | 381 |  | 6519 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 2230 | 6889 |  |  | 6834 |  |  | -3205 | -3205 | -3150 | Critical Branch | Validation phase | 55 | NA | 0 |  |  | 381 |  | 6519 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250712 | July | 2330 | 6289 |  |  | 6234 |  |  | -2601 | -2601 | -2546 | Critical Branch | Validation phase | 55 | NA | 0 |  |  | 368 |  | 5924 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250713 | July | 0030 | 7590 |  |  | 7566 |  |  | -4280 | -4280 | -4265 | Critical Branch | Critical Branch | 24 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 0130 | 7590 |  |  | 7566 |  |  | -4280 | -4280 | -4265 | Critical Branch | Critical Branch | 24 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 0230 | 7590 |  |  | 7566 |  |  | -4280 | -4280 | -4265 | Critical Branch | Critical Branch | 24 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 0330 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250713 | July | 0430 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250713 | July | 0530 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250713 | July | 0630 | 7027 |  |  | 7027 |  |  | -3709 | -3709 | -3708 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250713 | July | 0730 | 7681 |  |  | 7652 |  |  | -3219 | -3219 | -3201 | Critical Branch | Critical Branch | 29 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 0830 | 7681 |  |  | 7652 |  |  | -3219 | -3219 | -3201 | Critical Branch | Critical Branch | 29 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 0930 | 7324 |  |  | 7315 |  |  | -3939 | -3939 | -3928 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 1030 | 7324 |  |  | 7315 |  |  | -3939 | -3939 | -3928 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 1130 | 7324 |  |  | 7315 |  |  | -3939 | -3939 | -3928 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 1230 | 6359 |  |  | 6359 |  |  | -2851 | -2851 | -2851 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 372
20250713 | July | 1330 | 6359 |  |  | 6359 |  |  | -2851 | -2851 | -2851 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 372
20250713 | July | 1430 | 6359 |  |  | 6359 |  |  | -2851 | -2851 | -2851 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 372
20250713 | July | 1530 |  | 7851 | 883 |  | 7545 | 883 | -5681 | -5681 | 0 | Critical Branch | Critical Branch | NA | 306 | 5681 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 1630 |  | 7851 | 883 |  | 7779 | 883 | -5681 | -5681 | 0 | Critical Branch | Critical Branch | NA | 72 | 5681 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 1730 |  | 7851 | 883 |  | 7729 | 883 | -5681 | -5681 | 0 | Critical Branch | Critical Branch | NA | 122 | 5681 |  |  | 415 | Reduction because NTC over thermal limit on border
20250713 | July | 1830 |  | 6289 | 717 |  | 6288 | 717 | -4390 | -4390 | 0 | Critical Branch | Critical Branch | NA | 1 | 4390 |  |  | 395
20250713 | July | 1930 |  | 6289 | 717 |  | 6288 | 717 | -4390 | -4390 | 0 | Critical Branch | Critical Branch | NA | 1 | 4390 |  |  | 395
20250713 | July | 2030 |  | 6289 | 717 |  | 6288 | 717 | -4390 | -4390 | 0 | Critical Branch | Critical Branch | NA | 1 | 4390 |  |  | 395
20250713 | July | 2130 | 6582 |  |  | 6582 |  |  | -4239 | -4239 | -4238 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 384
20250713 | July | 2230 | 6582 |  |  | 6582 |  |  | -4239 | -4239 | -4238 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 384
20250713 | July | 2330 | 6582 |  |  | 6582 |  |  | -4239 | -4239 | -4238 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 384
20250714 | July | 0030 | 6595 |  |  | 6595 |  |  | -3725 | -3725 | -3725 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 385
20250714 | July | 0130 | 6595 |  |  | 6595 |  |  | -3725 | -3725 | -3725 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 385
20250714 | July | 0230 | 6595 |  |  | 6595 |  |  | -3725 | -3725 | -3725 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 385
20250714 | July | 0330 | 7133 |  |  | 7133 |  |  | -4012 | -4012 | -4011 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 414
20250714 | July | 0430 | 7133 |  |  | 7133 |  |  | -4012 | -4012 | -4011 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 414
20250714 | July | 0530 | 7133 |  |  | 7133 |  |  | -4012 | -4012 | -4011 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 414
20250714 | July | 0630 | 6933 |  |  | 6933 |  |  | -3806 | -3806 | -3806 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 414
20250714 | July | 0730 | 7413 |  |  | 7395 |  |  | -2716 | -2716 | -2698 | Critical Branch | Validation phase | 18 | NA | 0 |  |  | 415 |  | 7080 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250714 | July | 0830 | 7413 |  |  | 7395 |  |  | -2716 | -2716 | -2698 | Critical Branch | Validation phase | 18 | NA | 0 |  |  | 415 |  | 7080 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250714 | July | 0930 | 7793 |  |  | 7593 |  |  | -3378 | -3378 | -3178 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7278 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250714 | July | 1030 | 7793 |  |  | 7593 |  |  | -3378 | -3378 | -3178 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7278 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250714 | July | 1130 | 7793 |  |  | 7593 |  |  | -3378 | -3378 | -3178 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7278 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250714 | July | 1230 | 7862 |  |  | 7849 |  |  | -1523 | -1523 | -1511 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250714 | July | 1330 | 7862 |  |  | 7849 |  |  | -1523 | -1523 | -1511 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250714 | July | 1430 | 7862 |  |  | 7849 |  |  | -1523 | -1523 | -1511 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250714 | July | 1530 | 7528 |  |  | 7528 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20250714 | July | 1630 | 7528 |  |  | 7528 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20250714 | July | 1730 | 7528 |  |  | 7528 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20250714 | July | 1830 |  | 6278 | 579 |  | 6278 | 579 | -2699 | -2699 | 0 | Critical Branch | Critical Branch | NA | 0 | 2699 |  |  | 376
20250714 | July | 1930 |  | 6278 | 579 |  | 6278 | 579 | -2699 | -2699 | 0 | Critical Branch | Critical Branch | NA | 0 | 2699 |  |  | 376
20250714 | July | 2030 |  | 6278 | 579 |  | 6278 | 579 | -2699 | -2699 | 0 | Critical Branch | Critical Branch | NA | 0 | 2699 |  |  | 376
20250714 | July | 2130 |  | 6568 | 620 |  | 6567 | 620 | -4766 | -4766 | 0 | Critical Branch | Critical Branch | NA | 1 | 4766 |  |  | 391
20250714 | July | 2230 |  | 6568 | 620 |  | 6567 | 620 | -4766 | -4766 | 0 | Critical Branch | Critical Branch | NA | 1 | 4766 |  |  | 391
20250714 | July | 2330 |  | 5988 | 645 |  | 5987 | 645 | -4138 | -4138 | 0 | Critical Branch | Critical Branch | NA | 1 | 4138 |  |  | 378
20250715 | July | 0030 | 6542 |  |  | 6542 |  |  | -3554 | -3554 | -3554 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20250715 | July | 0130 | 6542 |  |  | 6542 |  |  | -3554 | -3554 | -3554 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20250715 | July | 0230 | 6542 |  |  | 6542 |  |  | -3554 | -3554 | -3554 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20250715 | July | 0330 | 7121 |  |  | 7121 |  |  | -3730 | -3730 | -3729 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250715 | July | 0430 | 7121 |  |  | 7121 |  |  | -3730 | -3730 | -3729 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250715 | July | 0530 | 7121 |  |  | 7121 |  |  | -3730 | -3730 | -3729 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250715 | July | 0630 | 6921 |  |  | 6921 |  |  | -3522 | -3522 | -3522 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 413
20250715 | July | 0730 | 6511 |  |  | 6510 |  |  | -3723 | -3723 | -3722 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 359
20250715 | July | 0830 | 6511 |  |  | 6510 |  |  | -3723 | -3723 | -3722 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 359
20250715 | July | 0930 | 7982 |  |  | 7937 |  |  | -4265 | -4265 | -4228 | Critical Branch | Validation phase | 45 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7708 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250715 | July | 1030 | 6782 |  |  | 6732 |  |  | -3003 | -3003 | -2964 | Critical Branch | Validation phase | 50 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6508 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250715 | July | 1130 | 6782 |  |  | 6732 |  |  | -3003 | -3003 | -2964 | Critical Branch | Validation phase | 50 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6508 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250715 | July | 1230 | 7501 |  |  | 7501 |  |  | -1022 | -1022 | -1022 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 419
20250715 | July | 1330 | 7501 |  |  | 7501 |  |  | -1022 | -1022 | -1022 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 419
20250715 | July | 1430 | 7501 |  |  | 7501 |  |  | -1022 | -1022 | -1022 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 419
20250715 | July | 1530 | 7326 |  |  | 7325 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 408
20250715 | July | 1630 | 7326 |  |  | 7325 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 408
20250715 | July | 1730 | 7326 |  |  | 7079 |  |  | -1169 | -1169 | -923 | Critical Branch | Critical Branch | 247 | NA | 0 |  |  | 393
20250715 | July | 1830 | 5580 |  |  | 5579 |  |  | -2920 | -2920 | -2920 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 297
20250715 | July | 1930 | 5580 |  |  | 5579 |  |  | -2920 | -2920 | -2920 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 297
20250715 | July | 2030 | 5580 |  |  | 5579 |  |  | -2920 | -2920 | -2920 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 297
20250715 | July | 2130 | 6752 |  |  | 6752 |  |  | -4347 | -4347 | -4347 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 366
20250715 | July | 2230 | 6752 |  |  | 6752 |  |  | -4347 | -4347 | -4347 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 366
20250715 | July | 2330 | 6152 |  |  | 6151 |  |  | -3743 | -3743 | -3743 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 352
20250716 | July | 0030 | 6884 |  |  | 6508 |  |  | -3795 | -3795 | -3419 | Critical Branch | Validation phase | 376 | NA | 0 |  |  | 398 |  | 6258 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0130 | 6884 |  |  | 6508 |  |  | -3795 | -3795 | -3419 | Critical Branch | Validation phase | 376 | NA | 0 |  |  | 398 |  | 6258 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0230 | 6884 |  |  | 6508 |  |  | -3795 | -3795 | -3419 | Critical Branch | Validation phase | 376 | NA | 0 |  |  | 398 |  | 6258 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0330 | 7208 |  |  | 6657 |  |  | -2501 | -2501 | -1950 | Critical Branch | Validation phase | 551 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6407 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0430 | 7208 |  |  | 6657 |  |  | -2501 | -2501 | -1950 | Critical Branch | Validation phase | 551 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6407 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0530 | 7208 |  |  | 6657 |  |  | -2501 | -2501 | -1950 | Critical Branch | Validation phase | 551 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6407 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0630 | 7008 |  |  | 6457 |  |  | -2289 | -2289 | -1738 | Critical Branch | Validation phase | 551 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6207 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 0730 | 6512 |  |  | 6169 |  |  | -3992 | -3992 | -3649 | Critical Branch | Validation phase | 343 | NA | 0 |  |  | 359 |  | 5919 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0830 | 6512 |  |  | 6169 |  |  | -3992 | -3992 | -3649 | Critical Branch | Validation phase | 343 | NA | 0 |  |  | 359 |  | 5919 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250716 | July | 0930 | 7921 |  |  | 7669 |  |  | -4356 | -4356 | -4111 | Critical Branch | Critical Branch | 252 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250716 | July | 1030 | 7921 |  |  | 7902 |  |  | -4356 | -4356 | -4344 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250716 | July | 1130 | 7921 |  |  | 7902 |  |  | -4356 | -4356 | -4344 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250716 | July | 1230 | 7666 |  |  | 7034 |  |  | -4005 | -4005 | -3373 | Critical Branch | Validation phase | 632 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6784 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250716 | July | 1330 | 7666 |  |  | 7034 |  |  | -4005 | -4005 | -3373 | Critical Branch | Validation phase | 632 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6784 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250716 | July | 1430 | 7666 |  |  | 7034 |  |  | -4005 | -4005 | -3373 | Critical Branch | Validation phase | 632 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6784 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250716 | July | 1530 | 7998 |  |  | 6818 |  |  | -1870 | -1870 | -690 | Critical Branch | Validation phase | 1180 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6568 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 1630 | 7998 |  |  | 6818 |  |  | -1870 | -1870 | -690 | Critical Branch | Validation phase | 1180 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6568 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 1730 | 7998 |  |  | 6818 |  |  | -1870 | -1870 | -690 | Critical Branch | Validation phase | 1180 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6568 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 1830 |  | 6153 | 568 |  | 6153 | 568 | -4313 | -4313 | 0 | Critical Branch | Critical Branch | NA | 0 | 4313 |  |  | 360
20250716 | July | 1930 |  | 6153 | 568 |  | 6153 | 568 | -4313 | -4313 | 0 | Critical Branch | Critical Branch | NA | 0 | 4313 |  |  | 360
20250716 | July | 2030 |  | 6153 | 568 |  | 6153 | 568 | -4313 | -4313 | 0 | Critical Branch | Critical Branch | NA | 0 | 4313 |  |  | 360
20250716 | July | 2130 | 7288 |  |  | 6754 |  |  | -4704 | -4704 | -4170 | Critical Branch | Validation phase | 534 | NA | 0 |  |  | 397 |  | 6504 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 2230 | 7288 |  |  | 6754 |  |  | -4704 | -4704 | -4170 | Critical Branch | Validation phase | 534 | NA | 0 |  |  | 397 |  | 6504 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250716 | July | 2330 | 6688 |  |  | 6154 |  |  | -4100 | -4100 | -3566 | Critical Branch | Validation phase | 534 | NA | 0 |  |  | 386 |  | 5904 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250717 | July | 0030 | 7331 |  |  | 7108 |  |  | -4073 | -4073 | -3850 | Critical Branch | Validation phase | 223 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6858 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0130 | 7331 |  |  | 7108 |  |  | -4073 | -4073 | -3850 | Critical Branch | Validation phase | 223 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6858 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0230 | 7331 |  |  | 7108 |  |  | -4073 | -4073 | -3850 | Critical Branch | Validation phase | 223 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6858 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0330 | 7474 |  |  | 7263 |  |  | -4139 | -4139 | -3930 | Critical Branch | Validation phase | 211 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7020 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0430 | 7474 |  |  | 7263 |  |  | -4139 | -4139 | -3930 | Critical Branch | Validation phase | 211 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7020 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0530 | 7474 |  |  | 7263 |  |  | -4139 | -4139 | -3930 | Critical Branch | Validation phase | 211 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7020 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0630 | 7274 |  |  | 7062 |  |  | -3934 | -3934 | -3725 | Critical Branch | Validation phase | 212 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6820 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0730 | 7037 |  |  | 6864 |  |  | -4289 | -4289 | -4116 | Critical Branch | Validation phase | 173 | NA | 0 |  |  | 391 |  | 6614 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0830 | 7037 |  |  | 6864 |  |  | -4289 | -4289 | -4116 | Critical Branch | Validation phase | 173 | NA | 0 |  |  | 391 |  | 6614 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 0930 | 7013 |  |  | 6818 |  |  | -3046 | -3046 | -2851 | Critical Branch | Validation phase | 195 | NA | 0 |  |  | 389 |  | 6568 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1030 | 7013 |  |  | 6818 |  |  | -3046 | -3046 | -2851 | Critical Branch | Validation phase | 195 | NA | 0 |  |  | 389 |  | 6568 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1130 | 7013 |  |  | 6818 |  |  | -3046 | -3046 | -2851 | Critical Branch | Validation phase | 195 | NA | 0 |  |  | 389 |  | 6568 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1230 | 7368 |  |  | 7084 |  |  | -3974 | -3974 | -3690 | Critical Branch | Validation phase | 284 | NA | 0 |  |  | 209 |  | 6834 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1330 | 7368 |  |  | 7084 |  |  | -3974 | -3974 | -3690 | Critical Branch | Validation phase | 284 | NA | 0 |  |  | 209 |  | 6834 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1430 | 7368 |  |  | 7084 |  |  | -3974 | -3974 | -3690 | Critical Branch | Validation phase | 284 | NA | 0 |  |  | 209 |  | 6834 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1530 | 7282 |  |  | 7059 |  |  | -3557 | -3557 | -3334 | Critical Branch | Validation phase | 223 | NA | 0 |  |  | 206 |  | 6809 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1630 | 7497 |  |  | 7079 |  |  | -3733 | -3733 | -3389 | Critical Branch | Validation phase | 418 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7024 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1730 | 7497 |  |  | 7274 |  |  | -3733 | -3733 | -3510 | Critical Branch | Validation phase | 223 | NA | 0 |  |  | 418 |  | 7024 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 1830 |  | 6845 | 666 |  | 6844 | 666 | -5120 | -5120 | 0 | Critical Branch | Critical Branch | NA | 1 | 5120 |  |  | 403
20250717 | July | 1930 |  | 6845 | 666 |  | 6844 | 666 | -5120 | -5120 | 0 | Critical Branch | Critical Branch | NA | 1 | 5120 |  |  | 403
20250717 | July | 2030 |  | 6845 | 666 |  | 6844 | 666 | -5120 | -5120 | 0 | Critical Branch | Critical Branch | NA | 1 | 5120 |  |  | 403
20250717 | July | 2130 | 7162 |  |  | 6878 |  |  | -4832 | -4832 | -4548 | Critical Branch | Validation phase | 284 | NA | 0 |  |  | 390 |  | 6628 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 2230 | 7162 |  |  | 6878 |  |  | -4832 | -4832 | -4548 | Critical Branch | Validation phase | 284 | NA | 0 |  |  | 390 |  | 6628 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250717 | July | 2330 | 6562 |  |  | 6278 |  |  | -4228 | -4228 | -3944 | Critical Branch | Validation phase | 284 | NA | 0 |  |  | 378 |  | 6028 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250718 | July | 0030 | 7182 |  |  | 6847 |  |  | -4008 | -4008 | -3676 | Critical Branch | Validation phase | 335 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6923 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0130 | 7182 |  |  | 6847 |  |  | -4008 | -4008 | -3676 | Critical Branch | Validation phase | 335 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6923 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0230 | 7182 |  |  | 6847 |  |  | -4008 | -4008 | -3676 | Critical Branch | Validation phase | 335 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6923 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0330 | 7248 |  |  | 6891 |  |  | -4147 | -4147 | -3767 | Critical Branch | TTC Validation phase - bilateral reduction | 357 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0430 | 7248 |  |  | 6891 |  |  | -4147 | -4147 | -3767 | Critical Branch | TTC Validation phase - bilateral reduction | 357 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0530 | 7248 |  |  | 6891 |  |  | -4147 | -4147 | -3767 | Critical Branch | TTC Validation phase - bilateral reduction | 357 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0630 | 7048 |  |  | 6689 |  |  | -3942 | -3942 | -3560 | Critical Branch | TTC Validation phase - bilateral reduction | 359 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0730 | 6742 |  |  | 6505 |  |  | -4349 | -4349 | -4110 | Critical Branch | Validation phase | 237 | NA | 0 |  |  | 373 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0830 | 6742 |  |  | 6505 |  |  | -4349 | -4349 | -4110 | Critical Branch | Validation phase | 237 | NA | 0 |  |  | 373 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 0930 | 7600 |  |  | 7056 |  |  | -2837 | -2837 | -2294 | Critical Branch | Validation phase | 544 | NA | 0 |  |  | 425 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1030 | 7600 |  |  | 7056 |  |  | -2837 | -2837 | -2294 | Critical Branch | Validation phase | 544 | NA | 0 |  |  | 425 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1130 | 7600 |  |  | 7056 |  |  | -2837 | -2837 | -2294 | Critical Branch | Validation phase | 544 | NA | 0 |  |  | 425 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1230 | 8091 |  |  | 7342 |  |  | -1211 | -1211 | -566 | Critical Branch | TTC Validation phase - bilateral reduction | 749 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1330 | 8091 |  |  | 7342 |  |  | -1211 | -1211 | -566 | Critical Branch | TTC Validation phase - bilateral reduction | 749 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1430 | 8091 |  |  | 7342 |  |  | -1211 | -1211 | -566 | Critical Branch | TTC Validation phase - bilateral reduction | 749 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1530 | 7344 |  |  | 6891 |  |  | -2847 | -2847 | -2376 | Critical Branch | Validation phase | 453 | NA | 0 |  |  | 409 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1630 | 7344 |  |  | 6891 |  |  | -2847 | -2847 | -2376 | Critical Branch | Validation phase | 453 | NA | 0 |  |  | 409 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1730 | 7344 |  |  | 6891 |  |  | -2847 | -2847 | -2376 | Critical Branch | Validation phase | 453 | NA | 0 |  |  | 409 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1830 |  | 6787 | 671 |  | 6391 | 671 | -5225 | -5225 | 0 | Critical Branch | Validation phase | NA | 396 | 5225 |  |  | 400 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 1930 |  | 6787 | 671 |  | 6391 | 671 | -5225 | -5225 | 0 | Critical Branch | Validation phase | NA | 396 | 5225 |  |  | 400 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2030 |  | 6787 | 671 |  | 6391 | 671 | -5225 | -5225 | 0 | Critical Branch | Validation phase | NA | 396 | 5225 |  |  | 400 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2130 | 6986 |  |  | 6710 |  |  | -4598 | -4598 | -4307 | Critical Branch | Validation phase | 276 | NA | 0 |  |  | 380 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2230 | 6986 |  |  | 6710 |  |  | -4598 | -4598 | -4307 | Critical Branch | Validation phase | 276 | NA | 0 |  |  | 380 |  |  |  | 2000 | Unplanned outage MERY VIELMOULIN 1
20250718 | July | 2330 | 6386 |  |  | 6386 |  |  | -3994 | -3994 | -3994 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 367
20250719 | July | 0030 | 6799 |  |  | 6789 |  |  | -3785 | -3785 | -3775 | Critical Branch | Validation phase | 10 | NA | 0 |  |  | 393 |  | 6539 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 0130 | 6799 |  |  | 6789 |  |  | -3785 | -3785 | -3775 | Critical Branch | Validation phase | 10 | NA | 0 |  |  | 393 |  | 6539 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 0230 | 6799 |  |  | 6789 |  |  | -3785 | -3785 | -3775 | Critical Branch | Validation phase | 10 | NA | 0 |  |  | 393 |  | 6539 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 0330 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 378
20250719 | July | 0430 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 378
20250719 | July | 0530 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 378
20250719 | July | 0630 | 6560 |  |  | 6560 |  |  | -2161 | -2161 | -2161 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 378
20250719 | July | 0730 | 7138 |  |  | 7138 |  |  | -2739 | -2739 | -2739 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 389
20250719 | July | 0830 | 7138 |  |  | 7138 |  |  | -2739 | -2739 | -2739 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 389
20250719 | July | 0930 | 7614 |  |  | 7614 |  |  | -4375 | -4375 | -4375 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 417
20250719 | July | 1030 | 7614 |  |  | 7614 |  |  | -4375 | -4375 | -4375 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 417
20250719 | July | 1130 | 7614 |  |  | 7614 |  |  | -4375 | -4375 | -4375 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 417
20250719 | July | 1230 | 8165 |  |  | 7837 |  |  | -1629 | -1629 | -1301 | Critical Branch | Validation phase | 328 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7592 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250719 | July | 1330 | 8165 |  |  | 7837 |  |  | -1629 | -1629 | -1301 | Critical Branch | Validation phase | 328 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7592 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250719 | July | 1430 | 8165 |  |  | 7837 |  |  | -1629 | -1629 | -1301 | Critical Branch | Validation phase | 328 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7592 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250719 | July | 1530 | 7287 |  |  | 7212 |  |  | -4057 | -4057 | -3982 | Critical Branch | Validation phase | 75 | NA | 0 |  |  | 397 |  | 6962 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 1630 | 7287 |  |  | 7212 |  |  | -4057 | -4057 | -3982 | Critical Branch | Validation phase | 75 | NA | 0 |  |  | 397 |  | 6962 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 1730 | 7287 |  |  | 7212 |  |  | -4057 | -4057 | -3982 | Critical Branch | Validation phase | 75 | NA | 0 |  |  | 397 |  | 6962 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250719 | July | 1830 | 5814 |  |  | 5813 |  |  | -3755 | -3755 | -3755 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 311
20250719 | July | 1930 | 5814 |  |  | 5813 |  |  | -3755 | -3755 | -3755 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 311
20250719 | July | 2030 | 5814 |  |  | 5813 |  |  | -3755 | -3755 | -3755 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 311
20250719 | July | 2130 | 5788 |  |  | 5787 |  |  | -3078 | -3078 | -3077 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 309
20250719 | July | 2230 | 5788 |  |  | 5787 |  |  | -3078 | -3078 | -3077 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 309
20250719 | July | 2330 | 5188 |  |  | 5187 |  |  | -2473 | -2473 | -2473 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 292
20250720 | July | 0030 | 5889 |  |  | 5815 |  |  | -1196 | -1196 | -1122 | Critical Branch | Validation phase | 74 | NA | 0 |  |  | 336 |  | 5565 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0130 | 5889 |  |  | 5815 |  |  | -1196 | -1196 | -1122 | Critical Branch | Validation phase | 74 | NA | 0 |  |  | 336 |  | 5565 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0230 | 5889 |  |  | 5815 |  |  | -1196 | -1196 | -1122 | Critical Branch | Validation phase | 74 | NA | 0 |  |  | 336 |  | 5565 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0330 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 64 | NA | 0 |  |  | 397 |  | 6562 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0430 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 64 | NA | 0 |  |  | 397 |  | 6562 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0530 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 64 | NA | 0 |  |  | 397 |  | 6562 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0630 | 6876 |  |  | 6812 |  |  | -2053 | -2053 | -1989 | Critical Branch | Validation phase | 64 | NA | 0 |  |  | 397 |  | 6562 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250720 | July | 0730 | 7299 |  |  | 7290 |  |  | -3598 | -3598 | -3592 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 0830 | 7299 |  |  | 7290 |  |  | -3598 | -3598 | -3592 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 0930 | 7747 |  |  | 7710 |  |  | -4810 | -4810 | -4785 | Critical Branch | Critical Branch | 37 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 1030 | 7747 |  |  | 7710 |  |  | -4810 | -4810 | -4785 | Critical Branch | Critical Branch | 37 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 1130 | 7747 |  |  | 7710 |  |  | -4810 | -4810 | -4785 | Critical Branch | Critical Branch | 37 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 1230 | 7358 |  |  | 7345 |  |  | -3914 | -3914 | -3898 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 1330 | 7358 |  |  | 7345 |  |  | -3914 | -3914 | -3898 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 1430 | 7358 |  |  | 7345 |  |  | -3914 | -3914 | -3898 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250720 | July | 1530 | 7088 |  |  | 7088 |  |  | -3586 | -3586 | -3585 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 411
20250720 | July | 1630 | 7088 |  |  | 7088 |  |  | -3586 | -3586 | -3585 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 411
20250720 | July | 1730 | 7088 |  |  | 7088 |  |  | -3586 | -3586 | -3585 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 411
20250720 | July | 1830 |  | 5656 | 592 |  | 5656 | 592 | -4133 | -4133 | 0 | Critical Branch | Critical Branch | NA | 0 | 4133 |  |  | 350
20250720 | July | 1930 |  | 5656 | 592 |  | 5656 | 592 | -4133 | -4133 | 0 | Critical Branch | Critical Branch | NA | 0 | 4133 |  |  | 350
20250720 | July | 2030 |  | 5656 | 592 |  | 5656 | 592 | -4133 | -4133 | 0 | Critical Branch | Critical Branch | NA | 0 | 4133 |  |  | 350
20250720 | July | 2130 | 5812 |  |  | 5811 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 331
20250720 | July | 2230 | 5812 |  |  | 5811 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 331
20250720 | July | 2330 | 5812 |  |  | 5811 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 331
20250721 | July | 0030 | 7122 |  |  | 7099 |  |  | -3783 | -3783 | -3760 | Critical Branch | Validation phase | 23 | NA | 0 |  |  |  |  | 6849 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0130 | 7122 |  |  | 7099 |  |  | -3796 | -3796 | -3773 | Critical Branch | Validation phase | 23 | NA | 0 |  |  |  |  | 6849 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0230 | 7122 |  |  | 7099 |  |  | -3796 | -3796 | -3773 | Critical Branch | Validation phase | 23 | NA | 0 |  |  |  |  | 6849 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0330 | 6895 |  |  | 6865 |  |  | -3244 | -3244 | -3214 | Critical Branch | Validation phase | 30 | NA | 0 |  |  |  |  | 6615 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0430 | 6895 |  |  | 6865 |  |  | -3244 | -3244 | -3214 | Critical Branch | Validation phase | 30 | NA | 0 |  |  |  |  | 6615 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0530 | 6895 |  |  | 6865 |  |  | -3244 | -3244 | -3214 | Critical Branch | Validation phase | 30 | NA | 0 |  |  |  |  | 6615 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250721 | July | 0630 | 6695 |  |  | 6665 |  |  | -3032 | -3032 | -3002 | Critical Branch | Validation phase | 30 | NA | 0 |  |  |  |  | 6420 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250722 | July | 0030 | 7207 |  |  | 7150 |  |  | -3597 | -3597 | 0 | Critical Branch | Critical Branch | 57 | NA | 3597 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0130 | 7207 |  |  | 7150 |  |  | -3597 | -3597 | 0 | Critical Branch | Critical Branch | 57 | NA | 3597 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0230 | 7207 |  |  | 7150 |  |  | -3597 | -3597 | 0 | Critical Branch | Critical Branch | 57 | NA | 3597 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0330 | 7282 |  |  | 7150 |  |  | -3943 | -3943 | 0 | Critical Branch | Critical Branch | 132 | NA | 3943 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0430 | 7282 |  |  | 7150 |  |  | -3943 | -3943 | 0 | Critical Branch | Critical Branch | 132 | NA | 3943 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0530 | 7282 |  |  | 7150 |  |  | -3943 | -3943 | 0 | Critical Branch | Critical Branch | 132 | NA | 3943 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0630 | 7082 |  |  | 6950 |  |  | -3742 | -3742 | 0 | Critical Branch | Critical Branch | 132 | NA | 3742 |  |  | 415 | Reduction because NTC over thermal limit on border
20250722 | July | 0730 | 6566 |  |  | 7000 |  |  | -3591 | -3591 | 0 | Critical Branch | Critical Branch | -434 | NA | 3591 |  |  | 363
20250722 | July | 0830 | 6566 |  |  | 5500 |  |  | -3591 | -3591 | 0 | Critical Branch | Critical Branch | 1066 | NA | 3591 |  |  | 363
20250722 | July | 0930 | 7275 |  |  | 4000 |  |  | -2605 | -2605 | 0 | Critical Branch | Validation phase | 3275 | NA | 2605 |  |  | 405
20250722 | July | 1030 | 7275 |  |  | 4000 |  |  | -2605 | -2605 | 0 | Critical Branch | Validation phase | 3275 | NA | 2605 |  |  | 405
20250722 | July | 1130 | 7275 |  |  | 4000 |  |  | -2605 | -2605 | 0 | Critical Branch | Validation phase | 3275 | NA | 2605 |  |  | 405
20250722 | July | 1230 | 8014 |  |  | 4000 |  |  | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 4014 | NA | 997 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250722 | July | 1330 | 8014 |  |  | 5500 |  |  | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 2514 | NA | 997 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250722 | July | 1430 | 8014 |  |  | 7000 |  |  | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1014 | NA | 997 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250722 | July | 1530 | 7946 |  |  | 7600 |  |  | -3787 | -3787 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 346 | NA | 3787 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250722 | July | 1630 | 7946 |  |  | 7600 |  |  | -3787 | -3787 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 346 | NA | 3787 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250722 | July | 1730 | 7946 |  |  | 7600 |  |  | -3787 | -3787 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 346 | NA | 3787 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2544 | Planned outage Venaus Villarodin 400kV
20250722 | July | 1830 |  | 7054 | 654 | 7742 |  |  | -4795 | -4795 | 0 | Critical Branch | Critical Branch | NA | NA | 4795 |  |  | 417
20250722 | July | 1930 |  | 7054 | 654 | 7742 |  |  | -4795 | -4795 | 0 | Critical Branch | Critical Branch | NA | NA | 4795 |  |  | 417
20250722 | July | 2030 |  | 7054 | 654 | 7742 |  |  | -4795 | -4795 | 0 | Critical Branch | Critical Branch | NA | NA | 4795 |  |  | 417
20250722 | July | 2130 | 7088 |  |  | 7711 |  |  | -4192 | -4192 | 0 | Critical Branch | Critical Branch | -623 | NA | 4192 |  |  | 386
20250722 | July | 2230 | 7088 |  |  | 7711 |  |  | -4192 | -4192 | 0 | Critical Branch | Critical Branch | -623 | NA | 4192 |  |  | 386
20250722 | July | 2330 | 6488 |  |  | 7108 |  |  | -3588 | -3588 | 0 | Critical Branch | Critical Branch | -620 | NA | 3588 |  |  | 373
20250723 | July | 0030 | 7197 |  |  | 7076 |  |  | -2764 | -2764 | -2643 | Critical Branch | Validation phase | 121 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6826 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0130 | 7197 |  |  | 7076 |  |  | -2764 | -2764 | -2643 | Critical Branch | Validation phase | 121 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6826 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0230 | 7197 |  |  | 7076 |  |  | -2764 | -2764 | -2643 | Critical Branch | Validation phase | 121 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6826 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0330 | 6521 |  |  | 6429 |  |  | -2871 | -2871 | -2779 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 375 |  | 6179 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0430 | 6521 |  |  | 6429 |  |  | -2871 | -2871 | -2779 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 375 |  | 6179 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0530 | 6521 |  |  | 6429 |  |  | -2871 | -2871 | -2779 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 375 |  | 6179 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0630 | 6321 |  |  | 6229 |  |  | -2663 | -2663 | -2571 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 374 |  | 5979 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 0730 | 6679 |  |  | 6678 |  |  | -3571 | -3571 | -3570 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 369
20250723 | July | 0830 | 6679 |  |  | 6678 |  |  | -3571 | -3571 | -3570 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 369
20250723 | July | 0930 | 7682 |  |  | 7637 |  |  | -4255 | -4255 | -4210 | Critical Branch | Validation phase | 45 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7389 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 1030 | 7682 |  |  | 7637 |  |  | -4255 | -4255 | -4210 | Critical Branch | Validation phase | 45 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7389 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 1130 | 7682 |  |  | 7637 |  |  | -4255 | -4255 | -4210 | Critical Branch | Validation phase | 45 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7389 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250723 | July | 1230 | 7771 |  |  | 7761 |  |  | -1126 | -1126 | -1116 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250723 | July | 1330 | 7771 |  |  | 7761 |  |  | -1126 | -1126 | -1116 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250723 | July | 1430 | 7771 |  |  | 7761 |  |  | -1126 | -1126 | -1116 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250723 | July | 1530 |  | 7037 | 718 |  | 7036 | 718 | -476 | -476 | 0 | Critical Branch | Critical Branch | NA | 1 | 476 |  |  | 425
20250723 | July | 1630 |  | 8341 | 718 |  | 8340 | 718 | -1633 | -1633 | 0 | Critical Branch | Critical Branch | NA | 1 | 1633 |  |  | 425
20250723 | July | 1730 |  | 8341 | 718 |  | 8340 | 718 | -1633 | -1633 | 0 | Critical Branch | Critical Branch | NA | 1 | 1633 |  |  | 425
20250723 | July | 1830 |  | 8330 | 649 |  | 7928 | 618 | -5621 | -5621 | 0 | Critical Branch | Validation phase | NA | 433 | 5621 |  |  | 416 |  | 8216 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 1930 |  | 8330 | 649 |  | 7928 | 519 | -5621 | -5621 | 0 | Critical Branch | Validation phase | NA | 532 | 5621 |  |  | 416 |  | 8216 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 2030 |  | 8330 | 649 |  | 7928 | 519 | -5621 | -5621 | 0 | Critical Branch | Validation phase | NA | 532 | 5621 |  |  | 416 |  | 8216 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 2130 |  | 8455 | 663 |  | 7894 | 519 | -5774 | -5774 | 0 | Critical Branch | Validation phase | NA | 705 | 5774 |  |  | 423 |  | 8190 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 2230 |  | 8455 | 663 |  | 7894 | 620 | -5774 | -5774 | 0 | Critical Branch | Validation phase | NA | 604 | 5774 |  |  | 423 |  | 8190 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250723 | July | 2330 |  | 7875 | 688 |  | 7334 | 646 | -5141 | -5141 | 0 | Critical Branch | Validation phase | NA | 583 | 5141 |  |  | 412 |  | 7590 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20250724 | July | 0030 | 8931 |  |  | 8582 |  |  | -3264 | -3264 | -2918 | Critical Branch | Validation phase | 349 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8339 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0130 | 8931 |  |  | 8582 |  |  | -3264 | -3264 | -2918 | Critical Branch | Validation phase | 349 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8339 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0230 | 8931 |  |  | 8582 |  |  | -3264 | -3264 | -2918 | Critical Branch | Validation phase | 349 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8339 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0330 | 8623 |  |  | 8210 |  |  | -4205 | -4205 | -3792 | Critical Branch | Validation phase | 413 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7960 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0430 | 8623 |  |  | 8210 |  |  | -4205 | -4205 | -3792 | Critical Branch | Validation phase | 413 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7960 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0530 | 8623 |  |  | 8210 |  |  | -4205 | -4205 | -3792 | Critical Branch | Validation phase | 413 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7960 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0630 | 8423 |  |  | 8010 |  |  | -3994 | -3994 | -3581 | Critical Branch | Validation phase | 413 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7760 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250724 | July | 0730 | 8209 |  |  | 8209 |  |  | -4914 | -4914 | -4914 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 390
20250724 | July | 0830 | 8209 |  |  | 8209 |  |  | -4914 | -4914 | -4914 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 390
20250724 | July | 0930 | 8513 |  |  | 8513 |  |  | 2489 | 0 | 2489 | Critical Branch | Critical Branch | 0 | NA | 2489 |  |  | 405
20250724 | July | 1030 | 8513 |  |  | 8513 |  |  | 2489 | 0 | 2489 | Critical Branch | Critical Branch | 0 | NA | 2489 |  |  | 405
20250724 | July | 1130 | 8725 |  |  | 8698 |  |  | 2489 | 212 | 2302 | Minimum Margin | Minimum Margin | 27 | NA | 4392 |  |  | 414
20250724 | July | 1230 | 7199 |  |  | 7198 |  |  | 2962 | 58 | 2904 | Minimum Margin | Minimum Margin | 1 | NA | 5750 |  |  | 338
20250724 | July | 1330 | 7199 |  |  | 7198 |  |  | 2962 | 58 | 2904 | Minimum Margin | Minimum Margin | 1 | NA | 5750 |  |  | 338
20250724 | July | 1430 | 7199 |  |  | 7198 |  |  | 2962 | 58 | 2904 | Minimum Margin | Minimum Margin | 1 | NA | 5750 |  |  | 338
20250724 | July | 1530 | 9073 |  |  | 8439 |  |  | -4739 | -4739 | -4105 | Critical Branch | Validation phase | 634 | NA | 0 |  |  | 414 |  | 8189 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250724 | July | 1630 | 9073 |  |  | 8439 |  |  | -4739 | -4739 | -4105 | Critical Branch | Validation phase | 634 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8189 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250724 | July | 1730 | 9073 |  |  | 8439 |  |  | -4739 | -4739 | -4105 | Critical Branch | Validation phase | 634 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8189 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250724 | July | 1830 | 8267 |  |  | 8267 |  |  | -5259 | -5259 | -5259 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 386
20250724 | July | 1930 | 8267 |  |  | 8267 |  |  | -5259 | -5259 | -5259 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 386
20250724 | July | 2030 | 8267 |  |  | 8267 |  |  | -5259 | -5259 | -5259 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 386
20250724 | July | 2130 | 8499 |  |  | 8498 |  |  | -5401 | -5401 | -5401 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 397
20250724 | July | 2230 | 8499 |  |  | 8498 |  |  | -5401 | -5401 | -5401 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 397
20250724 | July | 2330 | 7899 |  |  | 7899 |  |  | -4796 | -4796 | -4796 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 386
20250725 | July | 0030 | 8891 |  |  | 8868 |  |  | -3639 | -3639 | -3625 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250725 | July | 0130 | 8891 |  |  | 8868 |  |  | -3639 | -3639 | -3625 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250725 | July | 0230 | 8891 |  |  | 8868 |  |  | -3639 | -3639 | -3625 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250725 | July | 0330 | 9126 |  |  | 8957 |  |  | -5690 | -5690 | -5532 | Critical Branch | Validation phase | 169 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8735 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0430 | 9126 |  |  | 8957 |  |  | -5690 | -5690 | -5532 | Critical Branch | Validation phase | 169 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8735 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0530 | 9126 |  |  | 8957 |  |  | -5690 | -5690 | -5532 | Critical Branch | Validation phase | 169 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8735 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0630 | 8926 |  |  | 8756 |  |  | -5483 | -5483 | -5324 | Critical Branch | Validation phase | 170 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8535 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250725 | July | 0730 | 8314 |  |  | 8314 |  |  | -5245 | -5245 | -5244 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 395
20250725 | July | 0830 | 8314 |  |  | 8314 |  |  | -5245 | -5245 | -5244 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 395
20250725 | July | 0930 | 9099 |  |  | 9030 |  |  | -5361 | -5361 | -5291 | Critical Branch | Validation phase | 69 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8787 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250725 | July | 1030 | 9099 |  |  | 9030 |  |  | -5361 | -5361 | -5291 | Critical Branch | Validation phase | 69 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8787 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250725 | July | 1130 | 9099 |  |  | 7750 |  |  | -5361 | -5361 | -4005 | Critical Branch | Validation phase | 1349 | NA | 0 |  |  | 394 |  | 8787 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250725 | July | 1230 | 6790 |  |  | 6250 |  |  | 4626 | 60 | 5106 | Minimum Margin | Validation phase | 540 | NA | 10152 |  |  | 318 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250725 | July | 1330 | 6790 |  |  | 6250 |  |  | 4626 | 60 | 5106 | Minimum Margin | Validation phase | 540 | NA | 10152 |  |  | 318 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250725 | July | 1430 | 6790 |  |  | 6250 |  |  | 4626 | 60 | 5106 | Minimum Margin | Validation phase | 540 | NA | 10152 |  |  | 318 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250725 | July | 1530 | 7975 |  |  | 7750 |  |  | 4168 | 87 | 4306 | Minimum Margin | Minimum Margin | 225 | NA | 8525 |  |  | 378
20250725 | July | 1630 | 7975 |  |  | 7975 |  |  | 4168 | 87 | 4081 | Minimum Margin | Minimum Margin | 0 | NA | 8075 |  |  | 378
20250725 | July | 1730 | 7975 |  |  | 7975 |  |  | 4168 | 87 | 4081 | Minimum Margin | Minimum Margin | 0 | NA | 8075 |  |  | 378
20250725 | July | 1830 |  | 7703 | 595 |  | 7702 | 595 | -5287 | -5287 | 0 | Critical Branch | Critical Branch | NA | 1 | 5287 |  |  | 383
20250725 | July | 1930 |  | 7703 | 595 |  | 7702 | 548 | -5287 | -5287 | 0 | Critical Branch | Validation phase | NA | 48 | 5287 |  |  | 383
20250725 | July | 2030 |  | 7703 | 595 |  | 7702 | 548 | -5287 | -5287 | 0 | Critical Branch | Validation phase | NA | 48 | 5287 |  |  | 383
20250725 | July | 2130 |  | 8141 | 629 |  | 8140 | 548 | -5781 | -5781 | 0 | Critical Branch | Validation phase | NA | 82 | 5781 |  |  | 406
20250725 | July | 2230 |  | 8141 | 629 |  | 8140 | 629 | -5781 | -5781 | 0 | Critical Branch | Critical Branch | NA | 1 | 5781 |  |  | 406
20250725 | July | 2330 |  | 7581 | 654 |  | 7580 | 654 | -5159 | -5159 | 0 | Critical Branch | Critical Branch | NA | 1 | 5159 |  |  | 395
20250726 | July | 0030 | 7794 |  |  | 7723 |  |  | -4240 | -4240 | -4169 | Critical Branch | Validation phase | 71 | NA | 0 |  |  |  |  | 7473 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250726 | July | 0130 | 7794 |  |  | 7723 |  |  | -4240 | -4240 | -4169 | Critical Branch | Validation phase | 71 | NA | 0 |  |  |  |  | 7473 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250726 | July | 0230 | 7794 |  |  | 7723 |  |  | -4240 | -4240 | -4169 | Critical Branch | Validation phase | 71 | NA | 0 |  |  |  |  | 7473 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0030 |  | 8368 | 726 |  | 8259 | 718 | -5140 | -5140 | 0 | Critical Branch | Validation phase | NA | 117 | 5140 |  |  | 415 | Reduction because NTC over thermal limit on border | 8378 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0130 |  | 8368 | 726 |  | 8259 | 718 | -5140 | -5140 | 0 | Critical Branch | Validation phase | NA | 117 | 5140 |  |  | 415 | Reduction because NTC over thermal limit on border | 8378 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0230 |  | 8368 | 726 |  | 8259 | 718 | -5140 | -5140 | 0 | Critical Branch | Validation phase | NA | 117 | 5140 |  |  | 415 | Reduction because NTC over thermal limit on border | 8378 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250727 | July | 0330 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 0430 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 0530 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 0630 | 8874 |  |  | 8852 |  |  | -2978 | -2978 | -2965 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 0730 | 8467 |  |  | 8467 |  |  | -4844 | -4844 | -4844 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 404
20250727 | July | 0830 | 8467 |  |  | 8467 |  |  | -4844 | -4844 | -4844 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 404
20250727 | July | 0930 |  | 7924 | 755 |  | 7923 | 755 | -4428 | -4428 | 0 | Critical Branch | Critical Branch | NA | 1 | 4428 |  |  | 402
20250727 | July | 1030 |  | 7924 | 755 |  | 7923 | 755 | -4428 | -4428 | 0 | Critical Branch | Critical Branch | NA | 1 | 4428 |  |  | 402
20250727 | July | 1130 |  | 7924 | 755 |  | 7923 | 755 | -4428 | -4428 | 0 | Critical Branch | Critical Branch | NA | 1 | 4428 |  |  | 402
20250727 | July | 1230 |  | 8141 | 728 |  | 8141 | 728 | -4413 | -4413 | 0 | Critical Branch | Critical Branch | NA | 0 | 4413 |  |  | 414
20250727 | July | 1330 |  | 8141 | 728 |  | 8141 | 728 | -4413 | -4413 | 0 | Critical Branch | Critical Branch | NA | 0 | 4413 |  |  | 414
20250727 | July | 1430 |  | 8141 | 728 |  | 8141 | 728 | -4413 | -4413 | 0 | Critical Branch | Critical Branch | NA | 0 | 4413 |  |  | 414
20250727 | July | 1530 |  | 8204 | 707 |  | 8201 | 707 | -4857 | -4857 | 0 | Critical Branch | Critical Branch | NA | 3 | 4857 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 1630 |  | 8204 | 707 |  | 8201 | 707 | -4857 | -4857 | 0 | Critical Branch | Critical Branch | NA | 3 | 4857 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 1730 |  | 8204 | 707 |  | 8201 | 707 | -4857 | -4857 | 0 | Critical Branch | Critical Branch | NA | 3 | 4857 |  |  | 415 | Reduction because NTC over thermal limit on border
20250727 | July | 1830 |  | 7697 | 660 |  | 7696 | 660 | -4931 | -4931 | 0 | Critical Branch | Critical Branch | NA | 1 | 4931 |  |  | 390
20250727 | July | 1930 |  | 7697 | 660 |  | 7696 | 660 | -4931 | -4931 | 0 | Critical Branch | Critical Branch | NA | 1 | 4931 |  |  | 390
20250727 | July | 2030 |  | 7697 | 660 |  | 7696 | 660 | -4931 | -4931 | 0 | Critical Branch | Critical Branch | NA | 1 | 4931 |  |  | 390
20250727 | July | 2130 |  | 7763 | 665 |  | 7762 | 665 | -5069 | -5069 | 0 | Critical Branch | Critical Branch | NA | 1 | 5069 |  |  | 393
20250727 | July | 2230 |  | 7763 | 665 |  | 7762 | 665 | -5069 | -5069 | 0 | Critical Branch | Critical Branch | NA | 1 | 5069 |  |  | 393
20250727 | July | 2330 |  | 7535 | 665 |  | 7535 | 665 | -4854 | -4854 | 0 | Critical Branch | Critical Branch | NA | 0 | 4854 |  |  | 393
20250728 | July | 0030 | 9198 |  |  | 9096 |  |  | -3550 | -3550 | -3463 | Critical Branch | Validation phase | 102 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8882 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0130 | 9198 |  |  | 9096 |  |  | -3550 | -3550 | -3463 | Critical Branch | Validation phase | 102 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8882 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0230 | 9198 |  |  | 9096 |  |  | -3550 | -3550 | -3463 | Critical Branch | Validation phase | 102 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8882 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0330 | 9019 |  |  | 8936 |  |  | -4912 | -4912 | -4838 | Critical Branch | Validation phase | 83 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8713 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0430 | 9019 |  |  | 8936 |  |  | -4912 | -4912 | -4838 | Critical Branch | Validation phase | 83 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8713 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0530 | 9019 |  |  | 8936 |  |  | -4912 | -4912 | -4838 | Critical Branch | Validation phase | 83 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8713 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0630 | 8819 |  |  | 8736 |  |  | -4704 | -4704 | -4630 | Critical Branch | Validation phase | 83 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8513 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250728 | July | 0730 | 8376 |  |  | 8366 |  |  | -3428 | -3428 | -3423 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250728 | July | 0830 | 8376 |  |  | 8366 |  |  | -3428 | -3428 | -3423 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250728 | July | 0930 | 7977 |  |  | 7976 |  |  | 4119 | 280 | 3840 | Minimum Margin | Minimum Margin | 1 | NA | 7400 |  |  | 412
20250728 | July | 1030 | 7977 |  |  | 7976 |  |  | 4119 | 280 | 3840 | Minimum Margin | Minimum Margin | 1 | NA | 7400 |  |  | 412
20250728 | July | 1130 | 7977 |  |  | 7530 |  |  | 4119 | 280 | 4274 | Minimum Margin | Minimum Margin | 447 | NA | 8268 |  |  | 388
20250728 | July | 1230 | 6030 |  |  | 6030 |  |  | -465 | -465 | -465 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | NA | 0 |  |  | 305
20250728 | July | 1330 | 6030 |  |  | 6030 |  |  | -465 | -465 | -465 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | NA | 0 |  |  | 305
20250728 | July | 1430 | 6030 |  |  | 6030 |  |  | -465 | -465 | -465 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | NA | 0 |  |  | 305
20250728 | July | 1530 | 8337 |  |  | 7530 |  |  | -417 | -417 | 365 | Critical Branch | Critical Branch | 807 | NA | 1147 |  |  | 388
20250728 | July | 1630 | 8337 |  |  | 8329 |  |  | -417 | -417 | -414 | Critical Branch | Critical Branch | 8 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250728 | July | 1730 | 8337 |  |  | 8329 |  |  | -417 | -417 | -414 | Critical Branch | Critical Branch | 8 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250728 | July | 1830 |  | 8580 | 747 |  | 8247 | 747 | -5439 | -5439 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 333 | 5439 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3200 | Planned outage on Chaffard-Grande Ile 2
20250728 | July | 1930 |  | 8580 | 747 |  | 8247 | 747 | -5439 | -5439 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 333 | 5439 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3200 | Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2030 |  | 8580 | 747 |  | 8247 | 747 | -5439 | -5439 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 333 | 5439 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3200 | Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2130 |  | 8605 | 741 |  | 8260 | 741 | -4142 | -4142 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 345 | 4142 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3200 | Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2230 |  | 8605 | 741 |  | 8260 | 741 | -4142 | -4142 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 345 | 4142 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3200 | Planned outage on Chaffard-Grande Ile 2
20250728 | July | 2330 |  | 8025 | 766 |  | 7912 | 766 | -3510 | -3510 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 113 | 3510 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 3200 | Planned outage on Chaffard-Grande Ile 2
20250729 | July | 0030 | 8945 |  |  | 8877 |  |  | -1616 | -1616 | -1554 | Critical Branch | Critical Branch | 68 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0130 | 8945 |  |  | 8877 |  |  | -1616 | -1616 | -1554 | Critical Branch | Critical Branch | 68 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0230 | 8945 |  |  | 8877 |  |  | -1616 | -1616 | -1554 | Critical Branch | Critical Branch | 68 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0330 | 8902 |  |  | 8836 |  |  | -5105 | -5105 | -5019 | Critical Branch | Critical Branch | 66 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0430 | 8902 |  |  | 8836 |  |  | -5105 | -5105 | -5019 | Critical Branch | Critical Branch | 66 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0530 | 8902 |  |  | 8836 |  |  | -5105 | -5105 | -5019 | Critical Branch | Critical Branch | 66 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0630 | 8702 |  |  | 8634 |  |  | -4900 | -4900 | -4811 | Critical Branch | Critical Branch | 68 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250729 | July | 0730 | 8335 |  |  | 8328 |  |  | -1814 | -1814 | -1807 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 0830 | 8335 |  |  | 8328 |  |  | -1814 | -1814 | -1807 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 0930 | 7483 |  |  | 7483 |  |  | -3232 | -3232 | -3231 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 385
20250729 | July | 1030 | 7483 |  |  | 7483 |  |  | -3232 | -3232 | -3231 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 385
20250729 | July | 1130 | 7483 |  |  | 7483 |  |  | -3232 | -3232 | -3231 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 385
20250729 | July | 1230 | 7413 |  |  | 7412 |  |  | -3679 | -3679 | -3678 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 381
20250729 | July | 1330 | 7413 |  |  | 7412 |  |  | -3679 | -3679 | -3678 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 381
20250729 | July | 1430 | 7413 |  |  | 7412 |  |  | -3679 | -3679 | -3678 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 381
20250729 | July | 1530 | 8225 |  |  | 8224 |  |  | -4218 | -4218 | -4216 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 1630 | 8225 |  |  | 8224 |  |  | -4218 | -4218 | -4216 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 1730 | 8925 |  |  | 8924 |  |  | -4898 | -4898 | -4897 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 1830 |  | 8519 | 726 |  | 8517 | 726 | -1865 | -1865 | 0 | Critical Branch | Critical Branch | NA | 2 | 1865 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 1930 |  | 8519 | 726 |  | 8517 | 726 | -1865 | -1865 | 0 | Critical Branch | Critical Branch | NA | 2 | 1865 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 2030 |  | 8519 | 726 |  | 8517 | 726 | -1865 | -1865 | 0 | Critical Branch | Critical Branch | NA | 2 | 1865 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 2130 |  | 8901 | 731 |  | 8879 | 731 | -4572 | -4572 | 0 | Critical Branch | Critical Branch | NA | 22 | 4572 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 2230 |  | 8901 | 731 |  | 8879 | 731 | -4572 | -4572 | 0 | Critical Branch | Critical Branch | NA | 22 | 4572 |  |  | 425 | Reduction because NTC over thermal limit on border
20250729 | July | 2330 |  | 8321 | 756 |  | 8299 | 756 | -3946 | -3946 | 0 | Critical Branch | Critical Branch | NA | 22 | 3946 |  |  | 415 | Reduction because NTC over thermal limit on border
20250730 | July | 0030 | 9481 |  |  | 7476 |  |  | -3782 | -3782 | -1777 | Critical Branch | Validation phase | 2005 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7226 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 0130 | 9481 |  |  | 7476 |  |  | -3782 | -3782 | -1777 | Critical Branch | Validation phase | 2005 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7226 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 0230 | 9481 |  |  | 7476 |  |  | -3782 | -3782 | -1777 | Critical Branch | Validation phase | 2005 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7226 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 0330 | 9423 |  |  | 8567 |  |  | -3667 | -3667 | -2814 | Critical Branch | Validation phase | 856 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8323 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0430 | 9423 |  |  | 8567 |  |  | -3667 | -3667 | -2814 | Critical Branch | Validation phase | 856 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8323 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0530 | 9423 |  |  | 8567 |  |  | -3667 | -3667 | -2814 | Critical Branch | Validation phase | 856 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8323 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0630 | 9223 |  |  | 8366 |  |  | -3442 | -3442 | -2588 | Critical Branch | Validation phase | 857 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8123 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0730 | 8794 |  |  | 8181 |  |  | -1783 | -1783 | -1170 | Critical Branch | Validation phase | 613 | NA | 0 |  |  | 419 |  | 7931 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0830 | 8794 |  |  | 8181 |  |  | -1783 | -1783 | -1170 | Critical Branch | Validation phase | 613 | NA | 0 |  |  | 414 |  | 7931 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250730 | July | 0930 | 7183 |  |  | 7183 |  |  | -3245 | -3245 | -3245 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 361
20250730 | July | 1030 | 7183 |  |  | 7183 |  |  | -3245 | -3245 | -3245 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 361
20250730 | July | 1130 | 7183 |  |  | 7183 |  |  | -3245 | -3245 | -3245 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 361
20250730 | July | 1230 | 6196 |  |  | 6195 |  |  | -2343 | -2343 | -2342 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 307
20250730 | July | 1330 | 6196 |  |  | 6195 |  |  | -2343 | -2343 | -2342 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 307
20250730 | July | 1430 | 6196 |  |  | 6195 |  |  | -2343 | -2343 | -2342 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 307
20250730 | July | 1530 | 9266 |  |  | 7695 |  |  | -1546 | -1546 | 20 | Critical Branch | Validation phase | 1571 | NA | 1586 |  |  | 364 |  | 7978 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 1630 | 9266 |  |  | 8228 |  |  | -1546 | -1546 | -508 | Critical Branch | Validation phase | 1038 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7978 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 1730 | 9266 |  |  | 8228 |  |  | -1546 | -1546 | -508 | Critical Branch | Validation phase | 1038 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7978 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 1830 |  | 8545 | 673 |  | 7857 | 620 | -5474 | -5474 | 0 | Critical Branch | Validation phase | NA | 741 | 5474 |  |  | 425 | Reduction because NTC over thermal limit on border | 8159 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250730 | July | 1930 |  | 8545 | 673 |  | 7857 | 620 | -5474 | -5474 | 0 | Critical Branch | Validation phase | NA | 741 | 5474 |  |  | 425 | Reduction because NTC over thermal limit on border | 8159 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250730 | July | 2030 |  | 8545 | 673 |  | 7857 | 620 | -5474 | -5474 | 0 | Critical Branch | Validation phase | NA | 741 | 5474 |  |  | 425 | Reduction because NTC over thermal limit on border | 8159 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250730 | July | 2130 |  | 8633 | 692 |  | 8564 | 687 | -4330 | -4330 | 0 | Critical Branch | Validation phase | NA | 74 | 4330 |  |  | 425 | Reduction because NTC over thermal limit on border | 8677 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 2230 |  | 8633 | 692 |  | 8564 | 687 | -4330 | -4330 | 0 | Critical Branch | Validation phase | NA | 74 | 4330 |  |  | 425 | Reduction because NTC over thermal limit on border | 8677 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250730 | July | 2330 |  | 8053 | 717 |  | 8003 | 714 | -3703 | -3703 | 0 | Critical Branch | Validation phase | NA | 53 | 3703 |  |  | 415 | Reduction because NTC over thermal limit on border | 8077 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250731 | July | 0030 | 9161 |  |  | 8418 |  |  | -4909 | -4909 | -4166 | Critical Branch | Validation phase | 743 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8168 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0130 | 9161 |  |  | 8418 |  |  | -4909 | -4909 | -4166 | Critical Branch | Validation phase | 743 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8168 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0230 | 9161 |  |  | 8418 |  |  | -4909 | -4909 | -4166 | Critical Branch | Validation phase | 743 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8168 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0330 | 9157 |  |  | 8919 |  |  | -4911 | -4911 | -4682 | Critical Branch | Validation phase | 238 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8695 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0430 | 9157 |  |  | 8919 |  |  | -4911 | -4911 | -4682 | Critical Branch | Validation phase | 238 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8695 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0530 | 9157 |  |  | 8919 |  |  | -4911 | -4911 | -4682 | Critical Branch | Validation phase | 238 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8695 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0630 | 8957 |  |  | 8718 |  |  | -4704 | -4704 | -4475 | Critical Branch | Validation phase | 239 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8495 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 0730 | 8642 |  |  | 7895 |  |  | -2043 | -2043 | -1296 | Critical Branch | Validation phase | 747 | NA | 0 |  |  | 411 |  | 7645 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0830 | 8642 |  |  | 7895 |  |  | -2043 | -2043 | -1296 | Critical Branch | Validation phase | 747 | NA | 0 |  |  | 411 |  | 7645 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 0930 | 7994 |  |  | 7994 |  |  | -4792 | -4792 | -4792 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 379
20250731 | July | 1030 | 7994 |  |  | 7994 |  |  | -4792 | -4792 | -4792 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 379
20250731 | July | 1130 | 7994 |  |  | 7994 |  |  | -4792 | -4792 | -4792 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 379
20250731 | July | 1230 | 9132 |  |  | 8165 |  |  | -4374 | -4374 | -3407 | Critical Branch | Validation phase | 967 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7915 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1330 | 9132 |  |  | 8165 |  |  | -4374 | -4374 | -3407 | Critical Branch | Validation phase | 967 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7915 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1430 | 9132 |  |  | 8165 |  |  | -4374 | -4374 | -3407 | Critical Branch | Validation phase | 967 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7915 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1530 | 8601 |  |  | 8472 |  |  | -3673 | -3673 | -3544 | Critical Branch | Validation phase | 129 | NA | 0 |  |  | 409 |  | 8222 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 1630 | 8601 |  |  | 8472 |  |  | -3673 | -3673 | -3544 | Critical Branch | Validation phase | 129 | NA | 0 |  |  | 409 |  | 8222 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 1730 | 8601 |  |  | 8472 |  |  | -3673 | -3673 | -3544 | Critical Branch | Validation phase | 129 | NA | 0 |  |  | 409 |  | 8222 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250731 | July | 1830 |  | 8644 | 678 |  | 8568 | 673 | -4284 | -4284 | 0 | Critical Branch | Validation phase | NA | 81 | 4284 |  |  | 425 | Reduction because NTC over thermal limit on border | 8689 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 1930 |  | 8644 | 678 |  | 8568 | 673 | -4284 | -4284 | 0 | Critical Branch | Validation phase | NA | 81 | 4284 |  |  | 425 | Reduction because NTC over thermal limit on border | 8689 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 2030 |  | 8644 | 678 |  | 8568 | 673 | -4284 | -4284 | 0 | Critical Branch | Validation phase | NA | 81 | 4284 |  |  | 425 | Reduction because NTC over thermal limit on border | 8689 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250731 | July | 2130 |  | 8703 | 673 |  | 8691 | 673 | -4127 | -4127 | 0 | Critical Branch | Critical Branch | NA | 12 | 4127 |  |  | 425 | Reduction because NTC over thermal limit on border
20250731 | July | 2230 |  | 8703 | 673 |  | 8691 | 673 | -4127 | -4127 | 0 | Critical Branch | Critical Branch | NA | 12 | 4127 |  |  | 425 | Reduction because NTC over thermal limit on border
20250731 | July | 2330 |  | 8123 | 698 |  | 8112 | 698 | -3504 | -3504 | 0 | Critical Branch | Critical Branch | NA | 11 | 3504 |  |  | 415 | Reduction because NTC over thermal limit on border
20250801 | August | 0030 | 8910 |  |  | 8712 |  |  | -2167 | -2167 | -1969 | Critical Branch | Validation phase | 198 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8476 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250801 | August | 0130 | 8910 |  |  | 8712 |  |  | -2167 | -2167 | -1969 | Critical Branch | Validation phase | 198 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8476 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250801 | August | 0230 | 8910 |  |  | 8712 |  |  | -2167 | -2167 | -1969 | Critical Branch | Validation phase | 198 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8476 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250801 | August | 0330 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 69 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8669 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0430 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 69 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8669 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0530 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 69 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8669 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0630 | 8964 |  |  | 8895 |  |  | -4687 | -4687 | -4626 | Critical Branch | Validation phase | 69 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8669 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250801 | August | 0730 | 8654 |  |  | 8654 |  |  | -1679 | -1679 | -1679 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 405
20250801 | August | 0830 | 8654 |  |  | 8654 |  |  | -1679 | -1679 | -1679 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 405
20250801 | August | 0930 | 8572 |  |  | 8572 |  |  | -4609 | -4609 | -4609 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 401
20250801 | August | 1030 | 8572 |  |  | 8572 |  |  | -4609 | -4609 | -4609 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 401
20250801 | August | 1130 | 8572 |  |  | 8572 |  |  | -4609 | -4609 | -4609 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 401
20250801 | August | 1230 | 8573 |  |  | 8573 |  |  | -4753 | -4753 | -4753 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 401
20250801 | August | 1330 | 8573 |  |  | 8573 |  |  | -4753 | -4753 | -4753 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 401
20250801 | August | 1430 | 8573 |  |  | 8573 |  |  | -4753 | -4753 | -4753 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 401
20250801 | August | 1530 | 8035 |  |  | 8034 |  |  | -4414 | -4414 | -4414 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 374
20250801 | August | 1630 | 8035 |  |  | 8034 |  |  | -4414 | -4414 | -4414 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 374
20250801 | August | 1730 | 8035 |  |  | 8034 |  |  | -4414 | -4414 | -4414 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 374
20250801 | August | 1830 |  | 8589 | 668 |  | 8583 | 668 | -5937 | -5937 | 0 | Critical Branch | Critical Branch | NA | 6 | 5937 |  |  | 425 | Reduction because NTC over thermal limit on border
20250801 | August | 1930 |  | 8589 | 668 |  | 8583 | 668 | -5937 | -5937 | 0 | Critical Branch | Critical Branch | NA | 6 | 5937 |  |  | 425 | Reduction because NTC over thermal limit on border
20250801 | August | 2030 |  | 8589 | 668 |  | 8583 | 668 | -5937 | -5937 | 0 | Critical Branch | Critical Branch | NA | 6 | 5937 |  |  | 425 | Reduction because NTC over thermal limit on border
20250801 | August | 2130 |  | 8561 | 668 |  | 8557 | 668 | -5755 | -5755 | 0 | Critical Branch | Critical Branch | NA | 4 | 5755 |  |  | 425 | Reduction because NTC over thermal limit on border
20250801 | August | 2230 |  | 8561 | 668 |  | 8557 | 668 | -5755 | -5755 | 0 | Critical Branch | Critical Branch | NA | 4 | 5755 |  |  | 425 | Reduction because NTC over thermal limit on border
20250801 | August | 2330 |  | 7981 | 693 |  | 7978 | 693 | -5128 | -5128 | 0 | Critical Branch | Critical Branch | NA | 3 | 5128 |  |  | 415 | Reduction because NTC over thermal limit on border
20250802 | August | 0030 | 9450 |  |  | 9274 |  |  | -5024 | -5024 | -4864 | Critical Branch | Validation phase | 176 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 9069 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250802 | August | 0130 | 9450 |  |  | 9274 |  |  | -5024 | -5024 | -4864 | Critical Branch | Validation phase | 176 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 9069 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250802 | August | 0230 | 9450 |  |  | 9274 |  |  | -5024 | -5024 | -4864 | Critical Branch | Validation phase | 176 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 9069 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250802 | August | 0330 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8923 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0430 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8923 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0530 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8923 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0630 | 9453 |  |  | 9135 |  |  | -1954 | -1954 | -1639 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8923 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250802 | August | 0730 | 9146 |  |  | 9141 |  |  | -5506 | -5506 | -5500 | Critical Branch | Critical Branch | 5 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250802 | August | 0830 | 9146 |  |  | 9141 |  |  | -5506 | -5506 | -5500 | Critical Branch | Critical Branch | 5 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250802 | August | 0930 | 8072 |  |  | 8072 |  |  | -3982 | -3982 | -3982 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 376
20250802 | August | 1030 | 8072 |  |  | 8072 |  |  | -3982 | -3982 | -3982 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 376
20250802 | August | 1130 | 8072 |  |  | 8072 |  |  | -3982 | -3982 | -3982 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 376
20250802 | August | 1230 | 8509 |  |  | 8509 |  |  | -5054 | -5054 | -5054 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 398
20250802 | August | 1330 | 8509 |  |  | 8509 |  |  | -5054 | -5054 | -5054 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 398
20250802 | August | 1430 | 8509 |  |  | 8509 |  |  | -5054 | -5054 | -5054 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 398
20250802 | August | 1530 | 8897 |  |  | 8897 |  |  | -3560 | -3560 | -3560 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 417
20250802 | August | 1630 | 8897 |  |  | 8897 |  |  | -3560 | -3560 | -3560 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 417
20250802 | August | 1730 | 8897 |  |  | 8897 |  |  | -3560 | -3560 | -3560 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 417
20250802 | August | 1830 |  | 8574 | 682 |  | 8569 | 682 | -4924 | -4924 | 0 | Critical Branch | Critical Branch | NA | 5 | 4924 |  |  | 425 | Reduction because NTC over thermal limit on border
20250802 | August | 1930 |  | 8574 | 682 |  | 8569 | 682 | -4924 | -4924 | 0 | Critical Branch | Critical Branch | NA | 5 | 4924 |  |  | 425 | Reduction because NTC over thermal limit on border
20250802 | August | 2030 |  | 8574 | 682 |  | 8569 | 682 | -4924 | -4924 | 0 | Critical Branch | Critical Branch | NA | 5 | 4924 |  |  | 425 | Reduction because NTC over thermal limit on border
20250802 | August | 2130 | 8859 |  |  | 8858 |  |  | -5115 | -5115 | -5115 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 415
20250802 | August | 2230 | 8859 |  |  | 8858 |  |  | -5115 | -5115 | -5115 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 415
20250802 | August | 2330 | 8259 |  |  | 8259 |  |  | -4511 | -4511 | -4511 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 405
20250803 | August | 0030 | 9279 |  |  | 9236 |  |  | -5149 | -5149 | -5120 | Critical Branch | Critical Branch | 43 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0130 | 9279 |  |  | 9236 |  |  | -5149 | -5149 | -5120 | Critical Branch | Critical Branch | 43 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0230 | 9279 |  |  | 9236 |  |  | -5149 | -5149 | -5120 | Critical Branch | Critical Branch | 43 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0330 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0430 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0530 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0630 | 8721 |  |  | 8707 |  |  | -3955 | -3955 | -3947 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0730 | 8722 |  |  | 8708 |  |  | -5768 | -5768 | -5749 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0830 | 8722 |  |  | 8708 |  |  | -5768 | -5768 | -5749 | Critical Branch | Critical Branch | 14 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 0930 | 8558 |  |  | 8552 |  |  | -4182 | -4182 | -4178 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1030 | 8558 |  |  | 8552 |  |  | -4182 | -4182 | -4178 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1130 | 8558 |  |  | 8552 |  |  | -4182 | -4182 | -4178 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1230 | 8589 |  |  | 8582 |  |  | -1353 | -1353 | -1346 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1330 | 8589 |  |  | 8582 |  |  | -1353 | -1353 | -1346 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1430 | 8589 |  |  | 8582 |  |  | -1353 | -1353 | -1346 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1530 |  | 8518 | 774 |  | 8485 | 774 | -1068 | -1068 | 0 | Critical Branch | Critical Branch | NA | 33 | 1068 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1630 |  | 8518 | 774 |  | 8485 | 774 | -1068 | -1068 | 0 | Critical Branch | Critical Branch | NA | 33 | 1068 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1730 |  | 8518 | 774 |  | 8485 | 774 | -1068 | -1068 | 0 | Critical Branch | Critical Branch | NA | 33 | 1068 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1830 |  | 8851 | 796 |  | 8799 | 796 | -3429 | -3429 | 0 | Critical Branch | Critical Branch | NA | 52 | 3429 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 1930 |  | 8851 | 796 |  | 8799 | 796 | -3429 | -3429 | 0 | Critical Branch | Critical Branch | NA | 52 | 3429 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 2030 |  | 8851 | 796 |  | 8799 | 796 | -3429 | -3429 | 0 | Critical Branch | Critical Branch | NA | 52 | 3429 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 2130 | 9271 |  |  | 9228 |  |  | -3343 | -3343 | -3318 | Critical Branch | Critical Branch | 43 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 2230 | 9271 |  |  | 9228 |  |  | -3343 | -3343 | -3318 | Critical Branch | Critical Branch | 43 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250803 | August | 2330 | 9271 |  |  | 9228 |  |  | -3343 | -3343 | -3318 | Critical Branch | Critical Branch | 43 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0030 | 8815 |  |  | 8796 |  |  | -5588 | -5588 | -5575 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0130 | 8815 |  |  | 8796 |  |  | -5588 | -5588 | -5575 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0230 | 8815 |  |  | 8796 |  |  | -5588 | -5588 | -5575 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0330 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0430 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0530 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0630 | 8802 |  |  | 8784 |  |  | -5290 | -5290 | -5278 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250804 | August | 0730 | 7995 |  |  | 7624 |  |  | -3980 | -3980 | -3609 | Critical Branch | Validation phase | 371 | NA | 0 |  |  | 397 |  | 7374 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 0830 | 6595 |  |  | 6224 |  |  | -2615 | -2615 | -2244 | Critical Branch | Validation phase | 371 | NA | 0 |  |  | 391 |  | 5974 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 0930 | 6360 |  |  | 6224 |  |  | -3673 | -3673 | -3537 | Critical Branch | Validation phase | 136 | NA | 0 |  |  | 376 |  | 5974 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1030 | 6360 |  |  | 6224 |  |  | -3673 | -3673 | -3537 | Critical Branch | Validation phase | 136 | NA | 0 |  |  | 376 |  | 5974 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1130 | 6360 |  |  | 6224 |  |  | -3673 | -3673 | -3537 | Critical Branch | Validation phase | 136 | NA | 0 |  |  | 376 |  | 5974 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1230 | 6101 |  |  | 6100 |  |  | -3348 | -3348 | -3348 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 359
20250804 | August | 1330 | 6101 |  |  | 6100 |  |  | -3348 | -3348 | -3348 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 359
20250804 | August | 1430 | 6101 |  |  | 6100 |  |  | -3348 | -3348 | -3348 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 359
20250804 | August | 1530 |  | 6366 | 0 |  | 6306 | 0 | -4307 | -4307 | 0 | TTC Selection - LTTCExport | Validation phase | NA | 60 | 4307 |  |  | 376 |  | 6056 | Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250804 | August | 1630 |  | 6366 | 0 |  | 6306 | 0 | -4307 | -4307 | 0 | TTC Selection - LTTCExport | Validation phase | NA | 60 | 4307 |  |  | 376 |  | 6056 | Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250804 | August | 1730 |  | 6366 | 0 |  | 6306 | 0 | -4307 | -4307 | 0 | TTC Selection - LTTCExport | Validation phase | NA | 60 | 4307 |  |  | 376 |  | 6056 | Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250804 | August | 1830 |  | 6303 | 0 |  | 6258 | 0 | -4259 | -4259 | 0 | TTC Selection - LTTCExport | Validation phase | NA | 45 | 4259 |  |  | 372 |  | 6008 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 1930 |  | 6303 | 0 |  | 6258 | 0 | -4259 | -4259 | 0 | TTC Selection - LTTCExport | Validation phase | NA | 45 | 4259 |  |  | 372 |  | 6008 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 2030 |  | 6303 | 0 |  | 6258 | 0 | -4259 | -4259 | 0 | TTC Selection - LTTCExport | Validation phase | NA | 45 | 4259 |  |  | 372 |  | 6008 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250804 | August | 2130 |  | 5678 | 0 |  | 5677 | 0 | -3395 | -3395 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | NA | 1 | 3395 |  |  | 332
20250804 | August | 2230 |  | 5378 | 0 |  | 5378 | 0 | -3110 | -3110 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | NA | 0 | 3110 |  |  | 328
20250804 | August | 2330 |  | 4818 | 0 |  | 4818 | 0 | -2543 | -2543 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | NA | 0 | 2543 |  |  | 311
20250805 | August | 0930 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1030 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1130 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1230 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1330 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1430 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1530 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1630 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250805 | August | 1730 | 7116 |  |  | 5657 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1459 | NA | 0 |  |  |  |  | 5407 | No calculation has been done
20250806 | August | 0030 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0130 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0230 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0330 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0430 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0530 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0630 | 6556 |  |  | 6556 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0730 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0830 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 0930 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1030 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1130 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1230 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1330 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1430 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1530 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1630 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1730 | 7116 |  |  | 7116 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1830 |  | 5616 | 0 |  | 5616 | 0 | -2341 | -2341 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | NA | 0 | 2341 |  |  |  |  | 6866 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 1930 |  | 5616 | 0 |  | 5616 | 0 | -2341 | -2341 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | NA | 0 | 2341 |  |  |  |  | 6866 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2030 |  | 5616 | 0 |  | 5616 | 0 | -2341 | -2341 | 0 | TTC Selection - LTTCExport | TTC Selection - LTTCExport | NA | 0 | 2341 |  |  |  |  | 6866 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2130 | 6131 |  |  | 6131 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 6866 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2230 | 6131 |  |  | 6131 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 6866 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250806 | August | 2330 | 5571 |  |  | 5571 |  |  | -1011 | -1011 | -1011 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 6306 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250808 | August | 1230 | 6369 |  |  | 6250 |  |  | -1025 | -1025 | -906 | Critical Branch | Validation phase | 119 | NA | 0 |  |  |  |  | 6000 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1330 | 6369 |  |  | 6250 |  |  | -1025 | -1025 | -906 | Critical Branch | Validation phase | 119 | NA | 0 |  |  |  |  | 6000 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1430 | 6369 |  |  | 6250 |  |  | -1025 | -1025 | -906 | Critical Branch | Validation phase | 119 | NA | 0 |  |  |  |  | 6000 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1530 | 6375 |  |  | 6271 |  |  | -962 | -962 | -858 | Critical Branch | Validation phase | 104 | NA | 0 |  |  |  |  | 6021 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1630 | 6375 |  |  | 6271 |  |  | -962 | -962 | -858 | Critical Branch | Validation phase | 104 | NA | 0 |  |  |  |  | 6021 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250808 | August | 1730 | 6375 |  |  | 6271 |  |  | -962 | -962 | -858 | Critical Branch | Validation phase | 104 | NA | 0 |  |  |  |  | 6021 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250809 | August | 1230 | 5255 |  |  | 5124 |  |  | -499 | -499 | -368 | Critical Branch | Validation phase | 131 | NA | 0 |  |  |  |  | 4874 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250809 | August | 1330 | 5255 |  |  | 5124 |  |  | -499 | -499 | -368 | Critical Branch | Validation phase | 131 | NA | 0 |  |  |  |  | 4874 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250809 | August | 1430 | 5255 |  |  | 5124 |  |  | -499 | -499 | -368 | Critical Branch | Validation phase | 131 | NA | 0 |  |  |  |  | 4874 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250811 | August | 0330 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 251 | NA | 0 |  |  |  |  | 5571 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0430 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 251 | NA | 0 |  |  |  |  | 5571 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0530 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 251 | NA | 0 |  |  |  |  | 5571 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0630 | 6072 |  |  | 5821 |  |  | -2458 | -2458 | -2207 | Critical Branch | Validation phase | 251 | NA | 0 |  |  |  |  | 5571 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250811 | August | 0930 | 5378 |  |  | 5038 |  |  | 2680 | 432 | 2588 | Minimum Margin | Validation phase | 340 | NA | 4744 |  |  |  |  | 4788 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250811 | August | 1030 | 5378 |  |  | 5038 |  |  | 2680 | 432 | 2588 | Minimum Margin | Validation phase | 340 | NA | 4744 |  |  |  |  | 4788 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250811 | August | 1130 | 5378 |  |  | 5038 |  |  | 2680 | 432 | 2588 | Minimum Margin | Validation phase | 340 | NA | 4744 |  |  |  |  | 4788 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250811 | August | 1230 | 5377 |  |  | 5365 |  |  | -461 | -461 | -449 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 5115 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250811 | August | 1330 | 5377 |  |  | 5365 |  |  | -461 | -461 | -449 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 5115 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250811 | August | 1430 | 5377 |  |  | 5365 |  |  | -461 | -461 | -449 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 5115 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250812 | August | 0330 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 241 | NA | 0 |  |  |  |  | 5599 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0430 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 241 | NA | 0 |  |  |  |  | 5599 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0530 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 241 | NA | 0 |  |  |  |  | 5599 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250812 | August | 0630 | 6090 |  |  | 5849 |  |  | -3017 | -3017 | -2776 | Critical Branch | Validation phase | 241 | NA | 0 |  |  |  |  | 5599 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ
20250813 | August | 0330 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6118 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0430 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6118 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0530 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6118 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250813 | August | 0630 | 6380 |  |  | 6368 |  |  | -1504 | -1504 | -1492 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6118 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250814 | August | 0030 | 6883 |  |  | 6871 |  |  | -3705 | -3705 | -3693 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6621 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250814 | August | 0130 | 6883 |  |  | 6871 |  |  | -3705 | -3705 | -3693 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6621 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250814 | August | 0230 | 6883 |  |  | 6871 |  |  | -3705 | -3705 | -3693 | Critical Branch | Validation phase | 12 | NA | 0 |  |  |  |  | 6621 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250814 | August | 0930 | 5480 |  |  | 5250 |  |  | -4242 | -4242 | -4012 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 | [10 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1030 | 5480 |  |  | 5250 |  |  | -4242 | -4242 | -4012 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 | [10 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1130 | 5480 |  |  | 5250 |  |  | -4242 | -4242 | -4012 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 | [10 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1230 | 5480 |  |  | 5250 |  |  | -3281 | -3281 | -3051 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 | [10 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1330 | 5480 |  |  | 5250 |  |  | -3281 | -3281 | -3051 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 | [10 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1430 | 5480 |  |  | 5250 |  |  | -3281 | -3281 | -3051 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 | [10 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250814 | August | 1530 | 6911 |  |  | 6750 |  |  | -3608 | -3608 | -3447 | Critical Branch | Smoothing ramp | 161 | NA | 0 | Smoothing | Smoothing ramp
20250815 | August | 0030 |  | 7209 | 192 |  | 4996 | 160 | -4486 | -4486 | 0 | Critical Branch | Validation phase | NA | 2245 | 4486 |  |  | 220 |  | 6189 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0130 |  | 7209 | 192 |  | 4996 | 160 | -4486 | -4486 | 0 | Critical Branch | Validation phase | NA | 2245 | 4486 |  |  | 220 |  | 6189 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0230 |  | 7209 | 192 |  | 4996 | 160 | -4486 | -4486 | 0 | Critical Branch | Validation phase | NA | 2245 | 4486 |  |  | 220 |  | 6189 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0330 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 2374 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5191 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0430 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 2374 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5191 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0530 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 2374 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5191 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0630 | 7160 |  |  | 4786 |  |  | -3854 | -3854 | -1433 | Critical Branch | Validation phase | 2374 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5191 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0730 |  | 6553 | 173 |  | 4695 | 145 | -3807 | -3807 | 0 | Critical Branch | Validation phase | NA | 1886 | 3807 |  |  | 198 |  | 5680 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0830 |  | 6553 | 173 |  | 4695 | 145 | -3807 | -3807 | 0 | Critical Branch | Validation phase | NA | 1886 | 3807 |  |  | 198 |  | 5680 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 0930 | 5658 |  |  | 4571 |  |  | -1790 | -1790 | -785 | Critical Branch | Validation phase | 1087 | NA | 0 |  |  | 325 |  | 4873 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1030 | 5658 |  |  | 4571 |  |  | -1790 | -1790 | -785 | Critical Branch | Validation phase | 1087 | NA | 0 |  |  | 325 |  | 4873 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1130 | 5658 |  |  | 4571 |  |  | -1790 | -1790 | -785 | Critical Branch | Validation phase | 1087 | NA | 0 |  |  | 325 |  | 4873 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1230 | 6470 |  |  | 4989 |  |  | -3546 | -3546 | -2047 | Critical Branch | Validation phase | 1481 | NA | 0 |  |  | 377 |  | 5504 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1330 | 6470 |  |  | 4989 |  |  | -3546 | -3546 | -2047 | Critical Branch | Validation phase | 1481 | NA | 0 |  |  | 377 |  | 5504 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1430 | 6470 |  |  | 4989 |  |  | -3546 | -3546 | -2047 | Critical Branch | Validation phase | 1481 | NA | 0 |  |  | 377 |  | 5504 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1530 |  | 6609 | 724 |  | 4600 | 594 | -2817 | -2817 | 0 | Critical Branch | Validation phase | NA | 2139 | 2817 |  |  | 415 | Reduction because NTC over thermal limit on border | 5665 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1630 |  | 6609 | 724 |  | 4600 | 594 | -2817 | -2817 | 0 | Critical Branch | Validation phase | NA | 2139 | 2817 |  |  | 415 | Reduction because NTC over thermal limit on border | 5665 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1730 |  | 6609 | 724 |  | 4600 | 594 | -2817 | -2817 | 0 | Critical Branch | Validation phase | NA | 2139 | 2817 |  |  | 415 | Reduction because NTC over thermal limit on border | 5665 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1830 |  | 6555 | 704 |  | 4609 | 581 | -4187 | -4187 | 0 | Critical Branch | Validation phase | NA | 2069 | 4187 |  |  | 415 | Reduction because NTC over thermal limit on border | 5675 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 1930 |  | 6555 | 704 |  | 4609 | 581 | -4187 | -4187 | 0 | Critical Branch | Validation phase | NA | 2069 | 4187 |  |  | 415 | Reduction because NTC over thermal limit on border | 5675 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 2030 |  | 6555 | 704 |  | 4609 | 581 | -4187 | -4187 | 0 | Critical Branch | Validation phase | NA | 2069 | 4187 |  |  | 415 | Reduction because NTC over thermal limit on border | 5675 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 2130 |  | 7308 | 811 |  | 5165 | 701 | -5260 | -5260 | 0 | Critical Branch | Validation phase | NA | 2253 | 5260 |  |  | 415 | Reduction because NTC over thermal limit on border | 6611 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 2230 |  | 7308 | 811 |  | 5165 | 701 | -5260 | -5260 | 0 | Critical Branch | Validation phase | NA | 2253 | 5260 |  |  | 415 | Reduction because NTC over thermal limit on border | 6611 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250815 | August | 2330 |  | 7308 | 811 |  | 5165 | 701 | -5260 | -5260 | 0 | Critical Branch | Validation phase | NA | 2253 | 5260 |  |  | 415 | Reduction because NTC over thermal limit on border | 6601 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 1200 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | 1017 | Outage of HVDC FIL link 1 and link 2
20250816 | August | 0030 | 7253 |  |  | 6018 |  |  | -3699 | -3699 | -2464 | Critical Branch | Validation phase | 1235 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5768 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0130 | 7253 |  |  | 6018 |  |  | -3699 | -3699 | -2464 | Critical Branch | Validation phase | 1235 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5768 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0230 | 7253 |  |  | 6018 |  |  | -3699 | -3699 | -2464 | Critical Branch | Validation phase | 1235 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5768 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0330 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 1269 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5491 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0430 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 1269 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5491 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0530 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 1269 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5491 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0630 | 7010 |  |  | 5741 |  |  | -3282 | -3282 | -2013 | Critical Branch | Validation phase | 1269 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5491 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0730 | 7212 |  |  | 6010 |  |  | -3565 | -3565 | -2363 | Critical Branch | Validation phase | 1202 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 5760 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0830 | 7212 |  |  | 6010 |  |  | -3565 | -3565 | -2363 | Critical Branch | Validation phase | 1202 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 5760 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 0930 |  | 6932 | 838 |  | 6567 | 801 | -2566 | -2566 | 0 | Critical Branch | Validation phase | NA | 402 | 2566 |  |  | 425 | Reduction because NTC over thermal limit on border | 6915 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1030 |  | 6932 | 838 |  | 6567 | 801 | -2566 | -2566 | 0 | Critical Branch | Validation phase | NA | 402 | 2566 |  |  | 425 | Reduction because NTC over thermal limit on border | 6915 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1130 |  | 6932 | 838 |  | 6567 | 801 | -2566 | -2566 | 0 | Critical Branch | Validation phase | NA | 402 | 2566 |  |  | 425 | Reduction because NTC over thermal limit on border | 6915 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1230 | 7050 |  |  | 6615 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 435 | NA | 0 |  |  | 425 |  | 6365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1330 | 7050 |  |  | 6615 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 435 | NA | 0 |  |  | 425 |  | 6365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1430 | 7050 |  |  | 6615 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 435 | NA | 0 |  |  | 425 |  | 6365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1530 |  | 7078 | 755 |  | 6476 | 693 | -3843 | -3843 | 0 | Critical Branch | Validation phase | NA | 664 | 3843 |  |  | 425 | Reduction because NTC over thermal limit on border | 6829 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1630 |  | 7078 | 755 |  | 6476 | 693 | -3843 | -3843 | 0 | Critical Branch | Validation phase | NA | 664 | 3843 |  |  | 425 | Reduction because NTC over thermal limit on border | 6829 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1730 |  | 7078 | 755 |  | 6476 | 693 | -3843 | -3843 | 0 | Critical Branch | Validation phase | NA | 664 | 3843 |  |  | 425 | Reduction because NTC over thermal limit on border | 6829 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1830 |  | 7174 | 755 |  | 6515 | 687 | -4939 | -4939 | 0 | Critical Branch | Validation phase | NA | 727 | 4939 |  |  | 425 | Reduction because NTC over thermal limit on border | 6879 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 1930 |  | 7174 | 755 |  | 6515 | 687 | -4939 | -4939 | 0 | Critical Branch | Validation phase | NA | 727 | 4939 |  |  | 425 | Reduction because NTC over thermal limit on border | 6879 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2030 |  | 7174 | 755 |  | 6515 | 687 | -4939 | -4939 | 0 | Critical Branch | Validation phase | NA | 727 | 4939 |  |  | 425 | Reduction because NTC over thermal limit on border | 6879 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2130 | 7669 |  |  | 6602 |  |  | -1688 | -1688 | -621 | Critical Branch | Validation phase | 1067 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6352 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2230 | 7669 |  |  | 6602 |  |  | -1688 | -1688 | -621 | Critical Branch | Validation phase | 1067 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6352 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250816 | August | 2330 | 7069 |  |  | 6002 |  |  | -1087 | -1087 | -20 | Critical Branch | Validation phase | 1067 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5752 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250817 | August | 0030 | 7567 |  |  | 7050 |  |  | -1267 | -1267 | -756 | Critical Branch | Validation phase | 517 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6828 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0130 | 7567 |  |  | 7050 |  |  | -1267 | -1267 | -756 | Critical Branch | Validation phase | 517 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6828 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0230 | 7567 |  |  | 7050 |  |  | -1267 | -1267 | -756 | Critical Branch | Validation phase | 517 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6828 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0330 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250817 | August | 0430 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250817 | August | 0530 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250817 | August | 0630 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250817 | August | 0730 |  | 7117 | 1242 |  | 6689 | 1169 | -4520 | -4520 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 501 | 4520 |  |  | 227 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0830 |  | 7117 | 1242 |  | 6689 | 1169 | -4520 | -4520 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 501 | 4520 |  |  | 227 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 0930 |  | 7078 | 844 |  | 6818 | 844 | -1324 | -1324 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 260 | 1324 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1030 |  | 7078 | 844 |  | 6818 | 844 | -1324 | -1324 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 260 | 1324 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1130 |  | 7078 | 844 |  | 6818 | 844 | -1324 | -1324 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 260 | 1324 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1230 |  | 6617 | 718 |  | 6361 | 691 | -295 | -295 | 0 | Critical Branch | Validation phase | NA | 283 | 295 |  |  | 415 | Reduction because NTC over thermal limit on border | 6631 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250817 | August | 1330 |  | 6617 | 718 |  | 6361 | 691 | -295 | -295 | 0 | Critical Branch | Validation phase | NA | 283 | 295 |  |  | 415 | Reduction because NTC over thermal limit on border | 6631 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250817 | August | 1430 |  | 6617 | 718 |  | 6361 | 691 | -295 | -295 | 0 | Critical Branch | Validation phase | NA | 283 | 295 |  |  | 415 | Reduction because NTC over thermal limit on border | 6631 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250817 | August | 1530 |  | 7240 | 831 |  | 6858 | 821 | -5 | -5 | 0 | Critical Branch | Validation phase | NA | 392 | 5 |  |  | 415 | Reduction because NTC over thermal limit on border | 7293 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1630 |  | 7240 | 831 |  | 6858 | 821 | -5 | -5 | 0 | Critical Branch | Validation phase | NA | 392 | 5 |  |  | 415 | Reduction because NTC over thermal limit on border | 7293 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1730 |  | 7240 | 831 |  | 6858 | 821 | -5 | -5 | 0 | Critical Branch | Validation phase | NA | 392 | 5 |  |  | 415 | Reduction because NTC over thermal limit on border | 7293 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1830 |  | 7083 | 791 |  | 6820 | 791 | -2468 | -2468 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 263 | 2468 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 1930 |  | 7083 | 791 |  | 6820 | 791 | -2468 | -2468 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 263 | 2468 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2030 |  | 7083 | 791 |  | 6820 | 791 | -2468 | -2468 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 263 | 2468 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2130 |  | 7143 | 818 |  | 6687 | 786 | -5023 | -5023 | 0 | Critical Branch | Validation phase | NA | 488 | 5023 |  |  | 415 | Reduction because NTC over thermal limit on border | 7159 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2230 |  | 7143 | 818 |  | 6687 | 786 | -5023 | -5023 | 0 | Critical Branch | Validation phase | NA | 488 | 5023 |  |  | 415 | Reduction because NTC over thermal limit on border | 7159 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250817 | August | 2330 |  | 7143 | 818 |  | 6687 | 786 | -5023 | -5023 | 0 | Critical Branch | Validation phase | NA | 488 | 5023 |  |  | 415 | Reduction because NTC over thermal limit on border | 7159 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0030 |  | 6822 | 1152 |  | 6055 | 1011 | -3312 | -3312 | 0 | Critical Branch | Validation phase | NA | 908 | 3312 |  |  | 217 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0130 |  | 6822 | 1152 |  | 6055 | 1011 | -3312 | -3312 | 0 | Critical Branch | Validation phase | NA | 908 | 3312 |  |  | 217 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0230 |  | 6822 | 1152 |  | 6055 | 1011 | -3312 | -3312 | 0 | Critical Branch | Validation phase | NA | 908 | 3312 |  |  | 217 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0330 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | NA | 456 | 1793 |  |  | 203 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0430 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | NA | 456 | 1793 |  |  | 203 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0530 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | NA | 456 | 1793 |  |  | 203 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0630 |  | 6413 | 1170 |  | 6055 | 1072 | -1793 | -1793 | 0 | Critical Branch | Validation phase | NA | 456 | 1793 |  |  | 203 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0730 |  | 6190 | 905 |  | 6047 | 879 | -2088 | -2088 | 0 | Critical Branch | Validation phase | NA | 169 | 2088 |  |  | 183 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0830 |  | 6190 | 905 |  | 6047 | 879 | -2088 | -2088 | 0 | Critical Branch | Validation phase | NA | 169 | 2088 |  |  | 183 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 0930 | 5480 |  |  | 5250 |  |  | -4445 | -4445 | -4215 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  |  |  | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250818 | August | 1030 | 5480 |  |  | 5250 |  |  | -4445 | -4445 | -4215 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  |  |  | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250818 | August | 1130 | 5480 |  |  | 5250 |  |  | -4445 | -4445 | -4215 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  |  |  | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250818 | August | 1230 | 6771 |  |  | 6141 |  |  | 95 | 95 | 630 | Adjustment reached | Validation phase | 630 | NA | 1165 |  |  | 372 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250818 | August | 1330 | 6771 |  |  | 6141 |  |  | 95 | 95 | 630 | Adjustment reached | Validation phase | 630 | NA | 1165 |  |  | 372 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250818 | August | 1430 | 6771 |  |  | 6141 |  |  | 95 | 95 | 630 | Adjustment reached | Validation phase | 630 | NA | 1165 |  |  | 372 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250818 | August | 1530 |  | 7097 | 696 |  | 6104 | 603 | -4090 | -4090 | 0 | Critical Branch | Validation phase | NA | 1086 | 4090 |  |  | 425 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1630 |  | 7097 | 696 |  | 6104 | 603 | -4090 | -4090 | 0 | Critical Branch | Validation phase | NA | 1086 | 4090 |  |  | 425 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1730 |  | 7097 | 696 |  | 6104 | 603 | -4090 | -4090 | 0 | Critical Branch | Validation phase | NA | 1086 | 4090 |  |  | 425 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1830 |  | 6378 | 783 |  | 6047 | 746 | -4243 | -4243 | 0 | Critical Branch | Validation phase | NA | 368 | 4243 |  |  | 227 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 1930 |  | 6378 | 783 |  | 6047 | 746 | -4243 | -4243 | 0 | Critical Branch | Validation phase | NA | 368 | 4243 |  |  | 227 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2030 |  | 6378 | 783 |  | 6047 | 746 | -4243 | -4243 | 0 | Critical Branch | Validation phase | NA | 368 | 4243 |  |  | 227 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2130 |  | 6778 | 890 |  | 6047 | 804 | -4188 | -4188 | 0 | Critical Branch | Validation phase | NA | 817 | 4188 |  |  | 202 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2230 |  | 6778 | 890 |  | 6047 | 804 | -4188 | -4188 | 0 | Critical Branch | Validation phase | NA | 817 | 4188 |  |  | 202 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250818 | August | 2330 |  | 6201 | 935 |  | 6055 | 910 | -3558 | -3558 | 0 | Critical Branch | Validation phase | NA | 171 | 3558 |  |  | 196 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0030 |  | 6910 | 1072 |  | 6055 | 937 | -3443 | -3443 | 0 | Critical Branch | Validation phase | NA | 990 | 3443 |  |  | 220 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0130 |  | 6910 | 1072 |  | 6055 | 937 | -3443 | -3443 | 0 | Critical Branch | Validation phase | NA | 990 | 3443 |  |  | 220 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0230 |  | 6910 | 1072 |  | 6055 | 937 | -3443 | -3443 | 0 | Critical Branch | Validation phase | NA | 990 | 3443 |  |  | 220 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0330 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | NA | 1127 | 2278 |  |  | 224 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0430 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | NA | 1127 | 2278 |  |  | 224 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0530 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | NA | 1127 | 2278 |  |  | 224 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0630 |  | 7025 | 1117 |  | 6055 | 960 | -2278 | -2278 | 0 | Critical Branch | Validation phase | NA | 1127 | 2278 |  |  | 224 | Reduction because NTC over thermal limit on border | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0730 |  | 6545 | 852 |  | 6047 | 794 | -4066 | -4066 | 0 | Critical Branch | Validation phase | NA | 556 | 4066 |  |  | 194 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0830 |  | 6545 | 852 |  | 6047 | 794 | -4066 | -4066 | 0 | Critical Branch | Validation phase | NA | 556 | 4066 |  |  | 192 | Reduction because NTC over thermal limit on border | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 0930 | 5480 |  |  | 5480 |  |  | -2326 | -2326 | -2326 | TTC Selection - LTTC | Validation phase | 0 | NA | 0 |  |  | 296 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1030 | 5480 |  |  | 5480 |  |  | -2326 | -2326 | -2326 | TTC Selection - LTTC | Validation phase | 0 | NA | 0 |  |  | 296 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1130 | 5480 |  |  | 5480 |  |  | -2326 | -2326 | -2326 | TTC Selection - LTTC | Validation phase | 0 | NA | 0 |  |  | 296 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1230 | 6312 |  |  | 6141 |  |  | -369 | -369 | -198 | Critical Branch | Validation phase | 171 | NA | 0 |  |  | 345 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1330 | 6312 |  |  | 6141 |  |  | -369 | -369 | -198 | Critical Branch | Validation phase | 171 | NA | 0 |  |  | 345 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1430 | 6312 |  |  | 6141 |  |  | -369 | -369 | -198 | Critical Branch | Validation phase | 171 | NA | 0 |  |  | 345 |  | 5891 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1530 |  | 6221 | 631 |  | 6104 | 620 | -1843 | -1843 | 0 | Critical Branch | Validation phase | NA | 128 | 1843 |  |  | 369 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1630 |  | 6221 | 631 |  | 6104 | 620 | -1843 | -1843 | 0 | Critical Branch | Validation phase | NA | 128 | 1843 |  |  | 369 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1730 |  | 6221 | 631 |  | 6104 | 620 | -1843 | -1843 | 0 | Critical Branch | Validation phase | NA | 128 | 1843 |  |  | 369 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1830 |  | 5441 | 667 |  | 5441 | 666 | -3463 | -3463 | 0 | Critical Branch | Validation phase | NA | 1 | 3463 |  |  | 338 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 1930 |  | 5441 | 667 |  | 5441 | 666 | -3463 | -3463 | 0 | Critical Branch | Validation phase | NA | 1 | 3463 |  |  | 338 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 2030 |  | 5441 | 667 |  | 5441 | 666 | -3463 | -3463 | 0 | Critical Branch | Validation phase | NA | 1 | 3463 |  |  | 338 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250819 | August | 2130 |  | 6066 | 744 |  | 6042 | 743 | -3398 | -3398 | 0 | Critical Branch | Validation phase | NA | 25 | 3398 |  |  | 243 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 2230 |  | 6066 | 744 |  | 6042 | 743 | -3398 | -3398 | 0 | Critical Branch | Validation phase | NA | 25 | 3398 |  |  | 243 |  | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250819 | August | 2330 |  | 5516 | 789 |  | 5516 | 789 | -2785 | -2785 | 0 | Critical Branch | Validation phase | NA | 0 | 2785 |  |  | 227 |  | 6800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250820 | August | 0030 | 6695 |  |  | 6267 |  |  | -2276 | -2276 | -1848 | Critical Branch | Validation phase | 428 | NA | 0 |  |  | 392 |  | 6017 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0130 | 6695 |  |  | 6267 |  |  | -2276 | -2276 | -1848 | Critical Branch | Validation phase | 428 | NA | 0 |  |  | 392 |  | 6017 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0230 | 6695 |  |  | 6267 |  |  | -2276 | -2276 | -1848 | Critical Branch | Validation phase | 428 | NA | 0 |  |  | 392 |  | 6017 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0330 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | NA | 210 | 2788 |  |  | 415 | Reduction because NTC over thermal limit on border | 6661 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0430 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | NA | 210 | 2788 |  |  | 415 | Reduction because NTC over thermal limit on border | 6661 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0530 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | NA | 210 | 2788 |  |  | 415 | Reduction because NTC over thermal limit on border | 6661 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0630 |  | 6632 | 744 |  | 6442 | 724 | -2788 | -2788 | 0 | Critical Branch | Validation phase | NA | 210 | 2788 |  |  | 415 | Reduction because NTC over thermal limit on border | 6661 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 0730 | 6735 |  |  | 6314 |  |  | -2984 | -2984 | -2563 | Critical Branch | Validation phase | 421 | NA | 0 |  |  | 370 |  | 6064 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0830 | 6735 |  |  | 6314 |  |  | -2984 | -2984 | -2563 | Critical Branch | Validation phase | 421 | NA | 0 |  |  | 370 |  | 6064 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250820 | August | 0930 | 5480 |  |  | 5250 |  |  | -5112 | -5112 | -4882 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 | [7 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1030 | 5480 |  |  | 5250 |  |  | -5112 | -5112 | -4882 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 | [7 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1130 | 5480 |  |  | 5250 |  |  | -5112 | -5112 | -4882 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 | [7 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1230 | 5480 |  |  | 5250 |  |  | -5207 | -5207 | -4977 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 | [7 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1330 | 5480 |  |  | 5250 |  |  | -5207 | -5207 | -4977 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 | [7 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1430 | 5480 |  |  | 5250 |  |  | -5207 | -5207 | -4977 | TTC Selection - LTTC | Validation phase | 230 | NA | 0 |  |  | 296 | [7 empty] | 5000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250820 | August | 1530 | 7355 |  |  | 6750 |  |  | -1555 | -1555 | -950 | Critical Branch | Validation phase | 605 | NA | 0 |  |  | 385 |  | 6537 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1630 | 7355 |  |  | 6787 |  |  | -1555 | -1555 | -987 | Critical Branch | Validation phase | 568 | NA | 0 |  |  | 407 |  | 6537 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1730 | 7355 |  |  | 6787 |  |  | -1555 | -1555 | -987 | Critical Branch | Validation phase | 568 | NA | 0 |  |  | 407 |  | 6537 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1830 |  | 6848 | 649 |  | 6545 | 628 | -2181 | -2181 | 0 | Critical Branch | Validation phase | NA | 324 | 2181 |  |  | 410 |  | 6883 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 1930 |  | 6848 | 649 |  | 6545 | 628 | -2181 | -2181 | 0 | Critical Branch | Validation phase | NA | 324 | 2181 |  |  | 410 |  | 6883 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2030 |  | 6848 | 649 |  | 6545 | 628 | -2181 | -2181 | 0 | Critical Branch | Validation phase | NA | 324 | 2181 |  |  | 410 |  | 6883 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2130 |  | 6553 | 614 |  | 6384 | 598 | -1908 | -1908 | 0 | Critical Branch | Validation phase | NA | 185 | 1908 |  |  | 391 |  | 6655 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2230 |  | 6553 | 614 |  | 6384 | 598 | -1908 | -1908 | 0 | Critical Branch | Validation phase | NA | 185 | 1908 |  |  | 391 |  | 6655 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2200 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1
20250820 | August | 2330 |  | 5993 | 639 |  | 5823 | 623 | -1285 | -1285 | 0 | Critical Branch | Validation phase | NA | 186 | 1285 |  |  | 379 |  | 6054 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250821 | August | 0030 | 6624 |  |  | 5773 |  |  | -2108 | -2108 | -1257 | Critical Branch | Validation phase | 851 | NA | 0 |  |  |  |  | 5523 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 0130 | 6624 |  |  | 5773 |  |  | -2108 | -2108 | -1257 | Critical Branch | Validation phase | 851 | NA | 0 |  |  |  |  | 5523 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 0230 | 6624 |  |  | 5773 |  |  | -2108 | -2108 | -1257 | Critical Branch | Validation phase | 851 | NA | 0 |  |  |  |  | 5523 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 0330 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 238 | NA | 0 |  |  |  |  | 6534 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0430 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 238 | NA | 0 |  |  |  |  | 6534 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0530 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 238 | NA | 0 |  |  |  |  | 6534 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0630 | 7022 |  |  | 6784 |  |  | -1548 | -1548 | -1310 | Critical Branch | Validation phase | 238 | NA | 0 |  |  |  |  | 6534 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250821 | August | 0730 | 5685 |  |  | 5493 |  |  | -1452 | -1452 | -1260 | Critical Branch | Validation phase | 192 | NA | 0 |  |  |  |  | 5243 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 0830 | 5685 |  |  | 4750 |  |  | -1452 | -1452 | -517 | Critical Branch | Validation phase | 935 | NA | 0 |  |  |  |  | 5243 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 0930 | 5708 |  |  | 4750 |  |  | -1719 | -1719 | -761 | Critical Branch | Validation phase | 958 | NA | 0 |  |  |  |  | 4859 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1030 | 5708 |  |  | 4750 |  |  | -1719 | -1719 | -761 | Critical Branch | Validation phase | 958 | NA | 0 |  |  |  |  | 4859 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1130 | 5708 |  |  | 4750 |  |  | -1719 | -1719 | -761 | Critical Branch | Validation phase | 958 | NA | 0 |  |  |  |  | 4859 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1230 | 6277 |  |  | 4750 |  |  | -1119 | -1119 | 408 | Critical Branch | Validation phase | 1527 | NA | 1935 |  |  |  |  | 5479 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1330 | 6277 |  |  | 4750 |  |  | -1119 | -1119 | 408 | Critical Branch | Validation phase | 1527 | NA | 1935 |  |  |  |  | 5479 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1430 | 6277 |  |  | 4750 |  |  | -1119 | -1119 | 408 | Critical Branch | Validation phase | 1527 | NA | 1935 |  |  |  |  | 5479 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250821 | August | 1530 | 5673 |  |  | 4937 |  |  | -1328 | -1328 | -592 | Critical Branch | Validation phase | 736 | NA | 0 |  |  |  |  | 4687 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 1630 | 5673 |  |  | 4937 |  |  | -1328 | -1328 | -592 | Critical Branch | Validation phase | 736 | NA | 0 |  |  |  |  | 4687 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 1730 | 5673 |  |  | 4937 |  |  | -1328 | -1328 | -592 | Critical Branch | Validation phase | 736 | NA | 0 |  |  |  |  | 4687 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250821 | August | 1830 |  | 5741 | 538 |  | 5590 | 524 | -2833 | -2833 | 0 | Critical Branch | Validation phase | NA | 165 | 2833 |  |  |  |  | 5791 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 1930 |  | 5741 | 538 |  | 5590 | 524 | -2833 | -2833 | 0 | Critical Branch | Validation phase | NA | 165 | 2833 |  |  |  |  | 5791 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250821 | August | 2030 |  | 5741 | 538 |  | 5590 | 524 | -2833 | -2833 | 0 | Critical Branch | Validation phase | NA | 165 | 2833 |  |  |  |  | 5791 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ
20250822 | August | 0730 | 5480 |  |  | 5288 |  |  | -2127 | -2127 | -1935 | TTC Selection - LTTC | Validation phase | 192 | NA | 0 |  |  |  |  | 5038 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20250822 | August | 0830 | 5480 |  |  | 4750 |  |  | -2127 | -2127 | -1397 | TTC Selection - LTTC | Validation phase | 730 | NA | 0 |  |  |  |  | 5038 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 0930 | 5480 |  |  | 4750 |  |  | -2402 | -2402 | -1672 | TTC Selection - LTTC | Validation phase | 730 | NA | 0 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1030 | 5480 |  |  | 4750 |  |  | -2402 | -2402 | -1672 | TTC Selection - LTTC | Validation phase | 730 | NA | 0 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1130 | 5480 |  |  | 4750 |  |  | -2402 | -2402 | -1672 | TTC Selection - LTTC | Validation phase | 730 | NA | 0 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1230 | 6725 |  |  | 4750 |  |  | -832 | -832 | 1143 | Critical Branch | Validation phase | 1975 | NA | 3118 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1330 | 6725 |  |  | 4750 |  |  | -832 | -832 | 1143 | Critical Branch | Validation phase | 1975 | NA | 3118 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1430 | 6725 |  |  | 4750 |  |  | -832 | -832 | 1143 | Critical Branch | Validation phase | 1975 | NA | 3118 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250822 | August | 1530 |  | 6081 | 701 |  | 5998 | 701 | -852 | -852 | 0 | Critical Branch | Smoothing ramp | NA | 83 | 852 | Smoothing | Smoothing ramp
20250822 | August | 2130 | 7478 |  |  | 6645 |  |  | -3358 | -3358 | -2525 | Critical Branch | Validation phase | 833 | NA | 0 |  |  |  |  | 6395 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250822 | August | 2230 | 7478 |  |  | 6645 |  |  | -3358 | -3358 | -2525 | Critical Branch | Validation phase | 833 | NA | 0 |  |  |  |  | 6395 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250822 | August | 2330 | 6878 |  |  | 6045 |  |  | -2751 | -2751 | -1918 | Critical Branch | Validation phase | 833 | NA | 0 |  |  |  |  | 5795 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS
20250823 | August | 0030 | 8919 |  |  | 7304 |  |  | -4484 | -4484 | -2875 | Critical Branch | Validation phase | 1615 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7071 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0130 | 8919 |  |  | 7304 |  |  | -4484 | -4484 | -2875 | Critical Branch | Validation phase | 1615 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7071 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0230 | 8919 |  |  | 7304 |  |  | -4484 | -4484 | -2875 | Critical Branch | Validation phase | 1615 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7071 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0330 | 8576 |  |  | 6938 |  |  | -4672 | -4672 | -3034 | Critical Branch | Validation phase | 1638 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6688 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0430 | 8576 |  |  | 6938 |  |  | -4672 | -4672 | -3034 | Critical Branch | Validation phase | 1638 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6688 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0530 | 8576 |  |  | 6938 |  |  | -4672 | -4672 | -3034 | Critical Branch | Validation phase | 1638 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6688 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0630 | 7476 |  |  | 5838 |  |  | -3533 | -3533 | -1895 | Critical Branch | Validation phase | 1638 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 5588 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250823 | August | 0730 | 6920 |  |  | 6303 |  |  | -3002 | -3002 | -2385 | Critical Branch | Validation phase | 617 | NA | 0 |  |  | 366 |  | 6053 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 0830 | 6920 |  |  | 6303 |  |  | -3002 | -3002 | -2385 | Critical Branch | Validation phase | 617 | NA | 0 |  |  | 366 |  | 6053 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 0930 | 6808 |  |  | 6069 |  |  | -3181 | -3181 | -2442 | Critical Branch | Validation phase | 739 | NA | 0 |  |  | 359 |  | 5819 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1030 | 6808 |  |  | 6069 |  |  | -3181 | -3181 | -2442 | Critical Branch | Validation phase | 739 | NA | 0 |  |  | 359 |  | 5819 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1130 | 6808 |  |  | 6069 |  |  | -3181 | -3181 | -2442 | Critical Branch | Validation phase | 739 | NA | 0 |  |  | 359 |  | 5819 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1230 | 6568 |  |  | 5924 |  |  | -1021 | -1021 | -377 | Critical Branch | Validation phase | 644 | NA | 0 |  |  | 346 |  | 5674 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1330 | 6568 |  |  | 5924 |  |  | -1021 | -1021 | -377 | Critical Branch | Validation phase | 644 | NA | 0 |  |  | 346 |  | 5674 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1430 | 6568 |  |  | 5924 |  |  | -1021 | -1021 | -377 | Critical Branch | Validation phase | 644 | NA | 0 |  |  | 346 |  | 5674 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1530 | 7677 |  |  | 6436 |  |  | -3344 | -3344 | -2103 | Critical Branch | Validation phase | 1241 | NA | 0 |  |  | 409 |  | 6186 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1630 | 7677 |  |  | 6436 |  |  | -3344 | -3344 | -2103 | Critical Branch | Validation phase | 1241 | NA | 0 |  |  | 409 |  | 6186 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1730 | 8577 |  |  | 7336 |  |  | -4328 | -4328 | -3087 | Critical Branch | Validation phase | 1241 | NA | 0 |  |  | 411 |  | 7086 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA
20250823 | August | 1830 | 8562 |  |  | 8561 |  |  | -4536 | -4536 | -4536 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 400
20250823 | August | 1930 | 8562 |  |  | 8561 |  |  | -4536 | -4536 | -4536 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 400
20250823 | August | 2030 | 8562 |  |  | 8561 |  |  | -4536 | -4536 | -4536 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 400
20250823 | August | 2130 | 9009 |  |  | 8882 |  |  | -4949 | -4949 | -4822 | Critical Branch | Validation phase | 127 | NA | 0 |  |  | 422 |  | 8632 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250823 | August | 2230 | 9009 |  |  | 8882 |  |  | -4949 | -4949 | -4822 | Critical Branch | Validation phase | 127 | NA | 0 |  |  | 422 |  | 8632 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250823 | August | 2330 | 8409 |  |  | 8282 |  |  | -4342 | -4342 | -4215 | Critical Branch | Validation phase | 127 | NA | 0 |  |  | 412 |  | 8032 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 0030 | 9262 |  |  | 8676 |  |  | -5051 | -5051 | -4469 | Critical Branch | Validation phase | 586 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8438 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0130 | 9262 |  |  | 8676 |  |  | -5051 | -5051 | -4469 | Critical Branch | Validation phase | 586 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8438 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0230 | 9262 |  |  | 8676 |  |  | -5051 | -5051 | -4469 | Critical Branch | Validation phase | 586 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8438 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0330 | 9159 |  |  | 8589 |  |  | -4980 | -4980 | -4413 | Critical Branch | Validation phase | 570 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8347 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0430 | 9159 |  |  | 8589 |  |  | -4980 | -4980 | -4413 | Critical Branch | Validation phase | 570 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8347 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0530 | 9159 |  |  | 8589 |  |  | -4980 | -4980 | -4413 | Critical Branch | Validation phase | 570 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8347 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0630 | 8959 |  |  | 8389 |  |  | -4764 | -4764 | -4197 | Critical Branch | Validation phase | 570 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8147 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 0730 | 8117 |  |  | 7991 |  |  | -4154 | -4154 | -4028 | Critical Branch | Validation phase | 126 | NA | 0 |  |  | 407 |  | 7741 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 0830 | 8117 |  |  | 7991 |  |  | -4154 | -4154 | -4028 | Critical Branch | Validation phase | 126 | NA | 0 |  |  | 407 |  | 7741 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 0930 | 7688 |  |  | 7640 |  |  | -3833 | -3833 | -3785 | Critical Branch | Validation phase | 48 | NA | 0 |  |  | 384 |  | 7390 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1030 | 7688 |  |  | 7640 |  |  | -3833 | -3833 | -3785 | Critical Branch | Validation phase | 48 | NA | 0 |  |  | 384 |  | 7390 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1130 | 7688 |  |  | 7640 |  |  | -3833 | -3833 | -3785 | Critical Branch | Validation phase | 48 | NA | 0 |  |  | 384 |  | 7390 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1230 | 6808 |  |  | 6547 |  |  | -3150 | -3150 | -2889 | Critical Branch | Validation phase | 261 | NA | 0 |  |  | 337 |  | 6297 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1330 | 6808 |  |  | 6547 |  |  | -3150 | -3150 | -2889 | Critical Branch | Validation phase | 261 | NA | 0 |  |  | 337 |  | 6297 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1430 | 6808 |  |  | 6547 |  |  | -3150 | -3150 | -2889 | Critical Branch | Validation phase | 261 | NA | 0 |  |  | 337 |  | 6297 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1530 | 7805 |  |  | 7522 |  |  | -3727 | -3727 | -3444 | Critical Branch | Validation phase | 283 | NA | 0 |  |  | 391 |  | 7272 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1630 | 7805 |  |  | 7522 |  |  | -3727 | -3727 | -3444 | Critical Branch | Validation phase | 283 | NA | 0 |  |  | 391 |  | 7272 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1730 | 7805 |  |  | 7522 |  |  | -3727 | -3727 | -3444 | Critical Branch | Validation phase | 283 | NA | 0 |  |  | 391 |  | 7272 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250824 | August | 1830 | 7710 |  |  | 7662 |  |  | -4751 | -4751 | -4703 | Critical Branch | Validation phase | 48 | NA | 0 |  |  | 376 |  | 7412 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 1930 | 7710 |  |  | 7662 |  |  | -4751 | -4751 | -4703 | Critical Branch | Validation phase | 48 | NA | 0 |  |  | 376 |  | 7412 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2030 | 7710 |  |  | 7662 |  |  | -4751 | -4751 | -4703 | Critical Branch | Validation phase | 48 | NA | 0 |  |  | 376 |  | 7412 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2130 | 7996 |  |  | 7943 |  |  | -4606 | -4606 | -4553 | Critical Branch | Validation phase | 53 | NA | 0 |  |  | 391 |  | 7693 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2230 | 7996 |  |  | 7943 |  |  | -4606 | -4606 | -4553 | Critical Branch | Validation phase | 53 | NA | 0 |  |  | 391 |  | 7693 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250824 | August | 2330 | 7996 |  |  | 7943 |  |  | -4606 | -4606 | -4553 | Critical Branch | Validation phase | 53 | NA | 0 |  |  | 391 |  | 7693 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250825 | August | 0030 | 8711 |  |  | 7857 |  |  | -4060 | -4060 | -3206 | Critical Branch | Validation phase | 854 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7607 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250825 | August | 0130 | 8711 |  |  | 7857 |  |  | -4060 | -4060 | -3206 | Critical Branch | Validation phase | 854 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7607 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250825 | August | 0230 | 8711 |  |  | 7857 |  |  | -4060 | -4060 | -3206 | Critical Branch | Validation phase | 854 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7607 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250825 | August | 0330 | 8256 |  |  | 7540 |  |  | -2102 | -2102 | -1386 | Critical Branch | Validation phase | 716 | NA | 0 |  |  | 404 |  | 7290 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0430 | 8256 |  |  | 7540 |  |  | -2102 | -2102 | -1386 | Critical Branch | Validation phase | 716 | NA | 0 |  |  | 404 |  | 7290 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0530 | 8256 |  |  | 7540 |  |  | -2102 | -2102 | -1386 | Critical Branch | Validation phase | 716 | NA | 0 |  |  | 404 |  | 7290 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0630 | 8056 |  |  | 6250 |  |  | -1875 | -1875 | -69 | Critical Branch | Validation phase | 1806 | NA | 0 |  |  | 404 |  | 7090 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 0730 | 7367 |  |  | 4750 |  |  | -2987 | -2987 | -370 | Critical Branch | Validation phase | 2617 | NA | 0 |  |  | 176 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 0830 | 6967 |  |  | 4750 |  |  | -2545 | -2545 | -328 | Critical Branch | Validation phase | 2217 | NA | 0 |  |  | 174 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 0930 | 6065 |  |  | 4750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 1315 | NA | 0 |  |  | 151 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1030 | 6065 |  |  | 4750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 1315 | NA | 0 |  |  | 151 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1130 | 6065 |  |  | 4750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 1315 | NA | 0 |  |  | 151 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1230 | 6427 |  |  | 4750 |  |  | 2363 | 362 | 3678 | Minimum Margin | Validation phase | 1677 | NA | 6994 |  |  | 160 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1330 | 6435 |  |  | 4750 |  |  | 2363 | 370 | 3678 | Minimum Margin | Validation phase | 1685 | NA | 6986 |  |  | 161 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1430 | 6382 |  |  | 4750 |  |  | 2363 | 317 | 3678 | Minimum Margin | Validation phase | 1632 | NA | 7039 |  |  | 159 | [7 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250825 | August | 1530 | 8211 |  |  | 6250 |  |  | -3275 | -3275 | -1314 | Critical Branch | Smoothing ramp | 1961 | NA | 0 | Smoothing | Smoothing ramp | 200 |  | 7522 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 1630 | 8211 |  |  | 7750 |  |  | -3275 | -3275 | -2814 | Critical Branch | Smoothing ramp | 461 | NA | 0 | Smoothing | Smoothing ramp | 209 |  | 7522 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 1730 | 8361 |  |  | 7714 |  |  | -3433 | -3433 | -2788 | Critical Branch | Validation phase | 647 | NA | 0 |  |  | 192 |  | 7672 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250825 | August | 1830 |  | 5851 | 493 |  | 5850 | 493 | -3676 | -3676 | 0 | Critical Branch | Critical Branch | NA | 1 | 3676 |  |  | 153
20250825 | August | 1930 |  | 5851 | 493 |  | 5850 | 493 | -3676 | -3676 | 0 | Critical Branch | Critical Branch | NA | 1 | 3676 |  |  | 153
20250825 | August | 2030 |  | 5851 | 493 |  | 5850 | 493 | -3676 | -3676 | 0 | Critical Branch | Critical Branch | NA | 1 | 3676 |  |  | 153
20250825 | August | 2130 | 6868 |  |  | 6679 |  |  | -3547 | -3547 | -3358 | Critical Branch | Validation phase | 189 | NA | 0 |  |  | 169 |  | 6429 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250825 | August | 2230 | 6868 |  |  | 6679 |  |  | -3547 | -3547 | -3358 | Critical Branch | Validation phase | 189 | NA | 0 |  |  | 169 |  | 6429 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250825 | August | 2330 | 6278 |  |  | 6089 |  |  | -2947 | -2947 | -2758 | Critical Branch | Validation phase | 189 | NA | 0 |  |  | 166 |  | 5839 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0030 | 7216 |  |  | 6868 |  |  | -2517 | -2517 | -2169 | Critical Branch | Validation phase | 348 | NA | 0 |  |  |  |  | 6618 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0130 | 7216 |  |  | 6868 |  |  | -2517 | -2517 | -2169 | Critical Branch | Validation phase | 348 | NA | 0 |  |  |  |  | 6618 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0230 | 7216 |  |  | 6868 |  |  | -2517 | -2517 | -2169 | Critical Branch | Validation phase | 348 | NA | 0 |  |  |  |  | 6618 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0330 | 7298 |  |  | 6970 |  |  | -2233 | -2233 | -1905 | Critical Branch | Validation phase | 328 | NA | 0 |  |  |  |  | 6720 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0430 | 7298 |  |  | 6970 |  |  | -2233 | -2233 | -1905 | Critical Branch | Validation phase | 328 | NA | 0 |  |  |  |  | 6720 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0530 | 7298 |  |  | 6970 |  |  | -2233 | -2233 | -1905 | Critical Branch | Validation phase | 328 | NA | 0 |  |  |  |  | 6720 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0630 | 7098 |  |  | 6250 |  |  | -2018 | -2018 | -1170 | Critical Branch | Smoothing ramp | 848 | NA | 0 | Smoothing | Smoothing ramp |  |  | 6520 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 0730 |  | 5900 | 52 |  | 4661 | 49 | -3133 | -3133 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 1242 | 3133 |  |  |  |  | 5485 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 0830 |  | 5900 | 52 |  | 4661 | 49 | -3133 | -3133 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 1242 | 3133 |  |  |  |  | 5485 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 0930 | 6065 |  |  | 3750 |  |  | -5589 | -5589 | -3274 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 | [10 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1030 | 6065 |  |  | 3750 |  |  | -5589 | -5589 | -3274 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 | [10 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1130 | 6065 |  |  | 3750 |  |  | -5589 | -5589 | -3274 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 | [10 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1230 | 6065 |  |  | 4750 |  |  | -2942 | -2942 | -1627 | TTC Selection - LTTC | Validation phase | 1315 | NA | 0 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1330 | 6065 |  |  | 4750 |  |  | -2942 | -2942 | -1627 | TTC Selection - LTTC | Validation phase | 1315 | NA | 0 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1430 | 6065 |  |  | 4750 |  |  | -2942 | -2942 | -1627 | TTC Selection - LTTC | Validation phase | 1315 | NA | 0 | [10 empty] | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250826 | August | 1530 | 7738 |  |  | 6250 |  |  | -2794 | -2794 | -1306 | Critical Branch | Smoothing ramp | 1488 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 1630 | 7738 |  |  | 7511 |  |  | -2794 | -2794 | -2567 | Critical Branch | Validation phase | 227 | NA | 0 |  |  |  |  | 7261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 1730 | 7888 |  |  | 7661 |  |  | -2957 | -2957 | -2730 | Critical Branch | Validation phase | 227 | NA | 0 |  |  |  |  | 7411 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 2130 | 6864 |  |  | 6553 |  |  | -3246 | -3246 | -2935 | Critical Branch | Validation phase | 311 | NA | 0 |  |  |  |  | 6303 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 2230 | 6864 |  |  | 6553 |  |  | -3246 | -3246 | -2935 | Critical Branch | Validation phase | 311 | NA | 0 |  |  |  |  | 6303 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250826 | August | 2330 | 6274 |  |  | 5963 |  |  | -2645 | -2645 | -2334 | Critical Branch | Validation phase | 311 | NA | 0 |  |  |  |  | 5713 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0030 | 7773 |  |  | 7674 |  |  | -2897 | -2897 | -2798 | Critical Branch | Validation phase | 99 | NA | 0 |  |  |  |  | 7424 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0130 | 7773 |  |  | 7674 |  |  | -2897 | -2897 | -2798 | Critical Branch | Validation phase | 99 | NA | 0 |  |  |  |  | 7424 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0230 | 7773 |  |  | 7674 |  |  | -2897 | -2897 | -2798 | Critical Branch | Validation phase | 99 | NA | 0 |  |  |  |  | 7424 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0330 | 7788 |  |  | 7662 |  |  | -2786 | -2786 | -2660 | Critical Branch | Validation phase | 126 | NA | 0 |  |  |  |  | 7412 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0430 | 7788 |  |  | 7662 |  |  | -2786 | -2786 | -2660 | Critical Branch | Validation phase | 126 | NA | 0 |  |  |  |  | 7412 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0530 | 7788 |  |  | 7662 |  |  | -2786 | -2786 | -2660 | Critical Branch | Validation phase | 126 | NA | 0 |  |  |  |  | 7412 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0630 | 7588 |  |  | 6250 |  |  | -2573 | -2573 | -1235 | Critical Branch | Smoothing ramp | 1338 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7212 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 0730 | 6753 |  |  | 4750 |  |  | -4415 | -4415 | -2412 | Critical Branch | Validation phase | 2003 | NA | 0 |  |  |  |  | 6262 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 0830 | 6753 |  |  | 4750 |  |  | -4415 | -4415 | -2412 | Critical Branch | Validation phase | 2003 | NA | 0 |  |  |  |  | 6262 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 0930 | 6065 |  |  | 3750 |  |  | -5309 | -5309 | -2994 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 | [10 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1030 | 6065 |  |  | 3750 |  |  | -5309 | -5309 | -2994 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 | [10 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1130 | 6065 |  |  | 3750 |  |  | -5309 | -5309 | -2994 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 | [10 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1230 | 6145 |  |  | 4091 |  |  | 3165 | 80 | 5139 | Minimum Margin | Validation phase | 2054 | NA | 10198 | [10 empty] | 3841 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1330 | 6145 |  |  | 4091 |  |  | 3165 | 80 | 5139 | Minimum Margin | Validation phase | 2054 | NA | 10198 | [10 empty] | 3841 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1430 | 6145 |  |  | 4091 |  |  | 3165 | 80 | 5139 | Minimum Margin | Validation phase | 2054 | NA | 10198 | [10 empty] | 3841 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250827 | August | 1530 | 7812 |  |  | 5591 |  |  | -3406 | -3406 | -1185 | Critical Branch | Smoothing ramp | 2221 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7518 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1630 | 7812 |  |  | 7091 |  |  | -3406 | -3406 | -2685 | Critical Branch | Smoothing ramp | 721 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7518 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1730 | 7962 |  |  | 7914 |  |  | -3561 | -3561 | -3513 | Critical Branch | Smoothing ramp | 48 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7668 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1830 |  | 6016 | 581 |  | 5963 | 576 | -4174 | -4174 | 0 | Critical Branch | Validation phase | NA | 58 | 4174 |  |  |  |  | 6217 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 1930 |  | 6016 | 581 |  | 5963 | 576 | -4174 | -4174 | 0 | Critical Branch | Validation phase | NA | 58 | 4174 |  |  |  |  | 6217 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2030 |  | 6016 | 581 |  | 5963 | 576 | -4174 | -4174 | 0 | Critical Branch | Validation phase | NA | 58 | 4174 |  |  |  |  | 6217 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2130 | 7488 |  |  | 7194 |  |  | -4963 | -4963 | -4669 | Critical Branch | Validation phase | 294 | NA | 0 |  |  |  |  | 6944 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2230 | 7488 |  |  | 7194 |  |  | -4963 | -4963 | -4669 | Critical Branch | Validation phase | 294 | NA | 0 |  |  |  |  | 6944 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250827 | August | 2330 | 6898 |  |  | 6604 |  |  | -4368 | -4368 | -4074 | Critical Branch | Validation phase | 294 | NA | 0 |  |  |  |  | 6354 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0030 | 8037 |  |  | 7632 |  |  | -4482 | -4482 | -4077 | Critical Branch | Validation phase | 405 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7382 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250828 | August | 0130 | 8037 |  |  | 7632 |  |  | -4482 | -4482 | -4077 | Critical Branch | Validation phase | 405 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7382 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250828 | August | 0230 | 8037 |  |  | 7632 |  |  | -4482 | -4482 | -4077 | Critical Branch | Validation phase | 405 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7382 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250828 | August | 0330 | 7835 |  |  | 7497 |  |  | -2737 | -2737 | -2399 | Critical Branch | Validation phase | 338 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7247 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0430 | 7835 |  |  | 7497 |  |  | -2737 | -2737 | -2399 | Critical Branch | Validation phase | 338 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7247 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0530 | 7835 |  |  | 7497 |  |  | -2737 | -2737 | -2399 | Critical Branch | Validation phase | 338 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7247 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0630 | 7635 |  |  | 6250 |  |  | -2511 | -2511 | -1126 | Critical Branch | Smoothing ramp | 1385 | NA | 0 | Smoothing | Smoothing ramp | 210 | Reduction because NTC over thermal limit on border | 7047 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 0730 | 6707 |  |  | 4750 |  |  | -4678 | -4678 | -2721 | Critical Branch | Validation phase | 1957 | NA | 0 |  |  | 168 |  | 6201 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 0830 | 6707 |  |  | 4750 |  |  | -4678 | -4678 | -2721 | Critical Branch | Validation phase | 1957 | NA | 0 |  |  | 168 |  | 6201 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE |  |  |  |  | 4500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 0930 | 6065 |  |  | 3750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 |  |  | 151 | [7 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1030 | 6065 |  |  | 3750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 |  |  | 151 | [7 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1130 | 6065 |  |  | 3750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 2315 | NA | 0 |  |  | 151 | [7 empty] | 3500 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1230 | 6065 |  |  | 4051 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 2014 | NA | 0 |  |  | 151 | [7 empty] | 3801 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1330 | 6065 |  |  | 4051 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 2014 | NA | 0 |  |  | 151 | [7 empty] | 3801 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1430 | 6065 |  |  | 4051 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 2014 | NA | 0 |  |  | 151 | [7 empty] | 3801 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250828 | August | 1530 | 7472 |  |  | 5551 |  |  | -2589 | -2589 | -668 | Critical Branch | Smoothing ramp | 1921 | NA | 0 | Smoothing | Smoothing ramp | 189 |  | 6982 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1630 | 7472 |  |  | 7051 |  |  | -2589 | -2589 | -2168 | Critical Branch | Smoothing ramp | 421 | NA | 0 | Smoothing | Smoothing ramp | 189 |  | 6982 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1730 | 7837 |  |  | 7597 |  |  | -2924 | -2924 | -2684 | Critical Branch | Validation phase | 240 | NA | 0 |  |  | 384 |  | 7347 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1830 |  | 6632 | 733 |  | 6580 | 727 | -5553 | -5553 | 0 | Critical Branch | Validation phase | NA | 58 | 5553 |  |  | 172 |  | 6831 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 1930 |  | 6632 | 733 |  | 6580 | 727 | -5553 | -5553 | 0 | Critical Branch | Validation phase | NA | 58 | 5553 |  |  | 172 |  | 6831 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2030 |  | 6632 | 733 |  | 6580 | 727 | -5553 | -5553 | 0 | Critical Branch | Validation phase | NA | 58 | 5553 |  |  | 172 |  | 6831 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2130 | 7354 |  |  | 7028 |  |  | -4593 | -4593 | -4267 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 359 |  | 6778 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2230 | 7354 |  |  | 7028 |  |  | -4593 | -4593 | -4267 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 359 |  | 6778 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250828 | August | 2330 | 6754 |  |  | 6428 |  |  | -3985 | -3985 | -3659 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 346 |  | 6178 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0030 | 7790 |  |  | 7372 |  |  | -2463 | -2463 | -2045 | Critical Branch | Validation phase | 418 | NA | 0 |  |  |  |  | 7122 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0130 | 7790 |  |  | 7372 |  |  | -2463 | -2463 | -2045 | Critical Branch | Validation phase | 418 | NA | 0 |  |  |  |  | 7122 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0230 | 7790 |  |  | 7372 |  |  | -2463 | -2463 | -2045 | Critical Branch | Validation phase | 418 | NA | 0 |  |  |  |  | 7122 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0330 | 7687 |  |  | 7258 |  |  | -2256 | -2256 | -1827 | Critical Branch | Validation phase | 429 | NA | 0 |  |  |  |  | 7008 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0430 | 7687 |  |  | 7258 |  |  | -2256 | -2256 | -1827 | Critical Branch | Validation phase | 429 | NA | 0 |  |  |  |  | 7008 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0530 | 7687 |  |  | 7258 |  |  | -2256 | -2256 | -1827 | Critical Branch | Validation phase | 429 | NA | 0 |  |  |  |  | 7008 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0630 | 7687 |  |  | 6288 |  |  | -2256 | -2256 | -857 | Critical Branch | Smoothing ramp | 1399 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7008 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0730 | 5206 |  |  | 4788 |  |  | -2039 | -2039 | -1621 | Critical Branch | Validation phase | 418 | NA | 0 |  |  |  |  | 4538 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0830 | 5206 |  |  | 4788 |  |  | -2039 | -2039 | -1621 | Critical Branch | Validation phase | 418 | NA | 0 |  |  |  |  | 4538 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 0930 | 6071 |  |  | 5558 |  |  | -1426 | -1426 | -913 | Critical Branch | Validation phase | 513 | NA | 0 |  |  |  |  | 5308 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1030 | 6071 |  |  | 5558 |  |  | -1426 | -1426 | -913 | Critical Branch | Validation phase | 513 | NA | 0 |  |  |  |  | 5308 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1130 | 6071 |  |  | 5558 |  |  | -1426 | -1426 | -913 | Critical Branch | Validation phase | 513 | NA | 0 |  |  |  |  | 5308 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1230 | 5735 |  |  | 5398 |  |  | -2852 | -2852 | -2515 | Critical Branch | Validation phase | 337 | NA | 0 |  |  |  |  | 5148 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1330 | 5735 |  |  | 5398 |  |  | -2852 | -2852 | -2515 | Critical Branch | Validation phase | 337 | NA | 0 |  |  |  |  | 5148 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1430 | 5735 |  |  | 5398 |  |  | -2852 | -2852 | -2515 | Critical Branch | Validation phase | 337 | NA | 0 |  |  |  |  | 5148 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1530 | 6787 |  |  | 6317 |  |  | -2266 | -2266 | -1796 | Critical Branch | Validation phase | 470 | NA | 0 |  |  |  |  | 6067 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1630 | 6837 |  |  | 6367 |  |  | -2323 | -2323 | -1853 | Critical Branch | Validation phase | 470 | NA | 0 |  |  |  |  | 6117 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1730 | 8637 |  |  | 7867 |  |  | -4291 | -4291 | -3521 | Critical Branch | Smoothing ramp | 770 | NA | 0 | Smoothing | Smoothing ramp |  |  | 7917 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1830 |  | 6303 | 513 |  | 6178 | 503 | -3766 | -3766 | 0 | Critical Branch | Validation phase | NA | 135 | 3766 |  |  |  |  | 6329 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 1930 |  | 6303 | 513 |  | 6178 | 503 | -3766 | -3766 | 0 | Critical Branch | Validation phase | NA | 135 | 3766 |  |  |  |  | 6329 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2030 |  | 6303 | 513 |  | 6178 | 503 | -3766 | -3766 | 0 | Critical Branch | Validation phase | NA | 135 | 3766 |  |  |  |  | 6329 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2130 | 7340 |  |  | 6998 |  |  | -2869 | -2869 | -2527 | Critical Branch | Validation phase | 342 | NA | 0 |  |  |  |  | 6748 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2230 | 7340 |  |  | 6998 |  |  | -2869 | -2869 | -2527 | Critical Branch | Validation phase | 342 | NA | 0 |  |  |  |  | 6748 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250829 | August | 2330 | 6740 |  |  | 6398 |  |  | -2259 | -2259 | -1917 | Critical Branch | Validation phase | 342 | NA | 0 |  |  |  |  | 6148 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0030 | 7819 |  |  | 7462 |  |  | -2969 | -2969 | -2612 | Critical Branch | Validation phase | 357 | NA | 0 |  |  |  |  | 7212 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0130 | 7819 |  |  | 7462 |  |  | -2969 | -2969 | -2612 | Critical Branch | Validation phase | 357 | NA | 0 |  |  |  |  | 7212 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0230 | 7819 |  |  | 7462 |  |  | -2969 | -2969 | -2612 | Critical Branch | Validation phase | 357 | NA | 0 |  |  |  |  | 7212 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0330 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 371 | NA | 0 |  |  |  |  | 6884 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0430 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 371 | NA | 0 |  |  |  |  | 6884 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0530 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 371 | NA | 0 |  |  |  |  | 6884 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0630 | 7505 |  |  | 7134 |  |  | -2492 | -2492 | -2121 | Critical Branch | Validation phase | 371 | NA | 0 |  |  |  |  | 6884 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0730 | 7062 |  |  | 6666 |  |  | -2504 | -2504 | -2108 | Critical Branch | Validation phase | 396 | NA | 0 |  |  |  |  | 6416 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0830 | 7062 |  |  | 6666 |  |  | -2504 | -2504 | -2108 | Critical Branch | Validation phase | 396 | NA | 0 |  |  |  |  | 6416 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 0930 | 7392 |  |  | 6960 |  |  | -2487 | -2487 | -2055 | Critical Branch | Validation phase | 432 | NA | 0 |  |  |  |  | 6710 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1030 | 7392 |  |  | 6960 |  |  | -2487 | -2487 | -2055 | Critical Branch | Validation phase | 432 | NA | 0 |  |  |  |  | 6710 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1130 | 7392 |  |  | 6960 |  |  | -2487 | -2487 | -2055 | Critical Branch | Validation phase | 432 | NA | 0 |  |  |  |  | 6710 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1230 | 7655 |  |  | 7423 |  |  | -4355 | -4355 | -4123 | Critical Branch | Validation phase | 232 | NA | 0 |  |  |  |  | 7173 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250830 | August | 1330 | 7655 |  |  | 7423 |  |  | -4355 | -4355 | -4123 | Critical Branch | Validation phase | 232 | NA | 0 |  |  |  |  | 7173 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250830 | August | 1430 | 7655 |  |  | 7423 |  |  | -4355 | -4355 | -4123 | Critical Branch | Validation phase | 232 | NA | 0 |  |  |  |  | 7173 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250830 | August | 1530 |  | 7303 | 594 |  | 7171 | 583 | -2696 | -2696 | 0 | Critical Branch | Validation phase | NA | 143 | 2696 |  |  |  |  | 7423 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1630 |  | 7303 | 594 |  | 7171 | 583 | -2696 | -2696 | 0 | Critical Branch | Validation phase | NA | 143 | 2696 |  |  |  |  | 7423 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1730 |  | 7303 | 594 |  | 7171 | 583 | -2696 | -2696 | 0 | Critical Branch | Validation phase | NA | 143 | 2696 |  |  |  |  | 7423 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1830 |  | 6055 | 482 |  | 5946 | 473 | -3782 | -3782 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 118 | 3782 |  |  |  |  | 6121 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 1930 |  | 6055 | 482 |  | 5946 | 473 | -3782 | -3782 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 118 | 3782 |  |  |  |  | 6121 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2030 |  | 6055 | 482 |  | 5946 | 473 | -3782 | -3782 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 118 | 3782 |  |  |  |  | 6121 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2130 | 6577 |  |  | 6313 |  |  | -2686 | -2686 | -2422 | Critical Branch | Validation phase | 264 | NA | 0 |  |  |  |  | 6063 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2230 | 6577 |  |  | 6313 |  |  | -2686 | -2686 | -2422 | Critical Branch | Validation phase | 264 | NA | 0 |  |  |  |  | 6063 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250830 | August | 2330 | 5977 |  |  | 5713 |  |  | -2072 | -2072 | -1808 | Critical Branch | Validation phase | 264 | NA | 0 |  |  |  |  | 5463 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0030 | 7956 |  |  | 7667 |  |  | -2987 | -2987 | -2698 | Critical Branch | Validation phase | 289 | NA | 0 |  |  |  |  | 7417 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0130 | 7956 |  |  | 7667 |  |  | -2987 | -2987 | -2698 | Critical Branch | Validation phase | 289 | NA | 0 |  |  |  |  | 7417 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0230 | 7956 |  |  | 7667 |  |  | -2987 | -2987 | -2698 | Critical Branch | Validation phase | 289 | NA | 0 |  |  |  |  | 7417 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0330 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 115 | NA | 0 |  |  |  |  | 7131 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0430 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 115 | NA | 0 |  |  |  |  | 7131 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0530 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 115 | NA | 0 |  |  |  |  | 7131 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0630 | 7496 |  |  | 7381 |  |  | -2173 | -2173 | -2058 | Critical Branch | Validation phase | 115 | NA | 0 |  |  |  |  | 7131 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 0730 | 7592 |  |  | 7311 |  |  | -2274 | -2274 | -1993 | Critical Branch | Validation phase | 281 | NA | 0 |  |  |  |  | 7061 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0830 | 7592 |  |  | 7311 |  |  | -2274 | -2274 | -1993 | Critical Branch | Validation phase | 281 | NA | 0 |  |  |  |  | 7061 | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250831 | August | 0930 | 7225 |  |  | 6983 |  |  | -3886 | -3886 | -3644 | Critical Branch | Validation phase | 242 | NA | 0 |  |  |  |  | 6733 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250831 | August | 1030 | 7225 |  |  | 6983 |  |  | -3886 | -3886 | -3644 | Critical Branch | Validation phase | 242 | NA | 0 |  |  |  |  | 6733 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250831 | August | 1130 | 7225 |  |  | 6983 |  |  | -3886 | -3886 | -3644 | Critical Branch | Validation phase | 242 | NA | 0 |  |  |  |  | 6733 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250831 | August | 1830 |  | 6118 | 559 |  | 6093 | 557 | -3604 | -3604 | 0 | Critical Branch | Validation phase | NA | 27 | 3604 |  |  |  |  | 6270 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 1930 |  | 6118 | 559 |  | 6093 | 557 | -3604 | -3604 | 0 | Critical Branch | Validation phase | NA | 27 | 3604 |  |  |  |  | 6270 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2030 |  | 6118 | 559 |  | 6093 | 557 | -3604 | -3604 | 0 | Critical Branch | Validation phase | NA | 27 | 3604 |  |  |  |  | 6270 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2130 | 6383 |  |  | 6045 |  |  | -2441 | -2441 | -2103 | Critical Branch | Validation phase | 338 | NA | 0 |  |  |  |  | 5795 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2230 | 6383 |  |  | 6045 |  |  | -2441 | -2441 | -2103 | Critical Branch | Validation phase | 338 | NA | 0 |  |  |  |  | 5795 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250831 | August | 2330 | 6383 |  |  | 6045 |  |  | -2441 | -2441 | -2103 | Critical Branch | Validation phase | 338 | NA | 0 |  |  |  |  | 5795 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0030 | 7991 |  |  | 7590 |  |  | -3206 | -3206 | -2805 | Critical Branch | Validation phase | 401 | NA | 0 |  |  | 411 |  | 7340 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0130 | 7991 |  |  | 7590 |  |  | -3206 | -3206 | -2805 | Critical Branch | Validation phase | 401 | NA | 0 |  |  | 411 |  | 7340 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0230 | 7991 |  |  | 7590 |  |  | -3206 | -3206 | -2805 | Critical Branch | Validation phase | 401 | NA | 0 |  |  | 411 |  | 7340 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0330 | 8090 |  |  | 7864 |  |  | -3147 | -3147 | -2921 | Critical Branch | Validation phase | 226 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7614 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0430 | 8090 |  |  | 7864 |  |  | -3147 | -3147 | -2921 | Critical Branch | Validation phase | 226 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7614 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0530 | 8090 |  |  | 7864 |  |  | -3147 | -3147 | -2921 | Critical Branch | Validation phase | 226 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7614 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0630 | 6890 |  |  | 6565 |  |  | -1914 | -1914 | -1589 | Critical Branch | Validation phase | 325 | NA | 0 |  |  | 410 |  | 6414 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0730 | 5280 |  |  | 5065 |  |  | -2228 | -2228 | -2013 | TTC Selection - LTTC | Validation phase | 215 | NA | 0 |  |  | 292 |  | 4815 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0830 | 5280 |  |  | 5065 |  |  | -2228 | -2228 | -2013 | TTC Selection - LTTC | Validation phase | 215 | NA | 0 |  |  | 292 |  | 4815 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 0930 | 6736 |  |  | 6565 |  |  | -2665 | -2665 | -2494 | Critical Branch | Validation phase | 171 | NA | 0 |  |  | 381 |  | 6380 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 1030 | 6736 |  |  | 6630 |  |  | -2665 | -2665 | -2559 | Critical Branch | Validation phase | 106 | NA | 0 |  |  | 381 |  | 6380 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 1130 | 6736 |  |  | 6630 |  |  | -2665 | -2665 | -2559 | Critical Branch | Validation phase | 106 | NA | 0 |  |  | 381 |  | 6380 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 1230 | 6910 |  |  | 6424 |  |  | -2593 | -2593 | -2107 | Critical Branch | Validation phase | 486 | NA | 0 |  |  | 391 |  | 6174 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250901 | September | 1330 | 6910 |  |  | 6424 |  |  | -2593 | -2593 | -2107 | Critical Branch | Validation phase | 486 | NA | 0 |  |  | 391 |  | 6174 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250901 | September | 1430 | 6910 |  |  | 6424 |  |  | -2593 | -2593 | -2107 | Critical Branch | Validation phase | 486 | NA | 0 |  |  | 391 |  | 6174 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250901 | September | 1530 | 6571 |  |  | 6571 |  |  | -2563 | -2563 | -2563 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 371
20250901 | September | 1630 | 6571 |  |  | 6571 |  |  | -2563 | -2563 | -2563 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 371
20250901 | September | 1730 | 6571 |  |  | 6571 |  |  | -2563 | -2563 | -2563 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 371
20250901 | September | 1830 |  | 4874 | 469 |  | 4874 | 469 | -2914 | -2914 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 0 | 2914 |  |  | 292
20250901 | September | 1930 |  | 4874 | 469 |  | 4874 | 469 | -2914 | -2914 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 0 | 2914 |  |  | 292
20250901 | September | 2030 |  | 4874 | 469 |  | 4874 | 469 | -2914 | -2914 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 0 | 2914 |  |  | 292
20250901 | September | 2130 | 6078 |  |  | 5805 |  |  | -2433 | -2433 | -2160 | Critical Branch | Validation phase | 273 | NA | 0 |  |  | 341 |  | 5555 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 2230 | 6078 |  |  | 5805 |  |  | -2433 | -2433 | -2160 | Critical Branch | Validation phase | 273 | NA | 0 |  |  | 341 |  | 5555 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250901 | September | 2330 | 5478 |  |  | 5205 |  |  | -1827 | -1827 | -1554 | Critical Branch | Validation phase | 273 | NA | 0 |  |  | 325 |  | 4955 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0030 | 6081 |  |  | 5999 |  |  | -1499 | -1499 | -1417 | Critical Branch | Validation phase | 82 | NA | 0 |  |  |  |  | 5749 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0130 | 6081 |  |  | 5999 |  |  | -1499 | -1499 | -1417 | Critical Branch | Validation phase | 82 | NA | 0 |  |  |  |  | 5749 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0230 | 6081 |  |  | 5999 |  |  | -1499 | -1499 | -1417 | Critical Branch | Validation phase | 82 | NA | 0 |  |  |  |  | 5749 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0330 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 79 | NA | 0 |  |  |  |  | 5667 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0430 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 79 | NA | 0 |  |  |  |  | 5667 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0530 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 79 | NA | 0 |  |  |  |  | 5667 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0630 | 5996 |  |  | 5917 |  |  | -1266 | -1266 | -1187 | Critical Branch | Validation phase | 79 | NA | 0 |  |  |  |  | 5667 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0730 | 5280 |  |  | 4616 |  |  | -2744 | -2744 | -2080 | TTC Selection - LTTC | Validation phase | 664 | NA | 0 |  |  |  |  | 4366 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0830 | 5280 |  |  | 4616 |  |  | -2744 | -2744 | -2080 | TTC Selection - LTTC | Validation phase | 664 | NA | 0 |  |  |  |  | 4366 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 0930 | 6307 |  |  | 6116 |  |  | -1856 | -1856 | -1665 | Critical Branch | Smoothing ramp | 191 | NA | 0 | Smoothing | Smoothing ramp |  |  | 5892 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1030 | 6307 |  |  | 6142 |  |  | -1856 | -1856 | -1691 | Critical Branch | Validation phase | 165 | NA | 0 |  |  |  |  | 5892 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1130 | 6307 |  |  | 6142 |  |  | -1856 | -1856 | -1691 | Critical Branch | Validation phase | 165 | NA | 0 |  |  |  |  | 5892 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 1230 | 6962 |  |  | 6318 |  |  | -2276 | -2276 | -1632 | Critical Branch | Validation phase | 644 | NA | 0 |  |  |  |  | 6068 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250902 | September | 1330 | 6962 |  |  | 6318 |  |  | -2276 | -2276 | -1632 | Critical Branch | Validation phase | 644 | NA | 0 |  |  |  |  | 6068 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250902 | September | 1430 | 6962 |  |  | 6318 |  |  | -2276 | -2276 | -1632 | Critical Branch | Validation phase | 644 | NA | 0 |  |  |  |  | 6068 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250902 | September | 1530 | 6825 |  |  | 6309 |  |  | -2664 | -2664 | -2131 | Critical Branch | Validation phase | 516 | NA | 0 |  |  |  |  | 6560 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 1900 | Testing of HVDC cables imported from Italy to France
20250902 | September | 1630 | 6825 |  |  | 6309 |  |  | -2664 | -2664 | -2131 | Critical Branch | Validation phase | 516 | NA | 0 |  |  |  |  | 6560 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 1900 | Testing of HVDC cables imported from Italy to France
20250902 | September | 1730 | 6825 |  |  | 6780 |  |  | -2664 | -2664 | -2619 | Critical Branch | Smoothing ramp | 45 | NA | 0 | Smoothing | Smoothing ramp |  |  | 6560 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 2130 | 5280 |  |  | 5018 |  |  | -2378 | -2378 | -2116 | TTC Selection - LTTC | Validation phase | 262 | NA | 0 |  |  |  |  | 4768 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 2230 | 5280 |  |  | 5018 |  |  | -2378 | -2378 | -2116 | TTC Selection - LTTC | Validation phase | 262 | NA | 0 |  |  |  |  | 4768 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250902 | September | 2330 | 4680 |  |  | 4418 |  |  | -1770 | -1770 | -1508 | TTC Selection - LTTC | Validation phase | 262 | NA | 0 |  |  |  |  | 4168 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250903 | September | 0030 | 7458 |  |  | 6886 |  |  | -1708 | -1708 | -1138 | Critical Branch | Validation phase | 572 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6639 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250903 | September | 0130 | 7458 |  |  | 6886 |  |  | -1708 | -1708 | -1138 | Critical Branch | Validation phase | 572 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6639 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250903 | September | 0230 | 7458 |  |  | 6886 |  |  | -1708 | -1708 | -1138 | Critical Branch | Validation phase | 572 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6639 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20250903 | September | 0330 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 519 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6958 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2646 | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0430 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 519 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6958 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2646 | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0530 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 519 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6958 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2646 | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0630 | 7704 |  |  | 7185 |  |  | -1506 | -1506 | -991 | Critical Branch | Validation phase | 519 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6958 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2646 | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT]
20250903 | September | 0730 | 7456 |  |  | 6813 |  |  | -2235 | -2235 | -1592 | Critical Branch | Validation phase | 643 | NA | 0 |  |  | 425 |  | 6563 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 0830 | 7456 |  |  | 6813 |  |  | -2235 | -2235 | -1592 | Critical Branch | Validation phase | 643 | NA | 0 |  |  | 425 |  | 6563 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 0930 | 7548 |  |  | 7485 |  |  | -2127 | -2127 | -2065 | Critical Branch | Validation phase | 63 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7237 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1030 | 7548 |  |  | 7485 |  |  | -2127 | -2127 | -2065 | Critical Branch | Validation phase | 63 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7237 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1130 | 7548 |  |  | 7485 |  |  | -2127 | -2127 | -2065 | Critical Branch | Validation phase | 63 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7237 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1230 | 7605 |  |  | 7448 |  |  | -734 | -734 | -577 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7198 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1330 | 7605 |  |  | 7448 |  |  | -734 | -734 | -577 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7198 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1430 | 7605 |  |  | 7448 |  |  | -734 | -734 | -577 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7198 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1530 | 7439 |  |  | 7287 |  |  | -755 | -755 | -603 | Critical Branch | Validation phase | 152 | NA | 0 |  |  | 424 |  | 7037 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1630 | 7439 |  |  | 7287 |  |  | -755 | -755 | -603 | Critical Branch | Validation phase | 152 | NA | 0 |  |  | 424 |  | 7037 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1730 | 7439 |  |  | 7287 |  |  | -755 | -755 | -603 | Critical Branch | Validation phase | 152 | NA | 0 |  |  | 424 |  | 7037 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 1830 |  | 6471 | 650 |  | 6263 | 630 | -871 | -871 | 0 | Critical Branch | Validation phase | NA | 228 | 871 |  |  | 398 |  | 6500 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250903 | September | 1930 |  | 6471 | 650 |  | 6263 | 462 | -871 | -871 | 0 | Critical Branch | Validation phase | NA | 396 | 871 |  |  | 398 |  | 6500 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250903 | September | 2030 |  | 6471 | 650 |  | 6263 | 462 | -871 | -871 | 0 | Critical Branch | Validation phase | NA | 396 | 871 |  |  | 398 |  | 6500 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250903 | September | 2130 | 7606 |  |  | 7186 |  |  | -2101 | -2101 | -1681 | Critical Branch | Validation phase | 420 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6936 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 2230 | 7606 |  |  | 7186 |  |  | -2101 | -2101 | -1681 | Critical Branch | Validation phase | 420 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6936 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250903 | September | 2330 | 7006 |  |  | 6586 |  |  | -1489 | -1489 | -1069 | Critical Branch | Validation phase | 420 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6336 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250904 | September | 0030 | 7640 |  |  | 7277 |  |  | -2648 | -2648 | -2295 | Critical Branch | Validation phase | 363 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7221 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0130 | 7640 |  |  | 7277 |  |  | -2648 | -2648 | -2295 | Critical Branch | Validation phase | 363 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7221 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0230 | 7640 |  |  | 7277 |  |  | -2648 | -2648 | -2295 | Critical Branch | Validation phase | 363 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7221 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0330 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250904 | September | 0430 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250904 | September | 0530 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250904 | September | 0630 | 7160 |  |  | 7140 |  |  | -2086 | -2086 | -2073 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250904 | September | 0730 | 7221 |  |  | 6791 |  |  | -1585 | -1585 | -1155 | Critical Branch | Validation phase | 430 | NA | 0 |  |  | 410 |  | 6541 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250904 | September | 0830 | 7221 |  |  | 6298 |  |  | -1585 | -1585 | -748 | Critical Branch | Validation phase | 923 | NA | 0 |  |  | 410 |  | 6541 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 1900 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 0930 | 7571 |  |  | 6697 |  |  | -890 | -890 | -142 | Critical Branch | Validation phase | 874 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7185 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 1900 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1030 | 7571 |  |  | 6697 |  |  | -890 | -890 | -142 | Critical Branch | Validation phase | 874 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7185 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 1900 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1130 | 7571 |  |  | 7297 |  |  | -890 | -890 | -640 | Critical Branch | Validation phase | 274 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7185 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1230 | 7753 |  |  | 7384 |  |  | -2959 | -2959 | -2587 | Critical Branch | Validation phase | 369 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7339 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1330 | 7753 |  |  | 7384 |  |  | -2959 | -2959 | -2587 | Critical Branch | Validation phase | 369 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7339 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1430 | 7753 |  |  | 7384 |  |  | -2959 | -2959 | -2587 | Critical Branch | Validation phase | 369 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7339 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1530 | 7405 |  |  | 7405 |  |  | -2863 | -2863 | -2863 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 422
20250904 | September | 1630 | 7405 |  |  | 7405 |  |  | -2863 | -2863 | -2863 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 422
20250904 | September | 1730 | 7405 |  |  | 7405 |  |  | -2863 | -2863 | -2863 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 422
20250904 | September | 1830 |  | 6366 | 870 |  | 5724 | 789 | -1913 | -1913 | 0 | Critical Branch | Validation phase | NA | 723 | 1913 |  |  | 194 | Reduction because NTC over thermal limit on border | 6047 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 1930 |  | 6366 | 870 |  | 5724 | 789 | -1913 | -1913 | 0 | Critical Branch | Validation phase | NA | 723 | 1913 |  |  | 194 | Reduction because NTC over thermal limit on border | 6047 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2030 |  | 6366 | 870 |  | 5724 | 789 | -1913 | -1913 | 0 | Critical Branch | Validation phase | NA | 723 | 1913 |  |  | 194 | Reduction because NTC over thermal limit on border | 6047 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2130 | 7566 |  |  | 7134 |  |  | -3390 | -3390 | -2956 | Critical Branch | Validation phase | 432 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6923 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2230 | 7566 |  |  | 7134 |  |  | -3390 | -3390 | -2956 | Critical Branch | Validation phase | 432 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6923 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250904 | September | 2330 | 6966 |  |  | 6573 |  |  | -2782 | -2782 | -2389 | Critical Branch | Validation phase | 393 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6323 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250905 | September | 0030 | 7747 |  |  | 7296 |  |  | -3005 | -3005 | -2571 | Critical Branch | Validation phase | 451 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7256 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0130 | 7747 |  |  | 7296 |  |  | -3005 | -3005 | -2571 | Critical Branch | Validation phase | 451 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7256 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0230 | 7747 |  |  | 7296 |  |  | -3005 | -3005 | -2571 | Critical Branch | Validation phase | 451 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7256 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0330 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 391 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7383 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0430 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 391 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7383 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0530 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 391 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7383 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0630 | 7758 |  |  | 7367 |  |  | -2722 | -2722 | -2348 | Critical Branch | Validation phase | 391 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7383 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 0730 | 7313 |  |  | 7174 |  |  | -3927 | -3927 | -3788 | Critical Branch | Validation phase | 139 | NA | 0 |  |  | 416 |  | 6924 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 0830 | 7313 |  |  | 7174 |  |  | -3927 | -3927 | -3788 | Critical Branch | Validation phase | 139 | NA | 0 |  |  | 416 |  | 6924 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 0930 | 7286 |  |  | 6858 |  |  | -2583 | -2583 | -2155 | Critical Branch | Validation phase | 428 | NA | 0 |  |  | 414 |  | 6608 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1030 | 7286 |  |  | 6858 |  |  | -2583 | -2583 | -2155 | Critical Branch | Validation phase | 428 | NA | 0 |  |  | 414 |  | 6608 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1130 | 7286 |  |  | 6858 |  |  | -2583 | -2583 | -2155 | Critical Branch | Validation phase | 428 | NA | 0 |  |  | 414 |  | 6608 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1230 | 7192 |  |  | 6757 |  |  | -1169 | -1169 | -734 | Critical Branch | Validation phase | 435 | NA | 0 |  |  | 409 |  | 6507 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1330 | 7192 |  |  | 6757 |  |  | -1169 | -1169 | -734 | Critical Branch | Validation phase | 435 | NA | 0 |  |  | 409 |  | 6507 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1430 | 7192 |  |  | 6757 |  |  | -1169 | -1169 | -734 | Critical Branch | Validation phase | 435 | NA | 0 |  |  | 409 |  | 6507 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250905 | September | 1530 | 7535 |  |  | 7190 |  |  | -2989 | -2989 | -2640 | Critical Branch | Validation phase | 345 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7012 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1630 | 7535 |  |  | 7190 |  |  | -2989 | -2989 | -2640 | Critical Branch | Validation phase | 345 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7012 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1730 | 7535 |  |  | 7190 |  |  | -2989 | -2989 | -2640 | Critical Branch | Validation phase | 345 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7012 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1830 |  | 7234 | 974 |  | 6732 | 947 | -4938 | -4938 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 529 | 4938 |  |  | 223 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 1930 |  | 7234 | 974 |  | 6732 | 947 | -4938 | -4938 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 529 | 4938 |  |  | 223 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2030 |  | 7234 | 974 |  | 6732 | 947 | -4938 | -4938 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 529 | 4938 |  |  | 223 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2130 | 7912 |  |  | 7295 |  |  | -4245 | -4245 | -3628 | Critical Branch | Validation phase | 617 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7182 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2230 | 7912 |  |  | 7295 |  |  | -4245 | -4245 | -3628 | Critical Branch | Validation phase | 617 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7182 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250905 | September | 2330 | 7312 |  |  | 6832 |  |  | -3637 | -3637 | -3157 | Critical Branch | Validation phase | 480 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6582 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0030 | 7418 |  |  | 6639 |  |  | -2852 | -2852 | -2073 | Critical Branch | Validation phase | 779 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6389 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0130 | 7418 |  |  | 6639 |  |  | -2852 | -2852 | -2073 | Critical Branch | Validation phase | 779 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6389 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0230 | 7418 |  |  | 6639 |  |  | -2852 | -2852 | -2073 | Critical Branch | Validation phase | 779 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6389 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0330 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 762 | NA | 1176 |  |  | 415 |  | 5839 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0430 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 762 | NA | 1176 |  |  | 415 |  | 5839 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0530 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 762 | NA | 1176 |  |  | 415 |  | 5839 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0630 | 6851 |  |  | 6089 |  |  | -348 | -348 | 414 | Critical Branch | Validation phase | 762 | NA | 1176 |  |  | 415 |  | 5839 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0730 | 6970 |  |  | 6406 |  |  | -2612 | -2612 | -2048 | Critical Branch | Validation phase | 564 | NA | 0 |  |  | 395 |  | 6156 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0830 | 6970 |  |  | 6406 |  |  | -2612 | -2612 | -2048 | Critical Branch | Validation phase | 564 | NA | 0 |  |  | 395 |  | 6156 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 0930 | 7411 |  |  | 6498 |  |  | -2894 | -2894 | -1981 | Critical Branch | Validation phase | 913 | NA | 0 |  |  | 422 |  | 6248 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1030 | 7411 |  |  | 6498 |  |  | -2894 | -2894 | -1981 | Critical Branch | Validation phase | 913 | NA | 0 |  |  | 422 |  | 6248 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1130 | 7411 |  |  | 6498 |  |  | -2894 | -2894 | -1981 | Critical Branch | Validation phase | 913 | NA | 0 |  |  | 422 |  | 6248 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1230 | 6998 |  |  | 6954 |  |  | -3480 | -3480 | -3436 | Critical Branch | Validation phase | 44 | NA | 0 |  |  | 397 |  | 6704 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1330 | 6998 |  |  | 6954 |  |  | -3480 | -3480 | -3436 | Critical Branch | Validation phase | 44 | NA | 0 |  |  | 397 |  | 6704 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1430 | 6998 |  |  | 6954 |  |  | -3480 | -3480 | -3436 | Critical Branch | Validation phase | 44 | NA | 0 |  |  | 397 |  | 6704 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1530 |  | 5978 | 577 |  | 5645 | 545 | -3398 | -3398 | 0 | Critical Branch | Validation phase | NA | 365 | 3398 |  |  | 365 |  | 5919 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1630 |  | 5978 | 577 |  | 5645 | 545 | -3398 | -3398 | 0 | Critical Branch | Validation phase | NA | 365 | 3398 |  |  | 365 |  | 5919 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1730 |  | 5978 | 577 |  | 5645 | 545 | -3398 | -3398 | 0 | Critical Branch | Validation phase | NA | 365 | 3398 |  |  | 365 |  | 5919 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1830 |  | 5983 | 760 |  | 5385 | 684 | -3921 | -3921 | 0 | Critical Branch | Validation phase | NA | 674 | 3921 |  |  | 182 |  | 6027 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 1930 |  | 5983 | 760 |  | 5385 | 684 | -3921 | -3921 | 0 | Critical Branch | Validation phase | NA | 674 | 3921 |  |  | 182 |  | 6027 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2030 |  | 5983 | 760 |  | 5385 | 684 | -3921 | -3921 | 0 | Critical Branch | Validation phase | NA | 674 | 3921 |  |  | 182 |  | 6027 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2130 | 7040 |  |  | 6230 |  |  | -2694 | -2694 | -1884 | Critical Branch | Validation phase | 810 | NA | 0 |  |  | 399 |  | 5980 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2230 | 7040 |  |  | 6230 |  |  | -2694 | -2694 | -1884 | Critical Branch | Validation phase | 810 | NA | 0 |  |  | 399 |  | 5980 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250906 | September | 2330 | 6440 |  |  | 5630 |  |  | -2091 | -2091 | -1281 | Critical Branch | Validation phase | 810 | NA | 0 |  |  | 388 |  | 5380 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250907 | September | 0030 | 7851 |  |  | 7488 |  |  | -783 | -783 | -309 | Critical Branch | TTC Validation phase - bilateral reduction | 363 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0130 | 7851 |  |  | 7488 |  |  | -783 | -783 | -309 | Critical Branch | TTC Validation phase - bilateral reduction | 363 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0230 | 7851 |  |  | 7488 |  |  | -783 | -783 | -309 | Critical Branch | TTC Validation phase - bilateral reduction | 363 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0330 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7587 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0430 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7587 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0530 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7587 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0630 | 7891 |  |  | 7480 |  |  | -2328 | -2328 | -1940 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7587 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0730 | 7922 |  |  | 7496 |  |  | -2380 | -2380 | -1972 | Critical Branch | Validation phase | 426 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7617 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0830 | 7922 |  |  | 6754 |  |  | -2380 | -2380 | -1231 | Critical Branch | Validation phase | 1168 | NA | 0 |  |  | 408 |  | 7617 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 0930 | 5255 |  |  | 5254 |  |  | 1845 | 575 | 1271 | Minimum Margin | Minimum Margin | 1 | NA | 1967 |  |  | 310
20250907 | September | 1030 | 5255 |  |  | 5254 |  |  | 1845 | 575 | 1271 | Minimum Margin | Minimum Margin | 1 | NA | 1967 |  |  | 310
20250907 | September | 1130 | 5255 |  |  | 5254 |  |  | 1845 | 575 | 1271 | Minimum Margin | Minimum Margin | 1 | NA | 1967 |  |  | 310
20250907 | September | 1230 | 6162 |  |  | 6162 |  |  | -191 | -191 | -191 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 370
20250907 | September | 1330 | 6162 |  |  | 6162 |  |  | -191 | -191 | -191 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 370
20250907 | September | 1430 | 6162 |  |  | 6162 |  |  | -191 | -191 | -191 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 370
20250907 | September | 1530 |  | 6916 | 810 |  | 6709 | 810 | -2855 | -2855 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 207 | 2855 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 1630 |  | 6916 | 810 |  | 6709 | 810 | -2855 | -2855 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 207 | 2855 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 1730 |  | 7117 | 810 |  | 6920 | 810 | -3023 | -3023 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 197 | 3023 |  |  | 415 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250907 | September | 1830 |  | 6493 | 691 |  | 6493 | 691 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | NA | 0 | 3208 |  |  | 413
20250907 | September | 1930 |  | 6493 | 691 |  | 6493 | 691 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | NA | 0 | 3208 |  |  | 413
20250907 | September | 2030 |  | 6493 | 691 |  | 6493 | 691 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | NA | 0 | 3208 |  |  | 413
20250907 | September | 2130 | 7642 |  |  | 7604 |  |  | -2489 | -2489 | -2464 | Critical Branch | Critical Branch | 38 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250907 | September | 2230 | 7642 |  |  | 7604 |  |  | -2489 | -2489 | -2464 | Critical Branch | Critical Branch | 38 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250907 | September | 2330 | 7642 |  |  | 7604 |  |  | -2489 | -2489 | -2464 | Critical Branch | Critical Branch | 38 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0030 | 7203 |  |  | 7193 |  |  | -223 | -223 | -217 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0130 | 7203 |  |  | 7193 |  |  | -223 | -223 | -217 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0230 | 7203 |  |  | 7193 |  |  | -223 | -223 | -217 | Critical Branch | Critical Branch | 10 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0330 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 28 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0430 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 28 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0530 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 28 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0630 | 7494 |  |  | 7466 |  |  | -1995 | -1995 | -1978 | Critical Branch | Critical Branch | 28 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250908 | September | 0730 | 6580 |  |  | 6580 |  |  | -2512 | -2512 | -2512 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 361
20250908 | September | 0830 | 6580 |  |  | 6580 |  |  | -2512 | -2512 | -2512 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 361
20250908 | September | 0930 | 7762 |  |  | 7561 |  |  | -2627 | -2627 | -2419 | Critical Branch | Validation phase | 201 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7496 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1030 | 7762 |  |  | 7561 |  |  | -2627 | -2627 | -2419 | Critical Branch | Validation phase | 201 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7496 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1130 | 7762 |  |  | 7561 |  |  | -2627 | -2627 | -2419 | Critical Branch | Validation phase | 201 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7496 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1230 | 7933 |  |  | 7602 |  |  | -1192 | -1192 | -893 | Critical Branch | Validation phase | 331 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7568 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1330 | 7933 |  |  | 7602 |  |  | -1192 | -1192 | -893 | Critical Branch | Validation phase | 331 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7568 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1430 | 7933 |  |  | 7602 |  |  | -1192 | -1192 | -893 | Critical Branch | Validation phase | 331 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7568 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1530 | 7783 |  |  | 7582 |  |  | -2823 | -2823 | -2625 | Critical Branch | TTC Validation phase - bilateral reduction | 201 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1630 | 7783 |  |  | 7582 |  |  | -2823 | -2823 | -2625 | Critical Branch | TTC Validation phase - bilateral reduction | 201 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1730 | 7783 |  |  | 7582 |  |  | -2823 | -2823 | -2625 | Critical Branch | TTC Validation phase - bilateral reduction | 201 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1830 |  | 6310 | 798 |  | 6300 | 660 | -562 | -562 | 0 | Critical Branch | Validation phase | NA | 148 | 562 |  |  | 187 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 1930 |  | 6310 | 798 |  | 6300 | 660 | -562 | -562 | 0 | Critical Branch | Validation phase | NA | 148 | 562 |  |  | 187 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 2030 |  | 6310 | 798 |  | 6300 | 660 | -562 | -562 | 0 | Critical Branch | Validation phase | NA | 148 | 562 |  |  | 187 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250908 | September | 2130 | 6900 |  |  | 6900 |  |  | -1855 | -1855 | -1854 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 380
20250908 | September | 2230 | 6900 |  |  | 6900 |  |  | -1855 | -1855 | -1854 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 380
20250908 | September | 2330 | 6300 |  |  | 6300 |  |  | -1254 | -1254 | -1254 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 367
20250909 | September | 0030 | 7526 |  |  | 7496 |  |  | -947 | -947 | -929 | Critical Branch | Critical Branch | 30 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250909 | September | 0130 | 7526 |  |  | 7496 |  |  | -947 | -947 | -929 | Critical Branch | Critical Branch | 30 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250909 | September | 0230 | 7526 |  |  | 7496 |  |  | -947 | -947 | -929 | Critical Branch | Critical Branch | 30 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250909 | September | 0330 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 385 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7733 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0430 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 385 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7733 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0530 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 385 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7733 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0630 | 8048 |  |  | 7663 |  |  | -1420 | -1420 | -964 | Critical Branch | Validation phase | 385 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7733 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 0730 |  | 6407 | 806 |  | 6407 | 806 | -4511 | -4511 | 0 | Critical Branch | Critical Branch | NA | 0 | 4511 |  |  | 190
20250909 | September | 0830 |  | 6378 | 786 |  | 6378 | 786 | -4461 | -4461 | 0 | Critical Branch | Critical Branch | NA | 0 | 4461 |  |  | 163
20250909 | September | 0930 | 7374 |  |  | 7373 |  |  | -469 | -469 | -468 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 353
20250909 | September | 1030 | 7374 |  |  | 7373 |  |  | -469 | -469 | -468 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 353
20250909 | September | 1130 | 7374 |  |  | 7373 |  |  | -469 | -469 | -468 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 353
20250909 | September | 1230 | 6849 |  |  | 6848 |  |  | -3137 | -3137 | -3136 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 326
20250909 | September | 1330 | 6849 |  |  | 6848 |  |  | -3137 | -3137 | -3136 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 326
20250909 | September | 1430 | 6849 |  |  | 6848 |  |  | -3137 | -3137 | -3136 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 326
20250909 | September | 1530 | 8035 |  |  | 7702 |  |  | -3590 | -3590 | -3262 | Critical Branch | TTC Validation phase - bilateral reduction | 333 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 1630 | 8035 |  |  | 7702 |  |  | -3590 | -3590 | -3262 | Critical Branch | TTC Validation phase - bilateral reduction | 333 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 1730 | 8035 |  |  | 7702 |  |  | -3590 | -3590 | -3262 | Critical Branch | TTC Validation phase - bilateral reduction | 333 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250909 | September | 1830 |  | 6476 | 799 |  | 6476 | 799 | -4564 | -4564 | 0 | Critical Branch | Critical Branch | NA | 0 | 4564 |  |  | 165
20250909 | September | 1930 |  | 6476 | 799 |  | 6476 | 799 | -4564 | -4564 | 0 | Critical Branch | Validation phase | NA | 0 | 4564 |  |  | 165
20250909 | September | 2030 |  | 6476 | 799 |  | 6476 | 799 | -4564 | -4564 | 0 | Critical Branch | Validation phase | NA | 0 | 4564 |  |  | 165
20250909 | September | 2130 |  | 6706 | 655 |  | 6705 | 655 | -4005 | -4005 | 0 | Critical Branch | Validation phase | NA | 1 | 4005 |  |  | 347
20250909 | September | 2230 |  | 6706 | 655 |  | 6705 | 655 | -4005 | -4005 | 0 | Critical Branch | Critical Branch | NA | 1 | 4005 |  |  | 347
20250909 | September | 2330 |  | 6126 | 680 |  | 6126 | 680 | -3376 | -3376 | 0 | Critical Branch | Critical Branch | NA | 0 | 3376 |  |  | 335
20250910 | September | 0030 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0130 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0230 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0330 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0430 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0530 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0630 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250910 | September | 0730 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 0830 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 0930 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1030 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1130 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1230 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1330 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1430 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1530 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1630 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1730 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1830 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 1930 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2030 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2130 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2230 | 7590 |  |  | 7446 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  |  |  | 7340 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250910 | September | 2330 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  |  |  | 6740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250911 | September | 0030 | 8153 |  |  | 7541 |  |  | -951 | -951 | -265 | Critical Branch | Validation phase | 612 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7557 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0130 | 8153 |  |  | 7541 |  |  | -951 | -951 | -265 | Critical Branch | Validation phase | 612 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7557 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0230 | 8153 |  |  | 7541 |  |  | -951 | -951 | -265 | Critical Branch | Validation phase | 612 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7557 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0330 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 760 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7630 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0430 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 760 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7630 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0530 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 760 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7630 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0630 | 8343 |  |  | 7583 |  |  | -1272 | -1272 | -418 | Critical Branch | Validation phase | 760 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7630 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0730 | 8195 |  |  | 7603 |  |  | -1587 | -1587 | -909 | Critical Branch | Validation phase | 592 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7613 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0830 | 8195 |  |  | 7603 |  |  | -1587 | -1587 | -909 | Critical Branch | Validation phase | 592 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7613 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 0930 | 7327 |  |  | 7327 |  |  | -2277 | -2277 | -2276 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 351
20250911 | September | 1030 | 7327 |  |  | 7327 |  |  | -2277 | -2277 | -2276 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 351
20250911 | September | 1130 | 7327 |  |  | 7327 |  |  | -2277 | -2277 | -2276 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 351
20250911 | September | 1230 | 7409 |  |  | 7397 |  |  | -1496 | -1496 | -1484 | Critical Branch | Validation phase | 12 | NA | 0 |  |  | 355 |  | 7147 | Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20250911 | September | 1330 | 7409 |  |  | 7397 |  |  | -1496 | -1496 | -1484 | Critical Branch | Validation phase | 12 | NA | 0 |  |  | 355 |  | 7147 | Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20250911 | September | 1430 | 7409 |  |  | 7397 |  |  | -1496 | -1496 | -1484 | Critical Branch | Validation phase | 12 | NA | 0 |  |  | 355 |  | 7147 | Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20250911 | September | 1530 | 7839 |  |  | 7363 |  |  | -3097 | -3097 | -2577 | Critical Branch | Validation phase | 476 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7207 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1630 | 7839 |  |  | 7363 |  |  | -3097 | -3097 | -2577 | Critical Branch | Validation phase | 476 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7207 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1730 | 7839 |  |  | 7363 |  |  | -3097 | -3097 | -2577 | Critical Branch | Validation phase | 476 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7207 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1830 | 8375 |  |  | 7498 |  |  | -2884 | -2884 | -2033 | Critical Branch | Validation phase | 877 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7430 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 1930 | 8375 |  |  | 7498 |  |  | -2884 | -2884 | -2033 | Critical Branch | Validation phase | 877 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7430 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2030 | 8375 |  |  | 7498 |  |  | -2884 | -2884 | -2033 | Critical Branch | Validation phase | 877 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7430 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2130 | 8380 |  |  | 7584 |  |  | -1906 | -1906 | -1019 | Critical Branch | Validation phase | 796 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7580 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2230 | 8380 |  |  | 7584 |  |  | -1906 | -1906 | -1019 | Critical Branch | Validation phase | 796 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7580 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250911 | September | 2330 | 7780 |  |  | 7210 |  |  | -1300 | -1300 | -733 | Critical Branch | Validation phase | 570 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 6980 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0030 | 7568 |  |  | 7367 |  |  | -2274 | -2274 | -2080 | Critical Branch | Validation phase | 201 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7253 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0130 | 7568 |  |  | 7367 |  |  | -2274 | -2274 | -2080 | Critical Branch | Validation phase | 201 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7253 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0230 | 7568 |  |  | 7367 |  |  | -2274 | -2274 | -2080 | Critical Branch | Validation phase | 201 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7253 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0330 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0430 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0530 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0630 | 7753 |  |  | 7431 |  |  | -2124 | -2124 | -1811 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 355 | Reduction because NTC over thermal limit on border | 7365 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 0730 | 6954 |  |  | 6954 |  |  | -2532 | -2532 | -2532 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 332
20250912 | September | 0830 | 6954 |  |  | 6954 |  |  | -2532 | -2532 | -2532 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 332
20250912 | September | 0930 | 7763 |  |  | 7546 |  |  | -1773 | -1773 | -1566 | Critical Branch | TTC Validation phase - bilateral reduction | 217 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1030 | 7763 |  |  | 7546 |  |  | -1773 | -1773 | -1566 | Critical Branch | TTC Validation phase - bilateral reduction | 217 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1130 | 7763 |  |  | 7546 |  |  | -1773 | -1773 | -1566 | Critical Branch | TTC Validation phase - bilateral reduction | 217 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1230 | 7379 |  |  | 7239 |  |  | -1110 | -1110 | -973 | Critical Branch | Validation phase | 140 | NA | 0 |  |  | 364 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1330 | 7379 |  |  | 7239 |  |  | -1110 | -1110 | -973 | Critical Branch | Validation phase | 140 | NA | 0 |  |  | 364 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1430 | 7379 |  |  | 7239 |  |  | -1110 | -1110 | -973 | Critical Branch | Validation phase | 140 | NA | 0 |  |  | 364 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1530 | 7775 |  |  | 7463 |  |  | -1488 | -1488 | -1190 | Critical Branch | TTC Validation phase - bilateral reduction | 312 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1630 | 7775 |  |  | 7463 |  |  | -1488 | -1488 | -1190 | Critical Branch | TTC Validation phase - bilateral reduction | 312 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250912 | September | 1730 | 7835 |  |  | 7090 |  |  | -1554 | -1554 | -805 | Critical Branch | Critical Branch | 745 | NA | 0 |  |  | 403
20250912 | September | 1830 |  | 5166 | 502 |  | 5165 | 502 | -2503 | -2503 | 0 | Critical Branch | Critical Branch | NA | 1 | 2503 |  |  | 311
20250912 | September | 1930 |  | 5366 | 502 |  | 5365 | 502 | -2729 | -2729 | 0 | Critical Branch | Critical Branch | NA | 1 | 2729 |  |  | 314
20250912 | September | 2030 |  | 5366 | 502 |  | 5365 | 502 | -2729 | -2729 | 0 | Critical Branch | Critical Branch | NA | 1 | 2729 |  |  | 314
20250912 | September | 2130 | 6799 |  |  | 6710 |  |  | -2346 | -2346 | -2257 | Critical Branch | Validation phase | 89 | NA | 0 |  |  | 374 |  | 6460 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250912 | September | 2230 | 6799 |  |  | 6710 |  |  | -2346 | -2346 | -2257 | Critical Branch | Validation phase | 89 | NA | 0 |  |  | 374 |  | 6460 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250912 | September | 2330 | 6199 |  |  | 6110 |  |  | -1737 | -1737 | -1648 | Critical Branch | Validation phase | 89 | NA | 0 |  |  | 361 |  | 5860 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0030 | 6413 |  |  | 6412 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 374
20250913 | September | 0130 | 6413 |  |  | 6412 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 374
20250913 | September | 0230 | 6413 |  |  | 6412 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 374
20250913 | September | 0330 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6744 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0430 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6744 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0530 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6744 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0630 | 7213 |  |  | 6994 |  |  | -2070 | -2070 | -1851 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6744 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0730 | 6545 |  |  | 6439 |  |  | -1772 | -1772 | -1666 | Critical Branch | Validation phase | 106 | NA | 0 |  |  | 369 |  | 6189 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0830 | 6545 |  |  | 6439 |  |  | -1772 | -1772 | -1666 | Critical Branch | Validation phase | 106 | NA | 0 |  |  | 369 |  | 6189 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 0930 | 7666 |  |  | 7427 |  |  | -5189 | -5189 | -4952 | Critical Branch | TTC Validation phase - bilateral reduction | 239 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1030 | 7666 |  |  | 7427 |  |  | -5189 | -5189 | -4952 | Critical Branch | TTC Validation phase - bilateral reduction | 239 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1130 | 7666 |  |  | 7427 |  |  | -5189 | -5189 | -4952 | Critical Branch | TTC Validation phase - bilateral reduction | 239 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1230 | 6567 |  |  | 6567 |  |  | -3716 | -3716 | -3716 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 371
20250913 | September | 1330 | 6567 |  |  | 6567 |  |  | -3716 | -3716 | -3716 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 371
20250913 | September | 1430 | 6567 |  |  | 6567 |  |  | -3716 | -3716 | -3716 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 371
20250913 | September | 1530 | 7696 |  |  | 7443 |  |  | -2068 | -2068 | -1831 | Critical Branch | TTC Validation phase - bilateral reduction | 253 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1630 | 7696 |  |  | 7443 |  |  | -2068 | -2068 | -1831 | Critical Branch | TTC Validation phase - bilateral reduction | 253 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1730 | 7696 |  |  | 7370 |  |  | -2068 | -2068 | -1758 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 420 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250913 | September | 1830 |  | 5416 | 526 |  | 5416 | 526 | -2882 | -2882 | 0 | Critical Branch | Critical Branch | NA | 0 | 2882 |  |  | 328
20250913 | September | 1930 |  | 5616 | 526 |  | 5616 | 526 | -3111 | -3111 | 0 | Critical Branch | Critical Branch | NA | 0 | 3111 |  |  | 331
20250913 | September | 2030 |  | 5616 | 526 |  | 5616 | 526 | -3111 | -3111 | 0 | Critical Branch | Critical Branch | NA | 0 | 3111 |  |  | 331
20250913 | September | 2130 | 6798 |  |  | 6737 |  |  | -1935 | -1935 | -1874 | Critical Branch | Validation phase | 61 | NA | 0 |  |  | 374 |  | 6487 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 2230 | 6798 |  |  | 6737 |  |  | -1935 | -1935 | -1874 | Critical Branch | Validation phase | 61 | NA | 0 |  |  | 374 |  | 6487 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250913 | September | 2330 | 6198 |  |  | 6137 |  |  | -1324 | -1324 | -1263 | Critical Branch | Validation phase | 61 | NA | 0 |  |  | 361 |  | 5887 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0030 | 7509 |  |  | 7395 |  |  | 239 | 239 | 105 | Adjustment reached | Validation phase | 114 | NA | -29 |  |  | 415 | Reduction because NTC over thermal limit on border | 7168 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0130 | 7509 |  |  | 7395 |  |  | 239 | 239 | 105 | Adjustment reached | Validation phase | 114 | NA | -29 |  |  | 415 | Reduction because NTC over thermal limit on border | 7168 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0230 | 7509 |  |  | 7395 |  |  | 239 | 239 | 105 | Adjustment reached | Validation phase | 114 | NA | -29 |  |  | 415 | Reduction because NTC over thermal limit on border | 7168 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0330 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7184 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0430 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7184 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0530 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7184 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0630 | 7532 |  |  | 7410 |  |  | -1905 | -1905 | -1793 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7184 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0730 | 7384 |  |  | 7274 |  |  | -1964 | -1964 | -1867 | Critical Branch | Validation phase | 110 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7054 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0830 | 7384 |  |  | 7274 |  |  | -1964 | -1964 | -1867 | Critical Branch | Validation phase | 110 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7054 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 0930 | 7430 |  |  | 7383 |  |  | -2392 | -2392 | -2360 | Critical Branch | Validation phase | 47 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7170 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 1030 | 7430 |  |  | 7383 |  |  | -2392 | -2392 | -2360 | Critical Branch | Validation phase | 47 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7170 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 1130 | 7430 |  |  | 7383 |  |  | -2392 | -2392 | -2360 | Critical Branch | Validation phase | 47 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7170 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250914 | September | 1230 | 6684 |  |  | 6684 |  |  | -3837 | -3837 | -3836 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 404
20250914 | September | 1330 | 6684 |  |  | 6684 |  |  | -3837 | -3837 | -3836 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 404
20250914 | September | 1430 | 6684 |  |  | 6684 |  |  | -3837 | -3837 | -3836 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 404
20250914 | September | 1530 | 6850 |  |  | 6850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250914 | September | 1630 | 6850 |  |  | 6850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250914 | September | 1730 | 6850 |  |  | 6850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250914 | September | 1830 | 6241 |  |  | 6241 |  |  | -2755 | -2755 | -2755 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 375
20250914 | September | 1930 | 6441 |  |  | 6441 |  |  | -2968 | -2968 | -2968 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 376
20250914 | September | 2030 | 6441 |  |  | 6441 |  |  | -2968 | -2968 | -2968 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 376
20250914 | September | 2130 | 6620 |  |  | 6619 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20250914 | September | 2230 | 6620 |  |  | 6619 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20250914 | September | 2330 | 6620 |  |  | 6619 |  |  | -1116 | -1116 | -1116 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20250915 | September | 0030 | 6641 |  |  | 6380 |  |  | -1185 | -1185 | 0 | Critical Branch | Validation phase | 261 | NA | 1185 |  |  | 389 |  | 6130 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0130 | 6641 |  |  | 6380 |  |  | -1185 | -1185 | 0 | Critical Branch | Validation phase | 261 | NA | 1185 |  |  | 389 |  | 6130 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0230 | 6641 |  |  | 6380 |  |  | -1185 | -1185 | 0 | Critical Branch | Validation phase | 261 | NA | 1185 |  |  | 389 |  | 6130 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0330 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 171 | NA | 1181 |  |  | 415 | Reduction because NTC over thermal limit on border | 6663 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0430 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 171 | NA | 1181 |  |  | 415 | Reduction because NTC over thermal limit on border | 6663 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0530 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 171 | NA | 1181 |  |  | 415 | Reduction because NTC over thermal limit on border | 6663 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0630 | 7084 |  |  | 6913 |  |  | -1181 | -1181 | 0 | Critical Branch | Validation phase | 171 | NA | 1181 |  |  | 415 | Reduction because NTC over thermal limit on border | 6663 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0730 | 6490 |  |  | 6418 |  |  | -1834 | -1834 | 0 | Critical Branch | Validation phase | 72 | NA | 1834 |  |  | 356 |  | 6168 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0830 | 6490 |  |  | 6418 |  |  | -1834 | -1834 | 0 | Critical Branch | Validation phase | 72 | NA | 1834 |  |  | 356 |  | 6168 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250915 | September | 0930 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1030 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1130 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1230 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1330 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1430 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1530 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1630 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1730 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1830 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 1930 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2030 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2130 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2230 | 7650 |  |  | 7506 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 144 | NA | 0 |  |  | 425 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250915 | September | 2330 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 415
20250916 | September | 0030 | 6859 |  |  | 6737 |  |  | -1516 | -1516 | -1394 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 402 |  | 6487 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0130 | 6859 |  |  | 6737 |  |  | -1516 | -1516 | -1394 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 402 |  | 6487 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0230 | 6859 |  |  | 6737 |  |  | -1516 | -1516 | -1394 | Critical Branch | Validation phase | 122 | NA | 0 |  |  | 402 |  | 6487 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0330 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 160 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6662 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0430 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 160 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6662 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0530 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 160 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6662 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0630 | 7072 |  |  | 6912 |  |  | -1683 | -1683 | -1523 | Critical Branch | Validation phase | 160 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6662 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0730 | 7252 |  |  | 7149 |  |  | -2431 | -2431 | -2328 | Critical Branch | Validation phase | 103 | NA | 0 |  |  | 401 |  | 6899 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0830 | 7252 |  |  | 7149 |  |  | -2431 | -2431 | -2328 | Critical Branch | Validation phase | 103 | NA | 0 |  |  | 401 |  | 6899 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250916 | September | 0930 | 7239 |  |  | 7212 |  |  | -732 | -732 | -705 | Critical Branch | Validation phase | 27 | NA | 0 |  |  | 400 |  | 6962 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250916 | September | 1030 | 7239 |  |  | 7212 |  |  | -732 | -732 | -705 | Critical Branch | Validation phase | 27 | NA | 0 |  |  | 400 |  | 6962 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250916 | September | 1130 | 7239 |  |  | 7212 |  |  | -732 | -732 | -705 | Critical Branch | Validation phase | 27 | NA | 0 |  |  | 400 |  | 6962 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250916 | September | 1230 | 6641 |  |  | 6641 |  |  | -4124 | -4124 | -4124 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 365
20250916 | September | 1330 | 6641 |  |  | 6641 |  |  | -4124 | -4124 | -4124 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 365
20250916 | September | 1430 | 6641 |  |  | 6641 |  |  | -4124 | -4124 | -4124 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 365
20250916 | September | 1530 | 7635 |  |  | 7496 |  |  | -998 | -998 | -853 | Critical Branch | Validation phase | 139 | NA | 0 |  |  | 424 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1630 | 7635 |  |  | 7496 |  |  | -998 | -998 | -853 | Critical Branch | Validation phase | 139 | NA | 0 |  |  | 424 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1730 | 7635 |  |  | 7496 |  |  | -998 | -998 | -853 | Critical Branch | Validation phase | 139 | NA | 0 |  |  | 424 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1830 |  | 7107 | 672 |  | 6950 | 672 | -3133 | -3133 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 157 | 3133 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 1930 |  | 7107 | 672 |  | 6950 | 672 | -3133 | -3133 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 157 | 3133 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2030 |  | 7107 | 672 |  | 6950 | 672 | -3133 | -3133 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 157 | 3133 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2130 | 7422 |  |  | 7340 |  |  | -2332 | -2332 | -2249 | Critical Branch | Validation phase | 82 | NA | 0 |  |  | 411 |  | 7137 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2230 | 7422 |  |  | 7340 |  |  | -2332 | -2332 | -2249 | Critical Branch | Validation phase | 82 | NA | 0 |  |  | 411 |  | 7137 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250916 | September | 2330 | 6822 |  |  | 6787 |  |  | -1721 | -1721 | -1686 | Critical Branch | Validation phase | 35 | NA | 0 |  |  | 400 |  | 6537 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0030 | 7028 |  |  | 6876 |  |  | -1444 | -1444 | -1292 | Critical Branch | Validation phase | 152 | NA | 0 |  |  |  |  | 6626 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0130 | 7028 |  |  | 6876 |  |  | -1444 | -1444 | -1292 | Critical Branch | Validation phase | 152 | NA | 0 |  |  |  |  | 6626 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0230 | 7028 |  |  | 6876 |  |  | -1444 | -1444 | -1292 | Critical Branch | Validation phase | 152 | NA | 0 |  |  |  |  | 6626 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0330 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 183 | NA | 0 |  |  |  |  | 6261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0430 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 183 | NA | 0 |  |  |  |  | 6261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0530 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 183 | NA | 0 |  |  |  |  | 6261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0630 | 6694 |  |  | 6511 |  |  | -1074 | -1074 | -891 | Critical Branch | Validation phase | 183 | NA | 0 |  |  |  |  | 6261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0730 | 6664 |  |  | 6631 |  |  | -2209 | -2209 | -2176 | Critical Branch | Validation phase | 33 | NA | 0 |  |  |  |  | 6381 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 0830 | 6664 |  |  | 6631 |  |  | -2209 | -2209 | -2176 | Critical Branch | Validation phase | 33 | NA | 0 |  |  |  |  | 6381 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 2130 | 6469 |  |  | 6402 |  |  | -1310 | -1310 | -1243 | Critical Branch | Validation phase | 67 | NA | 0 |  |  |  |  | 6152 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 2230 | 6469 |  |  | 6402 |  |  | -1310 | -1310 | -1243 | Critical Branch | Validation phase | 67 | NA | 0 |  |  |  |  | 6152 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250917 | September | 2330 | 5869 |  |  | 5802 |  |  | -697 | -697 | -630 | Critical Branch | Validation phase | 67 | NA | 0 |  |  |  |  | 5552 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0030 | 6761 |  |  | 6531 |  |  | -1576 | -1576 | -1346 | Critical Branch | Validation phase | 230 | NA | 0 |  |  | 396 |  | 6281 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0130 | 6761 |  |  | 6531 |  |  | -1576 | -1576 | -1346 | Critical Branch | Validation phase | 230 | NA | 0 |  |  | 396 |  | 6281 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0230 | 6761 |  |  | 6531 |  |  | -1576 | -1576 | -1346 | Critical Branch | Validation phase | 230 | NA | 0 |  |  | 396 |  | 6281 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0330 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 405 |  | 6486 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0430 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 405 |  | 6486 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0530 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 405 |  | 6486 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0630 | 6893 |  |  | 6736 |  |  | -1588 | -1588 | -1431 | Critical Branch | Validation phase | 157 | NA | 0 |  |  | 405 |  | 6486 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 0730 | 5663 |  |  | 5663 |  |  | -1841 | -1841 | -1841 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 320
20250918 | September | 0830 | 5663 |  |  | 5663 |  |  | -1841 | -1841 | -1841 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 320
20250918 | September | 0930 | 7031 |  |  | 7010 |  |  | -1912 | -1912 | -1893 | Critical Branch | Validation phase | 21 | NA | 0 |  |  | 405 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1030 | 7031 |  |  | 7010 |  |  | -1912 | -1912 | -1893 | Critical Branch | Validation phase | 21 | NA | 0 |  |  | 405 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1130 | 7031 |  |  | 7010 |  |  | -1912 | -1912 | -1893 | Critical Branch | Validation phase | 21 | NA | 0 |  |  | 405 |  |  |  | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1230 | 7452 |  |  | 7029 |  |  | -2408 | -2408 | -1986 | Critical Branch | Validation phase | 423 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6811 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1330 | 7452 |  |  | 7029 |  |  | -2408 | -2408 | -1986 | Critical Branch | Validation phase | 423 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6811 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1430 | 7452 |  |  | 7029 |  |  | -2408 | -2408 | -1986 | Critical Branch | Validation phase | 423 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6811 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1530 | 7019 |  |  | 6985 |  |  | -2172 | -2172 | -2138 | Critical Branch | Validation phase | 34 | NA | 0 |  |  | 404 |  | 6740 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1630 | 7019 |  |  | 6985 |  |  | -2172 | -2172 | -2138 | Critical Branch | Validation phase | 34 | NA | 0 |  |  | 404 |  | 6740 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250918 | September | 1730 | 7319 |  |  | 7005 |  |  | -2502 | -2502 | -2195 | Critical Branch | Validation phase | 314 | NA | 0 |  |  | 386 |  | 7040 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 1830 |  | 5071 | 467 |  | 5071 | 467 | -2721 | -2721 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 0 | 2721 |  |  | 296
20250918 | September | 1930 |  | 5071 | 467 |  | 5071 | 467 | -2721 | -2721 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 0 | 2721 |  |  | 296
20250918 | September | 2030 |  | 5071 | 467 |  | 5071 | 467 | -2721 | -2721 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 0 | 2721 |  |  | 296
20250918 | September | 2130 | 6903 |  |  | 6581 |  |  | -2143 | -2143 | -1821 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 380 |  | 6331 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 2230 | 6903 |  |  | 6581 |  |  | -2143 | -2143 | -1821 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 380 |  | 6331 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250918 | September | 2330 | 6303 |  |  | 5981 |  |  | -1532 | -1532 | -1210 | Critical Branch | Validation phase | 322 | NA | 0 |  |  | 367 |  | 5731 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0030 | 7163 |  |  | 6587 |  |  | -3457 | -3457 | -2881 | Critical Branch | Validation phase | 576 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6337 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0130 | 7163 |  |  | 6587 |  |  | -3457 | -3457 | -2881 | Critical Branch | Validation phase | 576 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6337 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0230 | 7163 |  |  | 6587 |  |  | -3457 | -3457 | -2881 | Critical Branch | Validation phase | 576 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6337 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0330 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 187 | NA | 0 |  |  | 407 |  | 6502 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0430 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 187 | NA | 0 |  |  | 407 |  | 6502 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0530 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 187 | NA | 0 |  |  | 407 |  | 6502 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0630 | 6939 |  |  | 6752 |  |  | -1115 | -1115 | -928 | Critical Branch | Validation phase | 187 | NA | 0 |  |  | 407 |  | 6502 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250919 | September | 0730 | 5557 |  |  | 5556 |  |  | -3420 | -3420 | -3419 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 313
20250919 | September | 0830 | 5557 |  |  | 5556 |  |  | -3420 | -3420 | -3419 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 313
20250919 | September | 0930 | 6352 |  |  | 6352 |  |  | -2360 | -2360 | -2360 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 363
20250919 | September | 1030 | 6352 |  |  | 6352 |  |  | -2360 | -2360 | -2360 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 363
20250919 | September | 1130 | 6352 |  |  | 6352 |  |  | -2360 | -2360 | -2360 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 363
20250919 | September | 1230 | 6121 |  |  | 5803 |  |  | -4297 | -4297 | -3979 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 348 |  | 5553 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250919 | September | 1330 | 6121 |  |  | 5803 |  |  | -4297 | -4297 | -3979 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 348 |  | 5553 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250919 | September | 1430 | 6121 |  |  | 5803 |  |  | -4297 | -4297 | -3979 | Critical Branch | Validation phase | 318 | NA | 0 |  |  | 348 |  | 5553 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1
20250919 | September | 1530 | 7170 |  |  | 6872 |  |  | -2979 | -2979 | -2681 | Critical Branch | Validation phase | 298 | NA | 0 |  |  | 413 |  | 6622 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1630 | 7170 |  |  | 6872 |  |  | -2979 | -2979 | -2681 | Critical Branch | Validation phase | 298 | NA | 0 |  |  | 413 |  | 6622 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1730 | 7470 |  |  | 7005 |  |  | -3314 | -3314 | -2849 | Critical Branch | Smoothing ramp | 465 | NA | 0 | Smoothing | Smoothing ramp | 414 |  | 6922 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1830 | 7650 |  |  | 5505 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2145 | NA | 0 |  |  | 425 |  | 5255 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 1930 | 7650 |  |  | 5505 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2145 | NA | 0 |  |  | 425 |  | 5255 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2030 | 7650 |  |  | 5505 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2145 | NA | 0 |  |  | 425 |  | 5255 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2130 | 7650 |  |  | 6581 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1069 | NA | 0 |  |  | 425 |  | 6331 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2230 | 7650 |  |  | 6581 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1069 | NA | 0 |  |  | 425 |  | 6331 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250919 | September | 2330 | 7050 |  |  | 5981 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1069 | NA | 0 |  |  | 415 |  | 5731 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0030 | 6903 |  |  | 6013 |  |  | -1829 | -1829 | -939 | Critical Branch | Validation phase | 890 | NA | 0 |  |  |  |  | 5763 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0130 | 6903 |  |  | 6013 |  |  | -1829 | -1829 | -939 | Critical Branch | Validation phase | 890 | NA | 0 |  |  |  |  | 5763 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0230 | 6903 |  |  | 6013 |  |  | -1829 | -1829 | -939 | Critical Branch | Validation phase | 890 | NA | 0 |  |  |  |  | 5763 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0330 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 828 | NA | 0 |  |  |  |  | 5726 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0430 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 828 | NA | 0 |  |  |  |  | 5726 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0530 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 828 | NA | 0 |  |  |  |  | 5726 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0630 | 6804 |  |  | 5976 |  |  | -1645 | -1645 | -817 | Critical Branch | Validation phase | 828 | NA | 0 |  |  |  |  | 5726 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0730 | 6657 |  |  | 5792 |  |  | -2001 | -2001 | -1136 | Critical Branch | Validation phase | 865 | NA | 0 |  |  |  |  | 5542 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 0830 | 6657 |  |  | 5792 |  |  | -2001 | -2001 | -1136 | Critical Branch | Validation phase | 865 | NA | 0 |  |  |  |  | 5542 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 1530 | 7217 |  |  | 6639 |  |  | -2026 | -2026 | -1448 | Critical Branch | Validation phase | 578 | NA | 0 |  |  |  |  | 6389 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250920 | September | 1630 | 7217 |  |  | 6639 |  |  | -2026 | -2026 | -1448 | Critical Branch | Validation phase | 578 | NA | 0 |  |  |  |  | 6389 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250920 | September | 1730 | 7517 |  |  | 5798 |  |  | -2348 | -2348 | -629 | Critical Branch | Smoothing ramp | 1719 | NA | 0 | Smoothing | Smoothing ramp |  |  | 6689 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 1830 | 5480 |  |  | 4298 |  |  | -2511 | -2511 | -1329 | TTC Selection - LTTC | Validation phase | 1182 | NA | 0 |  |  |  |  | 4048 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 1930 | 5480 |  |  | 4298 |  |  | -2511 | -2511 | -1329 | TTC Selection - LTTC | Validation phase | 1182 | NA | 0 |  |  |  |  | 4048 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2030 | 5480 |  |  | 4298 |  |  | -2511 | -2511 | -1329 | TTC Selection - LTTC | Validation phase | 1182 | NA | 0 |  |  |  |  | 4048 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2130 | 6491 |  |  | 5798 |  |  | -1397 | -1397 | -704 | Critical Branch | Smoothing ramp | 693 | NA | 0 | Smoothing | Smoothing ramp |  |  | 5877 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2230 | 6491 |  |  | 6127 |  |  | -1397 | -1397 | -1033 | Critical Branch | Validation phase | 364 | NA | 0 |  |  |  |  | 5877 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250920 | September | 2330 | 5891 |  |  | 5527 |  |  | -788 | -788 | -424 | Critical Branch | Validation phase | 364 | NA | 0 |  |  |  |  | 5277 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250921 | September | 0030 | 8275 |  |  | 7029 |  |  | -1193 | -1193 | 0 | Critical Branch | Validation phase | 1246 | NA | 1193 |  |  | 415 | Reduction because NTC over thermal limit on border | 6779 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0130 | 8275 |  |  | 7029 |  |  | -1193 | -1193 | 0 | Critical Branch | Validation phase | 1246 | NA | 1193 |  |  | 415 | Reduction because NTC over thermal limit on border | 6779 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0230 | 8275 |  |  | 7029 |  |  | -1193 | -1193 | 0 | Critical Branch | Validation phase | 1246 | NA | 1193 |  |  | 415 | Reduction because NTC over thermal limit on border | 6779 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0330 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 1412 | NA | 5364 |  |  | 415 | Reduction because NTC over thermal limit on border | 6670 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0430 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 1412 | NA | 5364 |  |  | 415 | Reduction because NTC over thermal limit on border | 6670 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0530 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 1412 | NA | 5364 |  |  | 415 | Reduction because NTC over thermal limit on border | 6670 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0630 | 8332 |  |  | 6920 |  |  | -5364 | -5364 | 0 | Critical Branch | Validation phase | 1412 | NA | 5364 |  |  | 415 | Reduction because NTC over thermal limit on border | 6670 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0730 | 8429 |  |  | 7050 |  |  | -5825 | -5825 | 0 | Critical Branch | Validation phase | 1379 | NA | 5825 |  |  | 415 | Reduction because NTC over thermal limit on border | 6943 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0830 | 8429 |  |  | 7050 |  |  | -5825 | -5825 | 0 | Critical Branch | Validation phase | 1379 | NA | 5825 |  |  | 415 | Reduction because NTC over thermal limit on border | 6943 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 0930 | 8114 |  |  | 6905 |  |  | -4185 | -4185 | 0 | Critical Branch | Validation phase | 1209 | NA | 4185 |  |  | 415 | Reduction because NTC over thermal limit on border | 6655 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1030 | 8114 |  |  | 6905 |  |  | -4185 | -4185 | 0 | Critical Branch | Validation phase | 1209 | NA | 4185 |  |  | 415 | Reduction because NTC over thermal limit on border | 6655 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1130 | 8114 |  |  | 6905 |  |  | -4185 | -4185 | 0 | Critical Branch | Validation phase | 1209 | NA | 4185 |  |  | 415 | Reduction because NTC over thermal limit on border | 6655 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1230 | 6018 |  |  | 6984 |  |  | -2573 | -2573 | 0 | Critical Branch | Critical Branch | -966 | NA | 2573 |  |  | 349
20250921 | September | 1330 | 6018 |  |  | 6984 |  |  | -2573 | -2573 | 0 | Critical Branch | Critical Branch | -966 | NA | 2573 |  |  | 349
20250921 | September | 1430 | 6018 |  |  | 6984 |  |  | -2573 | -2573 | 0 | Critical Branch | Critical Branch | -966 | NA | 2573 |  |  | 349
20250921 | September | 1530 | 7602 |  |  | 7050 |  |  | -3976 | -3976 | 0 | Critical Branch | Validation phase | 552 | NA | 3976 |  |  | 415 | Reduction because NTC over thermal limit on border | 6803 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1630 | 7602 |  |  | 7050 |  |  | -3976 | -3976 | 0 | Critical Branch | Validation phase | 552 | NA | 3976 |  |  | 415 | Reduction because NTC over thermal limit on border | 6803 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 1730 | 7802 |  |  | 7043 |  |  | -4179 | -4179 | 0 | Critical Branch | Validation phase | 759 | NA | 4179 |  |  | 393 |  | 6803 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250921 | September | 1830 | 5395 |  |  | 7135 |  |  | -2668 | -2668 | 0 | Critical Branch | Critical Branch | -1740 | NA | 2668 |  |  | 300
20250921 | September | 1930 | 5395 |  |  | 7135 |  |  | -2668 | -2668 | 0 | Critical Branch | Critical Branch | -1740 | NA | 2668 |  |  | 300
20250921 | September | 2030 | 5395 |  |  | 7135 |  |  | -2668 | -2668 | 0 | Critical Branch | Critical Branch | -1740 | NA | 2668 |  |  | 300
20250921 | September | 2130 | 7576 |  |  | 6687 |  |  | -3139 | -3139 | 0 | Critical Branch | Validation phase | 889 | NA | 3139 |  |  | 393 |  | 6437 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250921 | September | 2230 | 7576 |  |  | 6687 |  |  | -3139 | -3139 | 0 | Critical Branch | Validation phase | 889 | NA | 3139 |  |  | 415 | Reduction because NTC over thermal limit on border | 6437 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250921 | September | 2330 | 7576 |  |  | 6687 |  |  | -3139 | -3139 | 0 | Critical Branch | Validation phase | 889 | NA | 3139 |  |  | 415 | Reduction because NTC over thermal limit on border | 6437 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 0030 | 7363 |  |  | 7163 |  |  | -2390 | -2390 | -2190 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6913 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 0130 | 7363 |  |  | 7163 |  |  | -2390 | -2390 | -2190 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6913 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 0230 | 7363 |  |  | 7163 |  |  | -2390 | -2390 | -2190 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6913 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 0330 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 411
20250922 | September | 0430 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 411
20250922 | September | 0530 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 411
20250922 | September | 0630 | 7201 |  |  | 7200 |  |  | -1911 | -1911 | -1911 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 411
20250922 | September | 0730 | 6792 |  |  | 6791 |  |  | -1972 | -1972 | -1971 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 363
20250922 | September | 0830 | 5792 |  |  | 5792 |  |  | -861 | -861 | -861 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 354
20250922 | September | 0930 | 7378 |  |  | 6839 |  |  | -2195 | -2195 | -1671 | Critical Branch | Validation phase | 539 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6907 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1030 | 7378 |  |  | 6839 |  |  | -2195 | -2195 | -1671 | Critical Branch | Validation phase | 539 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6907 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1130 | 7378 |  |  | 6839 |  |  | -2195 | -2195 | -1671 | Critical Branch | Validation phase | 539 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 6907 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1230 | 7526 |  |  | 6897 |  |  | -2226 | -2226 | -1603 | Critical Branch | Validation phase | 629 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7019 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1330 | 7526 |  |  | 6897 |  |  | -2226 | -2226 | -1603 | Critical Branch | Validation phase | 629 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7019 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1430 | 7526 |  |  | 6897 |  |  | -2226 | -2226 | -1603 | Critical Branch | Validation phase | 629 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7019 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250922 | September | 1530 | 6062 |  |  | 6062 |  |  | -956 | -956 | -956 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 375
20250922 | September | 1630 | 7062 |  |  | 7062 |  |  | -2047 | -2047 | -2047 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 382
20250922 | September | 1730 | 7062 |  |  | 7062 |  |  | -2047 | -2047 | -2047 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 382
20250922 | September | 1830 | 6474 |  |  | 6133 |  |  | -2758 | -2758 | -2417 | Critical Branch | Validation phase | 341 | NA | 0 |  |  | 347 |  | 5883 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 1930 | 6474 |  |  | 6133 |  |  | -2758 | -2758 | -2417 | Critical Branch | Validation phase | 341 | NA | 0 |  |  | 347 |  | 5883 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2030 | 6474 |  |  | 6133 |  |  | -2758 | -2758 | -2417 | Critical Branch | Validation phase | 341 | NA | 0 |  |  | 347 |  | 5883 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2130 | 6727 |  |  | 5995 |  |  | -1790 | -1790 | -1058 | Critical Branch | Validation phase | 732 | NA | 0 |  |  | 362 |  | 5745 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2230 | 6727 |  |  | 5995 |  |  | -1790 | -1790 | -1058 | Critical Branch | Validation phase | 732 | NA | 0 |  |  | 362 |  | 5745 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250922 | September | 2330 | 6127 |  |  | 5395 |  |  | -1179 | -1179 | -447 | Critical Branch | Validation phase | 732 | NA | 0 |  |  | 348 |  | 5145 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250923 | September | 0030 | 7509 |  |  | 7098 |  |  | -1874 | -1874 | -1463 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6848 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0130 | 7509 |  |  | 7098 |  |  | -1874 | -1874 | -1463 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6848 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0230 | 7509 |  |  | 7098 |  |  | -1874 | -1874 | -1463 | Critical Branch | Validation phase | 411 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6848 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0330 | 8029 |  |  | 7416 |  |  | -2361 | -2361 | -1754 | Critical Branch | Validation phase | 613 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7180 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0430 | 8029 |  |  | 7416 |  |  | -2361 | -2361 | -1754 | Critical Branch | Validation phase | 613 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7180 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0530 | 8029 |  |  | 7416 |  |  | -2361 | -2361 | -1754 | Critical Branch | Validation phase | 613 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7180 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 0630 | 8029 |  |  | 6809 |  |  | -2361 | -2361 | -1149 | Critical Branch | Validation phase | 1220 | NA | 0 |  |  | 410 |  | 7180 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250923 | September | 0730 |  | 5302 | 101 |  | 5131 | 98 | -2382 | -2382 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 174 | 2382 |  |  | 298 |  | 5209 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 0830 |  | 5302 | 101 |  | 5131 | 98 | -2382 | -2382 | 0 | TTC Selection - LTTCImport | Validation phase | NA | 174 | 2382 |  |  | 298 |  | 5209 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 0930 | 7192 |  |  | 6809 |  |  | -2131 | -2131 | -1750 | Critical Branch | Critical Branch | 383 | NA | 0 |  |  | 385
20250923 | September | 1030 | 7192 |  |  | 7191 |  |  | -2131 | -2131 | -2130 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 389
20250923 | September | 1130 | 7192 |  |  | 7191 |  |  | -2131 | -2131 | -2130 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 389
20250923 | September | 1230 | 7646 |  |  | 7317 |  |  | -2087 | -2087 | -1758 | Critical Branch | Validation phase | 329 | NA | 0 |  |  | 416 |  | 7067 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 1330 | 7646 |  |  | 7317 |  |  | -2087 | -2087 | -1758 | Critical Branch | Validation phase | 329 | NA | 0 |  |  | 416 |  | 7067 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 1430 | 7646 |  |  | 7317 |  |  | -2087 | -2087 | -1758 | Critical Branch | Validation phase | 329 | NA | 0 |  |  | 416 |  | 7067 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250923 | September | 1530 | 7220 |  |  | 7220 |  |  | -902 | -902 | -902 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20250923 | September | 1630 | 7220 |  |  | 7220 |  |  | -902 | -902 | -902 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20250923 | September | 1730 | 7220 |  |  | 6789 |  |  | -902 | -902 | -473 | Critical Branch | Critical Branch | 431 | NA | 0 |  |  | 385
20250923 | September | 1830 |  | 5091 | 610 |  | 4820 | 560 | -2573 | -2573 | 0 | Critical Branch | Validation phase | NA | 321 | 2573 |  |  | 209 |  | 5310 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 1930 |  | 5091 | 610 |  | 4820 | 560 | -2573 | -2573 | 0 | Critical Branch | Validation phase | NA | 321 | 2573 |  |  | 209 |  | 5310 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 2030 |  | 5091 | 610 |  | 4820 | 560 | -2573 | -2573 | 0 | Critical Branch | Validation phase | NA | 321 | 2573 |  |  | 209 |  | 5310 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
20250923 | September | 2130 | 6757 |  |  | 6757 |  |  | -1892 | -1892 | -1892 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 364
20250923 | September | 2230 | 6757 |  |  | 6757 |  |  | -1892 | -1892 | -1892 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 364
20250923 | September | 2330 | 6157 |  |  | 6157 |  |  | -1282 | -1282 | -1282 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 350
20250924 | September | 0030 | 7522 |  |  | 7360 |  |  | -2047 | -2047 | -1889 | Critical Branch | Validation phase | 162 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7121 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 0130 | 7522 |  |  | 7360 |  |  | -2047 | -2047 | -1889 | Critical Branch | Validation phase | 162 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7121 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 0230 | 7522 |  |  | 7360 |  |  | -2047 | -2047 | -1889 | Critical Branch | Validation phase | 162 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7121 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 0330 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250924 | September | 0430 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250924 | September | 0530 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250924 | September | 0630 | 7092 |  |  | 7092 |  |  | -1390 | -1390 | -1390 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20250924 | September | 0730 | 5630 |  |  | 5629 |  |  | -1833 | -1833 | -1833 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 298
20250924 | September | 0830 | 5630 |  |  | 5629 |  |  | -1833 | -1833 | -1833 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 298
20250924 | September | 0930 | 7052 |  |  | 7000 |  |  | -1788 | -1788 | -1736 | Critical Branch | Validation phase | 52 | NA | 0 |  |  | 381 |  | 6750 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 1030 | 7052 |  |  | 7000 |  |  | -1788 | -1788 | -1736 | Critical Branch | Validation phase | 52 | NA | 0 |  |  | 381 |  | 6750 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 1130 | 7052 |  |  | 7000 |  |  | -1788 | -1788 | -1736 | Critical Branch | Validation phase | 52 | NA | 0 |  |  | 381 |  | 6750 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250924 | September | 1230 | 8058 |  |  | 7771 |  |  | -1484 | -1484 | -1108 | Critical Branch | Validation phase | 287 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7748 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250924 | September | 1330 | 8058 |  |  | 7771 |  |  | -1484 | -1484 | -1108 | Critical Branch | Validation phase | 287 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7748 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250924 | September | 1430 | 8058 |  |  | 7771 |  |  | -1484 | -1484 | -1108 | Critical Branch | Validation phase | 287 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7748 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250924 | September | 1530 | 7032 |  |  | 7032 |  |  | -1782 | -1782 | -1782 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 380
20250924 | September | 1630 | 7032 |  |  | 7032 |  |  | -1782 | -1782 | -1782 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 380
20250924 | September | 1730 | 7032 |  |  | 7032 |  |  | -1782 | -1782 | -1782 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 380
20250924 | September | 1830 |  | 6141 | 562 |  | 6140 | 562 | -2460 | -2460 | 0 | Critical Branch | Critical Branch | NA | 1 | 2460 |  |  | 356
20250924 | September | 1930 |  | 6141 | 562 |  | 6140 | 562 | -2460 | -2460 | 0 | Critical Branch | Critical Branch | NA | 1 | 2460 |  |  | 356
20250924 | September | 2030 |  | 6141 | 562 |  | 6140 | 562 | -2460 | -2460 | 0 | Critical Branch | Critical Branch | NA | 1 | 2460 |  |  | 356
20250924 | September | 2130 | 7397 |  |  | 7396 |  |  | -1806 | -1806 | -1805 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 401
20250924 | September | 2230 | 7397 |  |  | 7396 |  |  | -1806 | -1806 | -1805 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 401
20250924 | September | 2330 | 6797 |  |  | 6797 |  |  | -1194 | -1194 | -1194 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 390
20250925 | September | 0030 | 7358 |  |  | 7200 |  |  | -1491 | -1491 | -1333 | Critical Branch | Validation phase | 158 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0130 | 7358 |  |  | 7200 |  |  | -1491 | -1491 | -1333 | Critical Branch | Validation phase | 158 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0230 | 7358 |  |  | 7200 |  |  | -1491 | -1491 | -1333 | Critical Branch | Validation phase | 158 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0330 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 96 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0430 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 96 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0530 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 96 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0630 | 7296 |  |  | 7200 |  |  | -1283 | -1283 | -1187 | Critical Branch | Validation phase | 96 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0730 | 6822 |  |  | 6822 |  |  | -2213 | -2213 | -2213 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 368 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0830 | 6822 |  |  | 6822 |  |  | -2213 | -2213 | -2213 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 368 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 0930 | 7043 |  |  | 6572 |  |  | -1901 | -1901 | -1407 | Critical Branch | Validation phase | 471 | NA | 0 |  |  | 380 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 1900 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1
20250925 | September | 1030 | 7043 |  |  | 6572 |  |  | -1901 | -1901 | -1407 | Critical Branch | Validation phase | 471 | NA | 0 |  |  | 380 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 1900 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1
20250925 | September | 1130 | 7043 |  |  | 6572 |  |  | -1901 | -1901 | -1407 | Critical Branch | Validation phase | 471 | NA | 0 |  |  | 380 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 1900 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1
20250925 | September | 1230 | 7121 |  |  | 7121 |  |  | -1846 | -1846 | -1846 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 385 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 1330 | 7121 |  |  | 7121 |  |  | -1846 | -1846 | -1846 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 385 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 1430 | 7121 |  |  | 7121 |  |  | -1846 | -1846 | -1846 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 385 |  | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250925 | September | 1530 | 8033 |  |  | 7656 |  |  | -1290 | -1290 | -853 | Critical Branch | Validation phase | 377 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1630 | 8033 |  |  | 7656 |  |  | -1290 | -1290 | -853 | Critical Branch | Validation phase | 377 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1730 | 8033 |  |  | 7656 |  |  | -1290 | -1290 | -853 | Critical Branch | Validation phase | 377 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1830 |  | 7495 | 723 |  | 7085 | 699 | -3568 | -3568 | 0 | Critical Branch | Validation phase | NA | 434 | 3568 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 1930 |  | 7495 | 723 |  | 7085 | 699 | -3568 | -3568 | 0 | Critical Branch | Validation phase | NA | 434 | 3568 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2030 |  | 7495 | 723 |  | 7085 | 699 | -3568 | -3568 | 0 | Critical Branch | Validation phase | NA | 434 | 3568 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2130 | 8172 |  |  | 7656 |  |  | -960 | -960 | -395 | Critical Branch | Validation phase | 516 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2230 | 8172 |  |  | 7656 |  |  | -960 | -960 | -395 | Critical Branch | Validation phase | 516 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250925 | September | 2330 | 7572 |  |  | 7200 |  |  | -348 | -348 | 24 | Critical Branch | Validation phase | 372 | NA | 396 |  |  | 415 | Reduction because NTC over thermal limit on border | 6950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2500 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2
20250926 | September | 0030 | 8298 |  |  | 8182 |  |  | -1345 | -1345 | -1245 | Critical Branch | Validation phase | 116 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7997 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250926 | September | 0130 | 8298 |  |  | 8182 |  |  | -1345 | -1345 | -1245 | Critical Branch | Validation phase | 116 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7997 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250926 | September | 0230 | 8298 |  |  | 8182 |  |  | -1345 | -1345 | -1245 | Critical Branch | Validation phase | 116 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7997 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250926 | September | 0330 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 51 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250926 | September | 0430 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 51 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250926 | September | 0530 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 51 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250926 | September | 0630 | 8027 |  |  | 7976 |  |  | -5465 | -5465 | -5400 | Critical Branch | Critical Branch | 51 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border
20250926 | September | 0730 | 7913 |  |  | 7906 |  |  | -2396 | -2396 | -2390 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 0830 | 7713 |  |  | 7706 |  |  | -2172 | -2172 | -2166 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 0930 | 7938 |  |  | 7918 |  |  | -2150 | -2150 | -2132 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 1030 | 7938 |  |  | 7918 |  |  | -2150 | -2150 | -2132 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 1130 | 7938 |  |  | 7918 |  |  | -2150 | -2150 | -2132 | Critical Branch | Critical Branch | 20 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 1230 | 8058 |  |  | 8031 |  |  | -1355 | -1355 | -1331 | Critical Branch | Critical Branch | 27 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 1330 | 8058 |  |  | 8031 |  |  | -1355 | -1355 | -1331 | Critical Branch | Critical Branch | 27 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 1430 | 8058 |  |  | 7684 |  |  | -1355 | -1355 | -984 | Critical Branch | Critical Branch | 374 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border
20250926 | September | 1530 | 6184 |  |  | 6184 |  |  | 200 | 104 | 96 | Minimum Margin | Minimum Margin | 0 | NA | 88 |  |  | 340
20250926 | September | 1630 | 7530 |  |  | 7530 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 349
20250926 | September | 1730 | 7530 |  |  | 7530 |  |  | -1572 | -1572 | -1572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 349
20250926 | September | 1830 |  | 8838 | 716 |  | 8606 | 716 | -3871 | -3871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 232 | 3871 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250926 | September | 1930 |  | 8838 | 716 |  | 8606 | 716 | -3871 | -3871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 232 | 3871 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250926 | September | 2030 |  | 8838 | 716 |  | 8606 | 716 | -3871 | -3871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 232 | 3871 |  |  | 425 | Reduction because NTC over thermal limit on border |  |  | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250926 | September | 2130 | 9058 |  |  | 9058 |  |  | -2998 | -2998 | -2998 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 425
20250926 | September | 2230 | 9058 |  |  | 9058 |  |  | -2998 | -2998 | -2998 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 425
20250926 | September | 2330 | 8458 |  |  | 8458 |  |  | -2380 | -2380 | -2380 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 415
20250927 | September | 0030 | 9209 |  |  | 8446 |  |  | -934 | -934 | -171 | Critical Branch | Validation phase | NA | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8196 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 0130 | 9209 |  |  | 8446 |  |  | -934 | -934 | -171 | Critical Branch | Validation phase | 763 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8196 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 0230 | 9209 |  |  | 8446 |  |  | -934 | -934 | -171 | Critical Branch | Validation phase | 763 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8196 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 0330 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 485 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8321 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0430 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 485 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8321 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0530 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 485 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8321 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0630 | 9050 |  |  | 8565 |  |  | -6189 | -6189 | -5702 | Critical Branch | Validation phase | 485 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8321 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0730 | 8766 |  |  | 8398 |  |  | -982 | -982 | -614 | Critical Branch | Validation phase | 368 | NA | 0 |  |  | 410 |  | 8148 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0830 | 7966 |  |  | 7598 |  |  | -102 | -102 | 266 | Critical Branch | Validation phase | 368 | NA | 634 |  |  | 409 |  | 7348 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA
20250927 | September | 0930 | 8053 |  |  | 7284 |  |  | -2656 | -2656 | -1887 | Critical Branch | Validation phase | 769 | NA | 0 |  |  | 414 |  | 7034 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1030 | 8053 |  |  | 7284 |  |  | -2656 | -2656 | -1887 | Critical Branch | Validation phase | 769 | NA | 0 |  |  | 414 |  | 7034 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1130 | 8053 |  |  | 7284 |  |  | -2656 | -2656 | -1887 | Critical Branch | Validation phase | 769 | NA | 0 |  |  | 414 |  | 7034 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1230 | 7550 |  |  | 7331 |  |  | -1824 | -1824 | -1605 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 386 |  | 7081 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1330 | 7550 |  |  | 7331 |  |  | -1824 | -1824 | -1605 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 386 |  | 7081 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1430 | 7550 |  |  | 7331 |  |  | -1824 | -1824 | -1605 | Critical Branch | Validation phase | 219 | NA | 0 |  |  | 386 |  | 7081 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia
20250927 | September | 1530 | 8257 |  |  | 7819 |  |  | -5633 | -5633 | -5195 | Critical Branch | Validation phase | 438 | NA | 0 |  |  | 425 |  | 7569 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250927 | September | 1630 | 8257 |  |  | 7819 |  |  | -5633 | -5633 | -5195 | Critical Branch | Validation phase | 438 | NA | 0 |  |  | 425 |  | 7569 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250927 | September | 1730 | 9057 |  |  | 8619 |  |  | -6428 | -6428 | -5990 | Critical Branch | Validation phase | 438 | NA | 0 |  |  | 425 |  | 8369 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20250927 | September | 1830 |  | 8537 | 928 |  | 8239 | 907 | -2445 | -2445 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 319 | 2445 |  |  | 213 | Reduction because NTC over thermal limit on border |  |  | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 1930 |  | 8537 | 928 |  | 8239 | 907 | -2445 | -2445 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 319 | 2445 |  |  | 213 | Reduction because NTC over thermal limit on border |  |  | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2030 |  | 8537 | 928 |  | 8239 | 907 | -2445 | -2445 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 319 | 2445 |  |  | 213 | Reduction because NTC over thermal limit on border |  |  | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2130 | 9217 |  |  | 8295 |  |  | -2545 | -2545 | -1623 | Critical Branch | Validation phase | 922 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8045 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2230 | 9217 |  |  | 8295 |  |  | -2545 | -2545 | -1623 | Critical Branch | Validation phase | 922 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8045 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3800 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250927 | September | 2330 | 8617 |  |  | 7695 |  |  | -1935 | -1935 | -1013 | Critical Branch | Validation phase | 922 | 9630 | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 7445 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250928 | September | 0030 | 9346 |  |  | 8626 |  |  | -1418 | -1418 | -701 | Critical Branch | Validation phase | 720 | 10044 | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8591 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0130 | 9346 |  |  | 8626 |  |  | -1418 | -1418 | -701 | Critical Branch | Validation phase | 720 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8591 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0230 | 9346 |  |  | 8626 |  |  | -1418 | -1418 | -701 | Critical Branch | Validation phase | 720 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8591 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0330 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 846 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8282 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0430 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 846 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8282 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0530 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 846 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8282 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0630 | 9319 |  |  | 8473 |  |  | -4189 | -4189 | -3347 | Critical Branch | Validation phase | 846 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8282 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 0730 | 8078 |  |  | 8077 |  |  | -6816 | -6816 | -6816 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 395
20250928 | September | 0830 | 8078 |  |  | 7750 |  |  | -6816 | -6816 | -6485 | Critical Branch | Critical Branch | 328 | NA | 0 |  |  | 380
20250928 | September | 0930 | 6280 |  |  | 6250 |  |  | -6797 | -6797 | -6767 | TTC Selection - LTTC | Validation phase | 30 | NA | 0 |  |  | 301 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250928 | September | 1030 | 6280 |  |  | 6250 |  |  | -6797 | -6797 | -6767 | TTC Selection - LTTC | Validation phase | 30 | NA | 0 |  |  | 301 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250928 | September | 1130 | 6280 |  |  | 6250 |  |  | -6797 | -6797 | -6767 | TTC Selection - LTTC | Validation phase | 30 | NA | 0 |  |  | 301 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250928 | September | 1230 | 6280 |  |  | 6279 |  |  | -5763 | -5763 | -5762 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 301
20250928 | September | 1330 | 6280 |  |  | 6279 |  |  | -5763 | -5763 | -5762 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 301
20250928 | September | 1430 | 6280 |  |  | 6279 |  |  | -5763 | -5763 | -5762 | TTC Selection - LTTC | TTC Selection - LTTC | 1 | NA | 0 |  |  | 301
20250928 | September | 1530 |  | 6956 | 601 |  | 6956 | 601 | -5043 | -5043 | 0 | Critical Branch | Critical Branch | NA | 0 | 5043 |  |  | 361
20250928 | September | 1630 |  | 6956 | 601 |  | 6956 | 601 | -5043 | -5043 | 0 | Critical Branch | Critical Branch | NA | 0 | 5043 |  |  | 361
20250928 | September | 1730 |  | 6956 | 601 |  | 6956 | 601 | -5043 | -5043 | 0 | Critical Branch | Critical Branch | NA | 0 | 5043 |  |  | 361
20250928 | September | 1830 |  | 9142 | 801 |  | 8360 | 781 | -5355 | -5355 | 0 | Critical Branch | Validation phase | NA | 802 | 5355 |  |  | 415 | Reduction because NTC over thermal limit on border | 9201 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 1930 |  | 9142 | 801 |  | 8360 | 781 | -5355 | -5355 | 0 | Critical Branch | Validation phase | NA | 802 | 5355 |  |  | 415 | Reduction because NTC over thermal limit on border | 9201 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2030 |  | 9142 | 801 |  | 8360 | 781 | -5355 | -5355 | 0 | Critical Branch | Validation phase | NA | 802 | 5355 |  |  | 415 | Reduction because NTC over thermal limit on border | 9201 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2130 | 9661 |  |  | 8842 |  |  | -2755 | -2755 | -1945 | Critical Branch | Validation phase | 819 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 9029 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2230 | 9661 |  |  | 8842 |  |  | -2755 | -2755 | -1945 | Critical Branch | Validation phase | 819 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 9029 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250928 | September | 2330 | 9661 |  |  | 8842 |  |  | -2755 | -2755 | -1945 | Critical Branch | Validation phase | 819 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 9029 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0030 | 9061 |  |  | 8433 |  |  | -2324 | -2324 | -1696 | Critical Branch | Validation phase | 628 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0130 | 9061 |  |  | 8433 |  |  | -2324 | -2324 | -1696 | Critical Branch | Validation phase | 628 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0230 | 9061 |  |  | 8433 |  |  | -2324 | -2324 | -1696 | Critical Branch | Validation phase | 628 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0330 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 766 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0430 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 766 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0530 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 766 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0630 | 9199 |  |  | 8433 |  |  | -1691 | -1691 | -929 | Critical Branch | Validation phase | 766 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 0730 |  | 7848 | 610 |  | 7848 | 610 | -2298 | -2298 | 0 | Critical Branch | Validation phase | NA | 0 | 2298 |  |  | 391 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 0830 |  | 7848 | 610 |  | 7848 | 610 | -2298 | -2298 | 0 | Critical Branch | Validation phase | NA | 0 | 2298 |  |  | 391 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 0930 | 8490 |  |  | 8490 |  |  | -3441 | -3441 | -3441 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 397 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 1030 | 8490 |  |  | 8490 |  |  | -3441 | -3441 | -3441 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 397 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 1130 | 8490 |  |  | 8490 |  |  | -3441 | -3441 | -3441 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 397 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 1230 | 9367 |  |  | 8806 |  |  | -2313 | -2313 | -1797 | Critical Branch | Validation phase | 561 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1330 | 9367 |  |  | 8806 |  |  | -2313 | -2313 | -1797 | Critical Branch | Validation phase | 561 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1430 | 9367 |  |  | 8806 |  |  | -2313 | -2313 | -1797 | Critical Branch | Validation phase | 561 | NA | 0 |  |  | 425 | Reduction because NTC over thermal limit on border | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1530 |  | 8141 | 629 |  | 8061 | 629 | -2209 | -2209 | 0 | Critical Branch | Validation phase | NA | 80 | 2209 |  |  | 406 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1630 |  | 8141 | 629 |  | 8061 | 629 | -2209 | -2209 | 0 | Critical Branch | Validation phase | NA | 80 | 2209 |  |  | 406 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1730 |  | 8141 | 629 |  | 8061 | 629 | -2209 | -2209 | 0 | Critical Branch | Validation phase | NA | 80 | 2209 |  |  | 406 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1830 |  | 7939 | 897 |  | 7743 | 882 | -3533 | -3533 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 211 | 3533 |  |  | 197 | Reduction because NTC over thermal limit on border | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 1930 |  | 7939 | 897 |  | 7743 | 882 | -3533 | -3533 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 211 | 3533 |  |  | 197 | Reduction because NTC over thermal limit on border | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 2030 |  | 7939 | 897 |  | 7743 | 882 | -3533 | -3533 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 211 | 3533 |  |  | 197 | Reduction because NTC over thermal limit on border | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250929 | September | 2130 | 8366 |  |  | 8366 |  |  | -1576 | -1576 | -1576 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 391 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 2230 | 8366 |  |  | 8366 |  |  | -1576 | -1576 | -1576 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 391 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250929 | September | 2330 | 7766 |  |  | 7766 |  |  | -966 | -966 | -965 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 379 |  | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0030 | 9072 |  |  | 8433 |  |  | -3400 | -3400 | -2761 | Critical Branch | Validation phase | 639 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 0130 | 9072 |  |  | 8433 |  |  | -3400 | -3400 | -2761 | Critical Branch | Validation phase | 639 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 0230 | 9072 |  |  | 8433 |  |  | -3400 | -3400 | -2761 | Critical Branch | Validation phase | 639 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 0330 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 204 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0430 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 204 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0530 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 204 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0630 | 8654 |  |  | 8450 |  |  | -4756 | -4756 | -4552 | Critical Branch | Validation phase | 204 | NA | 0 |  |  | 415 | Reduction because NTC over thermal limit on border | 8200 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0730 |  | 6841 | 684 |  | 6841 | 683 | -5646 | -5646 | 0 | Critical Branch | Validation phase | NA | 1 | 5646 |  |  | 344 |  | 8800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0830 |  | 6841 | 664 |  | 6841 | 664 | -5615 | -5615 | 0 | Critical Branch | Validation phase | NA | 0 | 5615 |  |  | 292 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 0930 | 9241 |  |  | 8746 |  |  | -2853 | -2853 | -2354 | Critical Branch | Validation phase | 495 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1030 | 9241 |  |  | 8746 |  |  | -2853 | -2853 | -2354 | Critical Branch | Validation phase | 495 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1130 | 9241 |  |  | 8746 |  |  | -2853 | -2853 | -2354 | Critical Branch | Validation phase | 495 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1230 | 9612 |  |  | 8746 |  |  | -6332 | -6332 | -5379 | Critical Branch | Validation phase | 866 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1330 | 9612 |  |  | 8746 |  |  | -6332 | -6332 | -5379 | Critical Branch | Validation phase | 866 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1430 | 9612 |  |  | 8746 |  |  | -6332 | -6332 | -5379 | Critical Branch | Validation phase | 866 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1530 |  | 7903 | 770 |  | 7727 | 765 | -3609 | -3609 | 0 | Critical Branch | Validation phase | NA | 181 | 3609 |  |  | 356 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1630 |  | 7903 | 770 |  | 7727 | 498 | -3609 | -3609 | 0 | Critical Branch | Validation phase | NA | 448 | 3609 |  |  | 356 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1730 |  | 7903 | 770 |  | 7727 | 235 | -3609 | -3609 | 0 | Critical Branch | Validation phase | NA | 711 | 3609 |  |  | 356 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 1830 |  | 7528 | 733 |  | 7528 | 235 | -5528 | -5528 | 0 | Critical Branch | Validation phase | NA | 498 | 5528 |  |  | 184 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 1930 |  | 7528 | 733 |  | 7528 | 235 | -5528 | -5528 | 0 | Critical Branch | Validation phase | NA | 498 | 5528 |  |  | 184 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 2030 |  | 7528 | 733 |  | 7528 | 235 | -5528 | -5528 | 0 | Critical Branch | Validation phase | NA | 498 | 5528 |  |  | 184 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250930 | September | 2130 |  | 8446 | 658 |  | 8181 | 184 | -5193 | -5193 | 0 | Critical Branch | Validation phase | NA | 739 | 5193 |  |  | 365 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 2230 |  | 8446 | 658 |  | 8181 | 417 | -5193 | -5193 | 0 | Critical Branch | Validation phase | NA | 506 | 5193 |  |  | 365 |  | 8740 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 3600 | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV
20250930 | September | 2330 |  | 7866 | 683 |  | 7865 | 610 | -4560 | -4560 | 0 | Critical Branch | Validation phase | NA | 74 | 4560 |  |  | 355 |  | 8140 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.

## DA FLAGS processing
FLAGS processing
TSO | Long description | Short | Type | # of TS | CB | CO
AT | Reduction because NTC over thermal limit on border | Reduction because NTC over thermal limit on border | NTC over thermal limit | 1446
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 429 | 220kV Riddes - Valpelline [DIR] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT Issues | 192
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 87 | 380kV Bulciago - Soazza [DIR] [CH], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 65 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 Pradella-Robbia + Filisur-Robbia
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | Overload | 58 | 220kV Riddes - Valpelline [DIR] [CH], | -1 VILLARODIN-VENAUS
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 55 | 380kV Bulciago - Soazza [DIR] [CH], | -2 Pradella-Robbia + Filisur-Robbia
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 54 | 220kV Avise - Riddes [OPP] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 50 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-VENAUS | Overload | 21 | 220kV Avise - Riddes [OPP] [CH], | -1 VILLARODIN-VENAUS
CH | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 21 | 380kV Sils - Soazza [DIR], | -2 Pradella-Robbia + Filisur-Robbia
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | Overload | 31 | 380kV Fiorano-Robbia [DIR][IT], | 80KV GORLAGO-ROBBIA
CH | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | Overload | 11 | 220kV Pressy-Vallorcine [OPP] [CH], | -1 BOIS TOLLOT-ROMANEL
CH | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA | CNE: 380kV Filisur - Robbia [DIR], C: 380KV SILS-SOAZZA | Overload | 11 | 380kV Filisur - Robbia [DIR], | 80KV SILS-SOAZZA
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | Overload | 9 | 220kV Riddes - Valpelline [DIR] [CH], | -1 AVISE-RIDDES
CH | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | Overload | 9 | 380kV Filisur - Robbia [DIR], | -1 PRADELLA-ROBBIA
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 9 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | No calculation has been done | No calculation has been done | Not Specified | 9
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ | Overload | 6 | 220kV Riddes - Valpelline [DIR] [CH], | -1 VILLARODIN-PRAZ
CH | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1 | CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1 | Overload | 6 | 380kV Pradella-Nauders 2 [OPP] [CH], | -1 PRADELLA-NAUDERS 1
CH | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 6 | 380kV Sils - Soazza [DIR], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 5 | 220kV Riddes - Valpelline [DIR] [CH],
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ | CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VILLARODIN-PRAZ | Overload | 4 | 220kV Avise - Riddes [OPP] [CH],
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 4 | 380kV Fiorano-Robbia [DIR][IT],
CH | Missing CNEC in CC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 3 | 220kV Avise - Riddes [OPP] [CH],
CH | Missing CNEC in CC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 3 | 220kV Riddes - Valpelline [DIR] [CH],
CH | Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | Overload | 3 | 380kV Bulciago - Soazza [DIR] [CH],
CH | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | Overload | 6 | 380kV Fiorano-Robbia [DIR][IT],
FR | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 | Outage | 223
FR | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1 | Planned outage of Albertville-Rondissonne 1&2 and limitation on PISA 1 | Outage | 58
FR | Unplanned outage MERY VIELMOULIN 1 | Unplanned outage MERY VIELMOULIN 1 | Outage | 23
FR | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV | Outage - Outage of Bus Bar 2.1 at GENISSIAT 400kV | Outage | 54
FR | Planned outage Venaus Villarodin 400kV | Planned outage Venaus Villarodin 400kV | Outage | 16
FR | Planned outage on Chaffard-Grande Ile 2 | Planned outage on Chaffard-Grande Ile 2 | Outage | 6
FR | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT] | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR][IT] | Overload | 4 | #VALUE!
FR | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1 | Planned Outage of GRANDE ILE - PIOSSASCO 1 & 2 + Essai fil 1 | Outage | 3
FR | Testing of HVDC cables imported from Italy to France | Testing of HVDC cables imported from Italy to France | Outage | 2
IT | Forecasted Security Violations | Forecasted Security Violations | Tense Situation | 39
IT | Outage of HVDC FIL link 1 and link 2 | Outage of HVDC FIL link 1 and link 2 | Outage | 24
IT | Secure Value | Secure Value | Not Specified | 7
SI | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | Overload | 70 | 400 kV Divaca-Redipuglia,
Smoothing | Smoothing ramp | Smoothing ramp | Smoothing | 25

## ID Full Results Data 2025Q3 (hidden)
ID results
|  |  | TTC Adjustment |  |  | TTC Validated |  |  | ANTC |  |  | LimitedBy | [8 empty] | AT | AT | AT | AT | AT | AT | CH | CH | CH | CH | CH | CH | FR | FR | FR | FR | FR | FR | SI | SI | SI | SI | SI | SI | IT | IT | IT | IT | IT | IT
Business day | Month | Timestamp | TTC_Full_Import | TTCImport | TTCExport | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | 70% red | TTCRed_Import | TTCRed_Transit_Import | TTCRed_Transit_Export | TTRed_Transit | TTC and 70% red | FLAG | Bilateral - MNII | MNII | Reason | Bilateral - MIEC | MNIE | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason
2025-09-01 | September | 1230 | 6531 |  |  | 6524 |  |  | -1640 | -1640 | -1635 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 362 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-01 | September | 1330 | 6531 |  |  | 6524 |  |  | -1640 | -1640 | -1635 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 362 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-01 | September | 1430 | 6531 |  |  | 6530 |  |  | -1640 | -1640 | -1638 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 140 | None | None | 368 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 1530 | 6569 |  |  | 6569 |  |  | -749 | -749 | -749 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 371 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 1630 | 6569 |  |  | 6569 |  |  | -749 | -749 | -749 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 371 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 1730 | 6569 |  |  | 6569 |  |  | -749 | -749 | -749 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 371 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 1830 |  | 4588 | 688 |  | 4550 | 605 | -2793 | -2793 | -2793 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 38 | 83 | 121 | 0 | 1 | 114 | None | None | 292 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 3747 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 1930 |  | 4601 | 714 |  | 4550 | 658 | -2789 | -2789 | -2789 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 51 | 56 | 107 | 0 | 1 | 140 | None | None | 136 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 3669 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 2030 |  | 4601 | 714 |  | 4550 | 676 | -2789 | -2789 | -2789 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 51 | 38 | 89 | 0 | 1 | 140 | None | None | 136 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 3839 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 2130 | 5098 |  |  | 5098 |  |  | -3519 | -3519 | -3519 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 324 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 2230 | 5619 |  |  | 5619 |  |  | -3770 | -3770 | -3770 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 140 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-01 | September | 2330 | 5203 |  |  | 5203 |  |  | -3269 | -3269 | -3269 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 307 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1230 | 6526 |  |  | 6316 |  |  | 689 | 210 | 689 | Minimum Margin | TTC Validation phase - bilateral reduction | 479 | 210 | NA | NA | NA | 210 | 1 | 140 | None | None | 368 | None | None | None | None | None | None | None | None | None | 6064 | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1330 | 6496 |  |  | 6286 |  |  | 710 | 210 | 710 | Minimum Margin | TTC Validation phase - bilateral reduction | 500 | 210 | NA | NA | NA | 210 | 1 | 140 | None | None | 366 | None | None | None | None | None | None | None | None | None | 6035 | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1430 | 6496 |  |  | 6286 |  |  | 710 | 210 | 710 | Minimum Margin | TTC Validation phase - bilateral reduction | 500 | 210 | NA | NA | NA | 210 | 1 | 140 | None | None | 366 | None | None | None | None | None | None | None | None | None | 6035 | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1530 | 6807 |  |  | 6308 |  |  | -2749 | -2749 | -2096 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 499 | NA | NA | NA | 0 | 1 | 140 | None | None | 385 | None | None | None | None | None | None | None | None | 1900 | None | Bilateral - Test GRANDE ILE PIOSSASCO 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1630 | 6807 |  |  | 6307 |  |  | -2749 | -2749 | -2096 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 500 | NA | NA | NA | 0 | 1 | 140 | None | None | 385 | None | None | None | 6507 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 1900 | None | Bilateral - Test GRANDE ILE PIOSSASCO 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1730 | 6807 |  |  | 5460 |  |  | -2750 | -2750 | -1920 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1347 | NA | NA | NA | 0 | 1 | 140 | None | None | 385 | None | None | None | 5210 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 1900 | None | Bilateral - Test GRANDE ILE PIOSSASCO 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-02 | September | 1830 |  | 5666 | 785 |  | 4477 | 683 | -3656 | -3656 | -3656 | Critical Branch | ID schedules | 0 | NA | 1189 | 102 | 1291 | 0 | 1 | 131 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -99 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 4674 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-02 | September | 1930 |  | 5666 | 785 |  | 4477 | 728 | -3656 | -3656 | -3656 | Critical Branch | ID schedules | 0 | NA | 1189 | 57 | 1246 | 0 | 1 | 131 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -99 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5028 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-02 | September | 2030 |  | 5666 | 785 |  | 4461 | 724 | -3656 | -3656 | -3656 | Critical Branch | ID schedules | 0 | NA | 1205 | 61 | 1266 | 0 | 1 | 131 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -99 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 4998 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-02 | September | 2130 |  | 4355 | 505 |  | 4276 | 545 | -3243 | -3243 | -3243 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 79 | -40 | 39 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 227 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 3626 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-02 | September | 2230 |  | 4433 | 56 |  | 4321 | 56 | -3305 | -3305 | -3305 | ID schedules | ID schedules | 0 | NA | 112 | 0 | 112 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 276 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 2905 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-02 | September | 2330 |  | 3829 | 32 |  | 3761 | 32 | -2669 | -2669 | -2669 | ID schedules | ID schedules | 0 | NA | 68 | 0 | 68 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 256 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-03 | September | 1230 | 7543 |  |  | 7537 |  |  | -3765 | -3765 | -3760 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1330 | 7543 |  |  | 7450 |  |  | -3765 | -3765 | -3672 | Critical Branch | Validation phase | 0 | 93 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | 7200 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1430 | 7543 |  |  | 7537 |  |  | -3765 | -3765 | -3760 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1530 | 7289 |  |  | 7289 |  |  | -4024 | -4024 | -4022 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1630 | 7289 |  |  | 7289 |  |  | -4024 | -4024 | -4022 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1730 | 7289 |  |  | 7003 |  |  | -4024 | -4024 | -3868 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 286 | NA | NA | NA | 0 | 1 | 140 | None | None | 415 | None | None | None | 6753 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1830 |  | 6416 | 857 |  | 6202 | 852 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 214 | 5 | 219 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 384 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 1930 |  | 6416 | 857 |  | 6096 | 816 | 0 | 0 | 0 | GSK Limitation | Validation phase | 0 | NA | 320 | 41 | 361 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 194 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5906 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 2030 |  | 6416 | 857 |  | 6242 | 852 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 174 | 5 | 179 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 194 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-03 | September | 2130 | 7680 |  |  | 6169 |  |  | -2348 | -2348 | -976 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1511 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 408 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-03 | September | 2230 | 7680 |  |  | 6630 |  |  | -2348 | -2348 | -1244 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1050 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 408 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7412 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | 2500 | None | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-03 | September | 2330 | 7080 |  |  | 5935 |  |  | -1737 | -1737 | -621 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1145 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1230 | 7349 |  |  | 7141 |  |  | 933 | 208 | 933 | Minimum Margin | TTC Validation phase - bilateral reduction | 725 | 208 | NA | NA | NA | 208 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 6890 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1330 | 7365 |  |  | 7157 |  |  | 922 | 208 | 922 | Minimum Margin | TTC Validation phase - bilateral reduction | 714 | 208 | NA | NA | NA | 208 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 6905 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1430 | 7564 |  |  | 7356 |  |  | 784 | 208 | 784 | Minimum Margin | TTC Validation phase - bilateral reduction | 576 | 208 | NA | NA | NA | 208 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 7105 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1530 | 7396 |  |  | 7396 |  |  | -4316 | -4316 | -4316 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 422 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1630 | 7331 |  |  | 7331 |  |  | -4248 | -4248 | -4248 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 422 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1730 | 7046 |  |  | 7067 |  |  | -3962 | -3962 | -3974 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -21 | NA | NA | NA | 0 | 1 | 140 | None | None | 422 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-04 | September | 1830 |  | 5917 | 798 |  | 5831 | 798 | -5140 | -5140 | -5140 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 0 | 1 | 134 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-04 | September | 1930 |  | 5917 | 798 |  | 5831 | 798 | -5140 | -5140 | -5140 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 0 | 1 | 134 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-04 | September | 2030 |  | 5917 | 798 |  | 5831 | 798 | -5140 | -5140 | -5140 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 0 | 1 | 134 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-04 | September | 2130 |  | 6160 | 658 |  | 6264 | 658 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -104 | 0 | -104 | 0 | 1 | 140 | None | None | 391 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-04 | September | 2230 |  | 6114 | 551 |  | 6233 | 551 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -119 | 0 | -119 | 0 | 1 | 139 | None | None | 408 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-04 | September | 2330 |  | 6060 | -3 |  | 6060 | -3 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 159 | None | None | 396 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-05 | September | 1230 | 6755 |  |  | 6755 |  |  | -3223 | -3223 | -3223 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-05 | September | 1330 | 6755 |  |  | 6755 |  |  | -3223 | -3223 | -3223 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-05 | September | 1430 | 6755 |  |  | 6755 |  |  | -3223 | -3223 | -3223 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-05 | September | 1530 | 7391 |  |  | 7188 |  |  | 1484 | 203 | 1484 | Minimum Margin | TTC Validation phase - bilateral reduction | 1281 | 203 | NA | NA | NA | 203 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 390 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 6937 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-05 | September | 1630 | 7391 |  |  | 7188 |  |  | 1484 | 203 | 1484 | Minimum Margin | TTC Validation phase - bilateral reduction | 1281 | 203 | NA | NA | NA | 203 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 6937 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-05 | September | 1730 | 7023 |  |  | 5768 |  |  | 1687 | 203 | 2263 | Minimum Margin | TTC Validation phase - bilateral reduction | 1484 | 1255 | NA | NA | NA | 779 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 132 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5950 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | 6569 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-05 | September | 1830 |  | 6283 | 965 |  | 6276 | 947 | -4596 | -4596 | -4596 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 7 | 18 | 25 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 223 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-05 | September | 1930 |  | 6292 | 969 |  | 6142 | 947 | -4598 | -4598 | -4598 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 150 | 22 | 172 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 192 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5952 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-05 | September | 2030 |  | 6292 | 969 |  | 6231 | 947 | -4598 | -4598 | -4598 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 61 | 22 | 83 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 192 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 6041 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-05 | September | 2130 |  | 6826 | 680 |  | 6671 | 665 | -2082 | -2082 | -2082 | Critical Branch | ID schedules | 0 | NA | 155 | 15 | 170 | 0 | 1 | 138 | None | None | 421 | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | 6421 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-05 | September | 2230 |  | 6827 | 680 |  | 6761 | 673 | -2081 | -2081 | -2081 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 66 | 7 | 73 | 0 | 1 | 138 | None | None | 423 | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | 6506 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-05 | September | 2330 |  | 6291 | 705 |  | 6274 | 705 | -1503 | -1503 | -1503 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 17 | 0 | 17 | 0 | 1 | 158 | None | None | 413 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-06 | September | 1230 | 4365 |  |  | 4365 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 281 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-06 | September | 1330 | 4365 |  |  | 4365 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 233 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-06 | September | 1430 | 4365 |  |  | 4365 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 128 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-06 | September | 1530 |  | 5683 | 554 |  | 5510 | 554 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 173 | 0 | 173 | 0 | 1 | -343 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 343 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-06 | September | 1630 |  | 5683 | 554 |  | 5682 | 554 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | -343 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 345 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-06 | September | 1730 |  | 5683 | 554 |  | 5682 | 554 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 140 | None | None | 345 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-06 | September | 1830 |  | 5073 | 626 |  | 5073 | 625 | -3813 | -3813 | -3813 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | 102 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 182 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-06 | September | 1930 |  | 5038 | 683 |  | 5038 | 683 | -3518 | -3518 | -3518 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 113 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -113 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-06 | September | 2030 |  | 5038 | 683 |  | 5038 | 683 | -3518 | -3518 | -3518 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 113 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -113 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-06 | September | 2130 | 5305 |  |  | 5305 |  |  | -3555 | -3555 | -3555 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 350 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-06 | September | 2230 | 5842 |  |  | 5839 |  |  | -3872 | -3872 | -3871 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 3 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 350 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-06 | September | 2330 | 5301 |  |  | 5301 |  |  | -3277 | -3277 | -3277 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-07 | September | 1230 |  | 2134 | 335 |  | 1834 | 335 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 300 | 0 | 300 | 0 | 1 | 160 | None | None | 370 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-07 | September | 1330 |  | 2134 | 335 |  | 1760 | 335 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 374 | 0 | 374 | 0 | 1 | 160 | None | None | 370 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-07 | September | 1430 |  | 2134 | 335 |  | 1262 | 335 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 872 | 0 | 872 | 0 | 1 | 160 | None | None | -141 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-07 | September | 1530 |  | 4411 | 923 |  | 3287 | 906 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1124 | 17 | 1141 | 0 | 1 | 152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 64 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-07 | September | 1630 |  | 3434 | 1026 |  | 3434 | 995 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 31 | 31 | 0 | 1 | 152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 38 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-07 | September | 1730 |  | 4339 | 1025 |  | 4317 | 993 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 22 | 32 | 54 | 0 | 1 | 152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-07 | September | 1830 |  | 6510 | 726 |  | 5191 | 726 | -3552 | -3552 | -3552 | Critical Branch | ID schedules | 0 | NA | 1319 | 0 | 1319 | 0 | 1 | -413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-07 | September | 1930 |  | 6510 | 726 |  | 5961 | 726 | -3552 | -3552 | -3552 | Critical Branch | ID schedules | 0 | NA | 549 | 0 | 549 | 0 | 1 | 157 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-07 | September | 2030 |  | 6510 | 726 |  | 6163 | 726 | -3552 | -3552 | -3552 | Critical Branch | ID schedules | 0 | NA | 347 | 0 | 347 | 0 | 1 | 157 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-07 | September | 2130 | 7183 |  |  | 7183 |  |  | -4314 | -4314 | -4314 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-07 | September | 2230 | 7259 |  |  | 7259 |  |  | -4371 | -4371 | -4371 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-07 | September | 2330 | 7232 |  |  | 7232 |  |  | -4360 | -4360 | -4360 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-08 | September | 1230 | 7619 |  |  | 7502 |  |  | -988 | -988 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 117 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-08 | September | 1330 | 7619 |  |  | 7498 |  |  | -987 | -987 | -874 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 121 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-08 | September | 1430 | 7619 |  |  | 7501 |  |  | -988 | -988 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 118 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7166 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-08 | September | 1530 | 8009 |  |  | 7711 |  |  | -3477 | -3477 | -3184 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 298 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-08 | September | 1630 | 8009 |  |  | 7711 |  |  | -3477 | -3477 | -3184 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 298 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-08 | September | 1730 | 8009 |  |  | 7496 |  |  | -3477 | -3477 | -2970 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 513 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | 7383 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-08 | September | 1830 |  | 6495 | 739 |  | 6406 | 660 | -877 | -877 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 89 | 79 | 168 | 0 | 1 | 123 | None | None | 193 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-08 | September | 1930 |  | 6495 | 739 |  | 6406 | 660 | -877 | -877 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 89 | 79 | 168 | 0 | 1 | 123 | None | None | 193 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-08 | September | 2030 |  | 6495 | 739 |  | 5689 | 660 | -877 | -877 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 806 | 79 | 885 | 0 | 1 | 123 | None | None | 193 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5306 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-08 | September | 2130 |  | 5999 | 620 |  | 6063 | 521 | -4091 | -4091 | -4091 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -64 | 99 | 35 | 0 | 1 | 140 | None | None | 323 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-08 | September | 2230 |  | 6009 | 657 |  | 5988 | 657 | -4076 | -4076 | -4076 | ID schedules | ID schedules | 0 | NA | 21 | 0 | 21 | 0 | 1 | 139 | None | None | 353 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5649 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-08 | September | 2330 |  | 5480 | 683 |  | 5566 | 683 | -3458 | -3458 | -3458 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -86 | 0 | -86 | 0 | 1 | 159 | None | None | 367 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-09 | September | 1230 | 6742 |  |  | 6742 |  |  | -2730 | -2730 | -2730 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 326 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 1330 | 6847 |  |  | 6847 |  |  | -2854 | -2854 | -2854 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 326 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 1430 | 6847 |  |  | 6847 |  |  | -2854 | -2854 | -2854 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 326 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 1530 |  | 7096 | 703 |  | 7096 | 703 | -412 | -412 | -412 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 117 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 364 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-09 | September | 1630 |  | 6995 | 703 |  | 6995 | 703 | -287 | -287 | -287 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 117 | None | None | 365 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 1730 |  | 7176 | 703 |  | 6959 | 703 | -205 | -205 | -205 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 217 | 0 | 217 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 1830 |  | 5815 | 799 |  | 5654 | 798 | -3831 | -3831 | -3831 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 161 | 1 | 162 | 0 | 1 | 119 | None | None | 102 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5322 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 1930 |  | 5828 | 799 |  | 4976 | 798 | -3839 | -3839 | -3839 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 852 | 1 | 853 | 0 | 1 | 119 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -119 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5522 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-09 | September | 2030 |  | 5837 | 799 |  | 5076 | 799 | -3845 | -3845 | -3845 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 761 | 0 | 761 | 0 | 1 | 119 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -119 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-09 | September | 2130 |  | 6469 | 849 |  | 5102 | 799 | -3825 | -3825 | -3825 | Critical Branch | ID schedules | 0 | NA | 1367 | 50 | 1417 | 0 | 1 | 120 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 232 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5853 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-09 | September | 2230 |  | 6512 | 849 |  | 6172 | 842 | -3846 | -3846 | -3846 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 340 | 7 | 347 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 166 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-09 | September | 2330 |  | 5904 | 894 |  | 5845 | 886 | -3235 | -3235 | -3235 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 59 | 8 | 67 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 335 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1230 | 7907 |  |  | 7628 |  |  | 682 | 207 | 894 | Minimum Margin | TTC Validation phase - bilateral reduction | 475 | 279 | NA | NA | NA | 419 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - N-2 Albertville-Rondissone | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1330 | 7907 |  |  | 7628 |  |  | 682 | 207 | 894 | Minimum Margin | TTC Validation phase - bilateral reduction | 475 | 279 | NA | NA | NA | 419 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - N-2 Albertville-Rondissone | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1430 | 7907 |  |  | 7628 |  |  | 682 | 207 | 894 | Minimum Margin | TTC Validation phase - bilateral reduction | 475 | 279 | NA | NA | NA | 419 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - N-2 Albertville-Rondissone | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1530 |  | 6912 | 667 |  | 6874 | 667 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 38 | 0 | 38 | 0 | 1 | 119 | None | None | 365 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - N-2 Albertville-Rondissone | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1630 |  | 6912 | 667 |  | 6808 | 667 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 104 | 0 | 104 | 0 | 1 | 119 | None | None | 348 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - N-2 Albertville-Rondissone | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1730 |  | 6912 | 667 |  | 5324 | 557 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1588 | 110 | 1698 | 0 | 1 | 119 | None | None | 365 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5503 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | Bilateral - Outage - N-2 Albertville-Rondissone | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1830 |  | 5115 | 803 |  | 5377 | 803 | -4079 | -4079 | -4079 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -262 | 0 | -262 | 0 | 1 | 120 | None | None | 196 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 4880 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 1930 |  | 5294 | 803 |  | 5423 | 803 | -4306 | -4306 | -4306 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -129 | 0 | -129 | 0 | 1 | 120 | None | None | 181 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 4916 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 2030 |  | 5049 | 803 |  | 5299 | 803 | -4005 | -4005 | -4005 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -250 | 0 | -250 | 0 | 1 | 120 | None | None | 188 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 4798 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 2130 | 6774 |  |  | 6774 |  |  | -2409 | -2409 | -2409 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 365 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 2230 | 6774 |  |  | 6774 |  |  | -2409 | -2409 | -2409 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 365 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-10 | September | 2330 | 6979 |  |  | 6979 |  |  | -2686 | -2686 | -2686 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 355 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 1230 | 7434 |  |  | 7419 |  |  | 252 | 248 | 61 | Minimum Margin | TTC Validation phase - bilateral reduction | 4 | 15 | NA | NA | NA | 57 | 1 | 120 | None | None | 356 | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 1330 | 7434 |  |  | 7419 |  |  | 252 | 248 | 61 | Minimum Margin | TTC Validation phase - bilateral reduction | 4 | 15 | NA | NA | NA | 57 | 1 | -355 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 356 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-11 | September | 1430 | 7469 |  |  | 7441 |  |  | 102 | 102 | 0 | Adjustment reached | ID schedules | 0 | 28 | NA | NA | NA | 0 | 1 | -355 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-11 | September | 1530 |  | 6818 | 644 |  | 6800 | 644 | -1847 | -1847 | -1847 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 0 | 1 | -358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-11 | September | 1630 |  | 6856 | 658 |  | 6800 | 658 | -1882 | -1882 | -1882 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 56 | 0 | 56 | 0 | 1 | -358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-11 | September | 1730 |  | 6856 | 658 |  | 6800 | 658 | -1882 | -1882 | -1882 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 56 | 0 | 56 | 0 | 1 | -358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 358 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-11 | September | 1830 |  | 7508 | 919 |  | 6959 | 900 | -3142 | -3142 | -3142 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 549 | 19 | 568 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 1930 |  | 7592 | 919 |  | 7036 | 900 | -3134 | -3134 | -3134 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 556 | 19 | 575 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 208 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 2030 |  | 7507 | 919 |  | 6958 | 900 | -3142 | -3142 | -3142 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 549 | 19 | 568 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 2130 | 8391 |  |  | 7907 |  |  | -1933 | -1933 | -1319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 484 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 2230 | 8391 |  |  | 7907 |  |  | -1933 | -1933 | -1319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 484 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-11 | September | 2330 | 7791 |  |  | 7532 |  |  | -1326 | -1326 | -1011 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 259 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 355 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1230 | 7093 |  |  | 7077 |  |  | -4400 | -4400 | -4384 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 120 | None | None | 364 | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - RDCR FIL 1 & 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1330 | 7203 |  |  | 7203 |  |  | -4515 | -4515 | -4515 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 364 | None | None | None | None | None | None | None | None | 2500 | None | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1430 | 7238 |  |  | 7238 |  |  | -4552 | -4552 | -4552 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 364 | None | None | None | None | None | None | None | None | 2500 | None | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1530 |  | 7399 | 717 |  | 6910 | 717 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 489 | 0 | 489 | 0 | 1 | 117 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - RDCR FIL 1 & 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1630 |  | 7399 | 717 |  | 6969 | 717 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 430 | 0 | 430 | 0 | 1 | 117 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1730 |  | 7459 | 717 |  | 7049 | 717 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 410 | 0 | 410 | 0 | 1 | 136 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1830 |  | 6384 | 890 |  | 6225 | 879 | -1206 | -1206 | -1206 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 159 | 11 | 170 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 311 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 1930 |  | 6676 | 890 |  | 5743 | 785 | -1415 | -1415 | -1415 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 933 | 105 | 1038 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5553 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-12 | September | 2030 |  | 6676 | 890 |  | 5736 | 784 | -1415 | -1415 | -1415 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 940 | 106 | 1046 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 198 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5546 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 2130 | 7966 |  |  | 7686 |  |  | -1710 | -1710 | -1328 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 280 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 2230 | 7966 |  |  | 7686 |  |  | -1710 | -1710 | -1328 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 280 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-12 | September | 2330 | 7366 |  |  | 7312 |  |  | -1103 | -1103 | -1041 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 54 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 1230 | 6639 |  |  | 5511 |  |  | -3817 | -3817 | -2709 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1128 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-13 | September | 1330 | 6639 |  |  | 5566 |  |  | -3817 | -3817 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1073 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-13 | September | 1430 | 6639 |  |  | 5350 |  |  | -3817 | -3817 | -2550 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1289 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-13 | September | 1530 | 5986 |  |  | 5988 |  |  | -1636 | -1636 | -1637 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -2 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 1630 | 7150 |  |  | 7150 |  |  | -2582 | -2582 | -2582 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 1730 | 6966 |  |  | 6971 |  |  | -2581 | -2581 | -2584 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -5 | NA | NA | NA | 0 | 1 | 140 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 1830 | 5867 |  |  | 5867 |  |  | -3691 | -3691 | -3691 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 328 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 1930 | 5755 |  |  | 5777 |  |  | -3744 | -3744 | -3755 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -22 | NA | NA | NA | 0 | 1 | 140 | None | None | 331 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 2030 | 6020 |  |  | 6020 |  |  | -3843 | -3843 | -3843 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 331 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 2130 | 6735 |  |  | 6735 |  |  | -4163 | -4163 | -4163 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 370 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 2230 | 6735 |  |  | 6735 |  |  | -4163 | -4163 | -4163 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 370 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-13 | September | 2330 | 6136 |  |  | 6136 |  |  | -3559 | -3559 | -3559 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-14 | September | 1230 |  | 4441 | 387 |  | 4333 | 387 | -715 | -715 | -715 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 108 | 0 | 108 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1330 |  | 5314 | 392 |  | 5314 | 392 | -1179 | -1179 | -1179 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 159 | None | None | 358 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1430 |  | 4968 | 387 |  | 4968 | 387 | -1147 | -1147 | -1147 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | None | 175 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1530 |  | 5042 | 645 |  | 5020 | 645 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 22 | 0 | 22 | 0 | 1 | 160 | None | None | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1630 |  | 4980 | 684 |  | 4980 | 684 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 114 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1730 |  | 5985 | 645 |  | 5985 | 581 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 64 | 64 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -27 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5154 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1830 |  | 5321 | 852 |  | 5321 | 871 | -4017 | -4017 | -4017 | ID schedules | ID schedules | 0 | NA | 0 | -19 | -19 | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -41 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 1930 |  | 5482 | 874 |  | 5482 | 874 | -3670 | -3670 | -3670 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 2030 |  | 5547 | 671 |  | 5547 | 613 | -4570 | -4570 | -4570 | ID schedules | ID schedules | 0 | NA | 0 | 58 | 58 | 0 | 1 | 119 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 4949 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-14 | September | 2130 | 6618 |  |  | 6618 |  |  | -3944 | -3944 | -3944 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 387 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-14 | September | 2230 | 6618 |  |  | 6618 |  |  | -3944 | -3944 | -3944 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 387 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-14 | September | 2330 | 6618 |  |  | 6618 |  |  | -3944 | -3944 | -3944 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 387 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1230 | 7421 |  |  | 7421 |  |  | -3583 | -3583 | -3583 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-CH] SILS-SOAZZA [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1330 | 7441 |  |  | 7441 |  |  | -3602 | -3602 | -3602 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-CH] SILS-SOAZZA [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1430 | 7481 |  |  | 7481 |  |  | -3642 | -3642 | -3642 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-CH] SILS-SOAZZA [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1530 | 7506 |  |  | 7506 |  |  | -2630 | -2630 | -2630 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1630 | 7506 |  |  | 7506 |  |  | -2630 | -2630 | -2630 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1730 | 7266 |  |  | 7302 |  |  | -2519 | -2519 | -2536 | Critical Branch | ID schedules | 0 | -36 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-15 | September | 1830 |  | 6956 | 657 |  | 6935 | 657 | -4580 | -4580 | -4580 | ID schedules | ID schedules | 0 | NA | 21 | 0 | 21 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC FIL 1 & 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-15 | September | 1930 |  | 6956 | 657 |  | 6935 | 657 | -4580 | -4580 | -4580 | ID schedules | ID schedules | 0 | NA | 21 | 0 | 21 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC FIL 1 & 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-15 | September | 2030 |  | 6955 | 559 |  | 6935 | 559 | -4579 | -4579 | -4579 | ID schedules | ID schedules | 0 | NA | 20 | 0 | 20 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC FIL 1 & 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-15 | September | 2130 |  | 6935 | 611 |  | 6935 | 611 | -2239 | -2239 | -2239 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-15 | September | 2230 |  | 6935 | 611 |  | 6935 | 611 | -2226 | -2226 | -2226 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-15 | September | 2330 |  | 6518 | 636 |  | 6518 | 636 | -1798 | -1798 | -1798 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-16 | September | 1230 | 7072 |  |  | 7072 |  |  | -848 | -848 | -846 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1330 | 7072 |  |  | 7072 |  |  | -848 | -848 | -846 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1430 | 7072 |  |  | 7072 |  |  | -848 | -848 | -846 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1530 |  | 6901 | 661 |  | 6901 | 661 | -2781 | -2781 | -2781 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1630 |  | 7007 | 661 |  | 6926 | 661 | -2737 | -2737 | -2737 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 81 | 0 | 81 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC FIL 1 & 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1730 |  | 7022 | 661 |  | 6926 | 661 | -2744 | -2744 | -2744 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 96 | 0 | 96 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC FIL 1 & 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1830 |  | 6495 | 809 |  | 6495 | 836 | -3647 | -3647 | -3647 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -27 | -27 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 1930 |  | 6495 | 825 |  | 6495 | 841 | -3589 | -3589 | -3589 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -16 | -16 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 2030 |  | 6495 | 808 |  | 6495 | 836 | -3672 | -3672 | -3672 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -28 | -28 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 2130 | 7158 |  |  | 7158 |  |  | -3186 | -3186 | -3186 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 2230 | 7158 |  |  | 7161 |  |  | -3186 | -3186 | -3188 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | -3 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-16 | September | 2330 | 6746 |  |  | 6746 |  |  | -2664 | -2664 | -2664 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 1230 | 6986 |  |  | 6986 |  |  | -735 | -735 | -735 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -386 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 386 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-17 | September | 1330 | 6890 |  |  | 6890 |  |  | -669 | -669 | -669 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -386 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 386 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-17 | September | 1430 | 7000 |  |  | 7000 |  |  | -745 | -745 | -745 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 386 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-17 | September | 1530 | 7814 |  |  | 7600 |  |  | -1810 | -1810 | -1622 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 214 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 1630 | 7814 |  |  | 7600 |  |  | -1810 | -1810 | -1622 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 214 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 1730 | 7814 |  |  | 7600 |  |  | -1810 | -1810 | -1622 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 214 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 1830 |  | 6513 | 851 |  | 6380 | 847 | -3159 | -3159 | -3159 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 133 | 4 | 137 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 363 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 1930 |  | 6602 | 851 |  | 6456 | 845 | -3206 | -3206 | -3206 | Critical Branch | Validation phase | 0 | NA | 146 | 6 | 152 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 196 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 6393 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 2030 |  | 6512 | 851 |  | 6259 | 827 | -3158 | -3158 | -3158 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 253 | 24 | 277 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 363 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | 6123 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 2130 | 7706 |  |  | 7538 |  |  | -2049 | -2049 | -1885 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 168 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 2230 | 7706 |  |  | 7538 |  |  | -2049 | -2049 | -1885 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 168 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-17 | September | 2330 | 7106 |  |  | 7102 |  |  | -1440 | -1440 | -1436 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 4 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 1230 | 6954 |  |  | 6954 |  |  | 186 | 186 | -1 | Adjustment reached | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2428 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-18 | September | 1330 | 7028 |  |  | 7028 |  |  | -75 | -75 | -75 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-18 | September | 1430 | 7028 |  |  | 7028 |  |  | -75 | -75 | -75 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 1530 | 7455 |  |  | 7270 |  |  | -3271 | -3271 | -3028 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 185 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 1630 | 7455 |  |  | 7270 |  |  | -3271 | -3271 | -3028 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 185 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 1730 | 7755 |  |  | 7572 |  |  | -3553 | -3553 | -3312 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 183 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 1830 |  | 6398 | 953 |  | 6336 | 950 | -974 | -974 | -974 | Critical Branch | Validation phase | 0 | NA | 62 | 3 | 65 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 6183 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 1930 |  | 6398 | 953 |  | 5968 | 900 | -974 | -974 | -974 | Critical Branch | Validation phase | 0 | NA | 430 | 53 | 483 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5778 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 2500 | None | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 2030 |  | 6317 | 953 |  | 6061 | 928 | -938 | -938 | -938 | Critical Branch | ID schedules | 0 | NA | 256 | 25 | 281 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5921 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-18 | September | 2130 | 7735 |  |  | 7560 |  |  | -3789 | -3789 | -3560 | Critical Branch | ID schedules | 0 | 175 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-18 | September | 2230 | 7735 |  |  | 7560 |  |  | -3789 | -3789 | -3560 | Critical Branch | ID schedules | 0 | 175 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-18 | September | 2330 | 7135 |  |  | 7135 |  |  | -3182 | -3182 | -3180 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-19 | September | 1230 | 7352 |  |  | 7111 |  |  | -5052 | -5052 | -4787 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 241 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 329 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-19 | September | 1330 | 7352 |  |  | 7111 |  |  | -5052 | -5052 | -4787 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 241 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 329 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-19 | September | 1430 | 7352 |  |  | 7207 |  |  | -5052 | -5052 | -4905 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 145 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-19 | September | 1530 | 7862 |  |  | 7489 |  |  | -1319 | -1319 | -809 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 373 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-19 | September | 1630 | 7862 |  |  | 7489 |  |  | -1319 | -1319 | -809 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 373 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-19 | September | 1730 | 8162 |  |  | 7356 |  |  | -1560 | -1560 | -665 | Critical Branch | ID schedules | 0 | 806 | NA | NA | NA | 0 | 1 | 140 | None | None | 401 | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - N-2 Albertville-Rondissone / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-19 | September | 1830 |  | 5342 | 913 |  | 5342 | 827 | -1084 | -1084 | -1084 | Critical Branch | ID schedules | 0 | NA | 0 | 86 | 86 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 156 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-19 | September | 1930 |  | 5342 | 913 |  | 5342 | 827 | -1084 | -1084 | -1084 | Critical Branch | ID schedules | 0 | NA | 0 | 86 | 86 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 156 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-19 | September | 2030 |  | 5342 | 913 |  | 5342 | 827 | -1084 | -1084 | -1084 | Critical Branch | ID schedules | 0 | NA | 0 | 86 | 86 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 156 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-19 | September | 2130 | 6805 |  |  | 6804 |  |  | -1676 | -1676 | -1674 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | -361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 374 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-19 | September | 2230 | 6805 |  |  | 6804 |  |  | -1676 | -1676 | -1674 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | -361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 374 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-19 | September | 2330 | 6205 |  |  | 6205 |  |  | -1069 | -1069 | -1068 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-20 | September | 1230 | 6350 |  |  | 6350 |  |  | -4953 | -4953 | -4953 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 374 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-20 | September | 1330 | 6353 |  |  | 6353 |  |  | -4955 | -4955 | -4955 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 374 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-20 | September | 1430 | 6359 |  |  | 6359 |  |  | -4949 | -4949 | -4949 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 374 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-20 | September | 1530 | 7687 |  |  | 6302 |  |  | 1354 | 199 | 2427 | Minimum Margin | TTC Validation phase - bilateral reduction | 1155 | 1385 | NA | NA | NA | 1272 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 380 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-20 | September | 1630 | 7687 |  |  | 7392 |  |  | 1354 | 199 | 1601 | Minimum Margin | TTC Validation phase - bilateral reduction | 1155 | 295 | NA | NA | NA | 446 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 1730 | 7990 |  |  | 7637 |  |  | 1173 | 202 | 1477 | Minimum Margin | TTC Validation phase - bilateral reduction | 971 | 353 | NA | NA | NA | 506 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 1830 | 6137 |  |  | 6137 |  |  | -2134 | -2134 | -2133 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 335 | None | None | None | None | None | None | None | None | None | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 1930 | 6137 |  |  | 6137 |  |  | -2134 | -2134 | -2133 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 335 | None | None | None | None | None | None | None | None | None | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 2030 | 6137 |  |  | 6137 |  |  | -2134 | -2134 | -2133 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 335 | None | None | None | None | None | None | None | None | None | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 2130 | 7629 |  |  | 7492 |  |  | -5132 | -5132 | -4999 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 137 | NA | NA | NA | 0 | 1 | 140 | None | None | 423 | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 2230 | 7629 |  |  | 7492 |  |  | -5132 | -5132 | -4999 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 137 | NA | NA | NA | 0 | 1 | 140 | None | None | 423 | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-20 | September | 2330 | 7029 |  |  | 7028 |  |  | -4534 | -4534 | -4532 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 160 | None | None | 413 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 1230 | 3959 |  |  | 3500 |  |  | -4549 | -4549 | -4201 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 459 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 349 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-21 | September | 1330 | 3959 |  |  | 3500 |  |  | -4549 | -4549 | -4201 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 459 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 349 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-21 | September | 1430 | 4000 |  |  | 4000 |  |  | -4568 | -4568 | -4568 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 349 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-21 | September | 1530 | 7501 |  |  | 4972 |  |  | 435 | 360 | 2803 | Minimum Margin | TTC Validation phase - bilateral reduction | 75 | 2529 | NA | NA | NA | 2728 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-21 | September | 1630 | 7501 |  |  | 6671 |  |  | 435 | 360 | 942 | Minimum Margin | TTC Validation phase - bilateral reduction | 75 | 830 | NA | NA | NA | 867 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 1730 | 7534 |  |  | 7498 |  |  | 193 | 193 | 27 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 36 | NA | NA | NA | 27 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 1830 | 7135 |  |  | 7135 |  |  | -3681 | -3681 | -3681 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 300 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 1930 | 7135 |  |  | 7135 |  |  | -3681 | -3681 | -3681 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 300 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 2030 | 7135 |  |  | 7135 |  |  | -3681 | -3681 | -3681 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 300 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 2130 | 6708 |  |  | 6707 |  |  | -1452 | -1452 | -1451 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 160 | None | None | 381 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 2230 | 6708 |  |  | 6707 |  |  | -1452 | -1452 | -1451 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 160 | None | None | 381 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-21 | September | 2330 | 6708 |  |  | 6707 |  |  | -1452 | -1452 | -1451 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 160 | None | None | 381 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1230 | 6895 |  |  | 6895 |  |  | 1954 | -56 | 1954 | ID schedules | TTC Validation phase - bilateral reduction | 2010 | 0 | NA | NA | NA | -56 | 1 | None | None | None | None | None | None | None | 6508 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1330 | 6895 |  |  | 6895 |  |  | 1954 | -56 | 1954 | ID schedules | TTC Validation phase - bilateral reduction | 2010 | 0 | NA | NA | NA | -56 | 1 | None | None | None | None | None | None | None | 6644 | Reduction due to missing redispatch potential | None | None | None | 2500 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1430 | 6895 |  |  | 6895 |  |  | 1954 | -56 | 1954 | ID schedules | TTC Validation phase - bilateral reduction | 2010 | 0 | NA | NA | NA | -56 | 1 | None | None | None | None | None | None | None | 6644 | Reduction due to missing redispatch potential | None | None | None | 2500 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1530 | 6061 |  |  | 6061 |  |  | -3160 | -3160 | -3160 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1630 | 7061 |  |  | 7061 |  |  | -4153 | -4153 | -4153 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1730 | 6616 |  |  | 6620 |  |  | -3899 | -3899 | -3902 | ID schedules | ID schedules | 0 | -4 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1830 | 4906 |  |  | 4907 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 4515 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 1930 | 4632 |  |  | 4632 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 4191 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 2030 | 4769 |  |  | 4769 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 4305 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 2130 | 5965 |  |  | 5968 |  |  | -1651 | -1651 | -1652 | ID schedules | ID schedules | 0 | -3 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 2230 | 5822 |  |  | 5822 |  |  | -1564 | -1564 | -1564 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-22 | September | 2330 | 5393 |  |  | 5393 |  |  | -1058 | -1058 | -1058 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-23 | September | 1230 | 7315 |  |  | 7315 |  |  | -3294 | -3294 | -1894 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 396 | None | None | None | 6569 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-23 | September | 1330 | 7315 |  |  | 7315 |  |  | -3294 | -3294 | -1909 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 396 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-23 | September | 1430 | 7315 |  |  | 7315 |  |  | -3294 | -3294 | -1925 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 396 | None | None | None | 6917 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-23 | September | 1530 |  | 6270 | 648 |  | 6270 | 351 | -3715 | -3715 | -3005 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 297 | 297 | 0 | 1 | 107 | None | None | 391 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 1630 |  | 6270 | 680 |  | 6270 | 465 | -3356 | -3356 | -2950 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 215 | 215 | 0 | 1 | 140 | None | None | -140 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5766 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 1730 |  | 5897 | 814 |  | 5897 | 766 | -2583 | -2583 | -2904 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 48 | 48 | 0 | 1 | 137 | None | None | -75 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5400 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 1830 |  | 4010 | 560 |  | 4010 | 560 | -1575 | -1575 | -3697 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 91 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -91 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 3099 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 1930 |  | 4450 | 560 |  | 4450 | 560 | -2081 | -2081 | -4070 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 91 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -90 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 3219 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 2030 |  | 4818 | 529 |  | 4818 | 291 | -2646 | -2646 | -4150 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 238 | 238 | 0 | 1 | -178 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 178 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4196 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 2130 |  | 6199 | 657 |  | 6197 | 657 | -2124 | -2124 | -2267 | ID schedules | ID schedules | 0 | NA | 2 | 0 | 2 | 0 | 1 | 139 | None | None | 322 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 2230 |  | 6262 | 626 |  | 6261 | 222 | -2187 | -2187 | -2294 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 404 | 405 | 0 | 1 | 139 | None | None | 364 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5968 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-23 | September | 2330 |  | 5701 | 651 |  | 5701 | 97 | -1649 | -1649 | -1648 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 554 | 554 | 0 | 1 | 159 | None | None | 350 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 1230 | 7194 |  |  | 7194 |  |  | -2169 | -2169 | -2169 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -260 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 260 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6555 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-24 | September | 1330 | 6974 |  |  | 6974 |  |  | -1951 | -1951 | -1951 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 216 | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-24 | September | 1430 | 7374 |  |  | 7374 |  |  | -2320 | -2320 | -2320 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 348 | None | None | None | None | None | None | None | None | 2500 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-24 | September | 1530 |  | 6173 | 819 |  | 6107 | 391 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 66 | 428 | 494 | 0 | 1 | -289 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 289 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 1630 |  | 6173 | 819 |  | 6107 | 708 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 66 | 111 | 177 | 0 | 1 | 28 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -27 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 1730 |  | 6173 | 819 |  | 6107 | 824 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 66 | -5 | 61 | 0 | 1 | 138 | None | None | 144 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 1830 |  | 5754 | 704 |  | 5754 | 708 | -3292 | -3292 | -3292 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -4 | -4 | 0 | 1 | 117 | None | None | 300 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 1930 |  | 5754 | 748 |  | 5754 | 755 | -3171 | -3171 | -3171 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -7 | -7 | 0 | 1 | 140 | None | None | -73 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5493 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 2030 |  | 5754 | 704 |  | 5754 | 708 | -3400 | -3400 | -3400 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -4 | -4 | 0 | 1 | 117 | None | None | 356 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-24 | September | 2130 | 7395 |  |  | 7395 |  |  | -2019 | -2019 | -2019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 401 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-24 | September | 2230 | 7395 |  |  | 7395 |  |  | -2019 | -2019 | -2019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 401 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-24 | September | 2330 | 6796 |  |  | 6796 |  |  | -1408 | -1408 | -1408 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 390 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-25 | September | 1230 |  | 6083 | 842 |  | 6082 | 839 | -39 | -39 | -39 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 3 | 4 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 170 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1330 |  | 6084 | 842 |  | 6084 | 839 | -39 | -39 | -39 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 3 | 3 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 170 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1430 |  | 5943 | 842 |  | 5890 | 839 | -28 | -28 | -28 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 53 | 3 | 56 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 385 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1530 |  | 7117 | 712 |  | 7016 | 712 | -413 | -413 | -413 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 101 | 0 | 101 | 0 | 1 | 140 | None | None | 417 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1630 |  | 7136 | 712 |  | 7031 | 712 | -417 | -417 | -417 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 105 | 0 | 105 | 0 | 1 | 136 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1730 |  | 7132 | 712 |  | 7025 | 712 | -417 | -417 | -417 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 107 | 0 | 107 | 0 | 1 | 136 | None | None | 418 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1830 |  | 7040 | 725 |  | 7038 | 725 | -489 | -489 | -489 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 0 | 1 | 136 | None | None | 379 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 1930 |  | 7058 | 725 |  | 6972 | 725 | -493 | -493 | -493 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 0 | 1 | 136 | None | None | 424 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 2030 |  | 7046 | 725 |  | 7046 | 725 | -638 | -638 | -638 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 136 | None | None | 424 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-25 | September | 2130 | 8258 |  |  | 7921 |  |  | -1912 | -1912 | -1640 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 337 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-25 | September | 2230 | 8258 |  |  | 7921 |  |  | -1912 | -1912 | -1640 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 337 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-25 | September | 2330 | 7658 |  |  | 7464 |  |  | 0 | 0 | -1148 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 194 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-26 | September | 1230 | 7688 |  |  | 6879 |  |  | -411 | -411 | 133 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 809 | NA | NA | NA | 133 | 1 | 140 | None | None | 385 | None | None | None | 6629 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1330 | 7688 |  |  | 7018 |  |  | -411 | -411 | 39 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 670 | NA | NA | NA | 39 | 1 | 140 | None | None | 407 | None | None | None | 6768 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1430 | 7688 |  |  | 7375 |  |  | -296 | -296 | -85 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 313 | NA | NA | NA | 0 | 1 | 140 | None | None | 403 | None | None | None | 7337 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 2500 | None | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1530 |  | 5661 | 125 |  | 5656 | 125 | -579 | -579 | -579 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 5 | 0 | 5 | 0 | 1 | 95 | None | None | 68 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1630 |  | 7003 | 125 |  | 7003 | 125 | -2290 | -2290 | -2290 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 100 | None | None | 105 | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1730 |  | 6439 | 125 |  | 6439 | 125 | -1995 | -1995 | -1995 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 100 | None | None | 141 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1830 |  | 7869 | 893 |  | 7762 | 880 | -1490 | -1490 | -1490 | Critical Branch | ID schedules | 0 | NA | 107 | 13 | 120 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 181 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - Outage - GENISSIAT S1.2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 1930 |  | 7873 | 893 |  | 7873 | 880 | -1492 | -1492 | -1492 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 13 | 13 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 187 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - Outage - GENISSIAT S1.2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 2030 |  | 7739 | 892 |  | 7676 | 880 | -1490 | -1490 | -1490 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 63 | 12 | 75 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 360 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 2130 | 9048 |  |  | 9048 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | 3600 | None | Outage - GENISSIAT S1.2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 2230 | 9048 |  |  | 9048 |  |  | -2113 | -2113 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | 3600 | None | Outage - GENISSIAT S1.2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-26 | September | 2330 | 8448 |  |  | 8448 |  |  | -1486 | -1486 | -1486 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1230 | 7020 |  |  | 7020 |  |  | -666 | -666 | -666 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 374 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1330 | 7020 |  |  | 7020 |  |  | -666 | -666 | -666 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 374 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1430 | 7020 |  |  | 7020 |  |  | -666 | -666 | -666 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 374 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1530 |  | 6212 | -223 |  | 6178 | -224 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 34 | 1 | 35 | 0 | 1 | 140 | None | None | 401 | None | None | None | None | Reduction due to missing redispatch potential | None | 5619 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1630 |  | 7173 | 654 |  | 7096 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 77 | 0 | 77 | 0 | 1 | 140 | None | None | 401 | None | None | None | None | Reduction due to missing redispatch potential | None | 6589 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1730 |  | 6322 | -296 |  | 6289 | -296 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 33 | 0 | 33 | 0 | 1 | 140 | None | None | 292 | None | None | None | None | Reduction due to missing redispatch potential | None | 5727 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1830 |  | 7679 | 907 |  | 7284 | 856 | -1955 | -1955 | -1955 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 395 | 51 | 446 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 174 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 7067 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3800 | None | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 1930 |  | 7740 | 924 |  | 7654 | 907 | -1987 | -1987 | -1987 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 17 | 103 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 176 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 7387 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3800 | None | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 2030 |  | 7655 | 907 |  | 7356 | 867 | -1952 | -1952 | -1952 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 299 | 40 | 339 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 210 | None | Reduction because NTC over thermal limit on border | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | 7175 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 3800 | None | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 2130 | 8586 |  |  | 8585 |  |  | -4038 | -4038 | -4035 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 140 | None | None | 401 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 2230 | 8586 |  |  | 8585 |  |  | -4038 | -4038 | -4035 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 140 | None | None | 401 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-27 | September | 2330 | 7986 |  |  | 7985 |  |  | -3438 | -3438 | -3435 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 160 | None | None | 390 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-28 | September | 1230 |  | 2273 | 347 |  | 2110 | 347 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 163 | 0 | 163 | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1330 |  | 2530 | 205 |  | 1830 | 205 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 700 | 0 | 700 | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1430 |  | 2439 | 676 |  | 2439 | 676 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1530 |  | 4722 | 801 |  | 3642 | 813 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1080 | -12 | 1068 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1630 |  | 5146 | 801 |  | 5034 | 813 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 112 | -12 | 100 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1730 |  | 6125 | 729 |  | 4882 | 265 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1243 | 464 | 1707 | 0 | 1 | -361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1830 |  | 7403 | 780 |  | 6924 | 780 | -1162 | -1162 | -1162 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 479 | 0 | 479 | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 1930 |  | 7436 | 780 |  | 7436 | 780 | -1179 | -1179 | -1179 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3600 | None | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 2030 |  | 7364 | 754 |  | 7364 | 754 | -1143 | -1143 | -1143 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3600 | None | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-28 | September | 2130 | 8555 |  |  | 8485 |  |  | -254 | -254 | -189 | Critical Branch | ID schedules | 0 | 70 | NA | NA | NA | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 3600 | None | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-28 | September | 2230 | 8555 |  |  | 8485 |  |  | -254 | -254 | -189 | Critical Branch | ID schedules | 0 | 70 | NA | NA | NA | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 3600 | None | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-28 | September | 2330 | 8555 |  |  | 8302 |  |  | -254 | -254 | -69 | Critical Branch | ID schedules | 0 | 253 | NA | NA | NA | 0 | 1 | -232 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 232 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 3600 | None | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-09-29 | September | 1230 |  | 6597 | 651 |  | 6592 | 651 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 5 | 0 | 5 | 0 | 1 | 140 | None | None | 196 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 1330 |  | 6654 | 651 |  | 6672 | 651 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -18 | 0 | -18 | 0 | 1 | 140 | None | None | 208 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 1430 |  | 6817 | 651 |  | 6826 | 651 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -9 | 0 | -9 | 0 | 1 | 140 | None | None | 321 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 1530 |  | 7109 | 800 |  | 7109 | 699 | -3055 | -3055 | -3055 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 101 | 101 | 0 | 1 | 137 | None | None | 149 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 1630 |  | 7076 | 803 |  | 7076 | 705 | -3032 | -3032 | -3032 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 98 | 98 | 0 | 1 | 140 | None | None | 132 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 1730 |  | 7059 | 803 |  | 6778 | 793 | -3022 | -3022 | -3022 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 281 | 10 | 291 | 0 | 1 | 140 | None | None | 149 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 1830 |  | 5713 | 894 |  | 5410 | 882 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 303 | 12 | 315 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 157 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4700 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-29 | September | 1930 |  | 5750 | 894 |  | 5659 | 882 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 91 | 12 | 103 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4991 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-29 | September | 2030 |  | 5761 | 894 |  | 5556 | 882 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 205 | 12 | 217 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 134 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4829 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-09-29 | September | 2130 |  | 7347 | 651 |  | 7092 | 651 | -2654 | -2654 | -2654 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 255 | 0 | 255 | 0 | 1 | 140 | None | None | 391 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 2230 |  | 7341 | 651 |  | 7341 | 651 | -2649 | -2649 | -2649 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 391 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-29 | September | 2330 |  | 6724 | 664 |  | 6686 | 278 | -2003 | -2003 | -2003 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 38 | 386 | 424 | 0 | 1 | 159 | None | None | 379 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1230 |  | 6794 | 777 |  | 6814 | 793 | -1894 | -1894 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -20 | -16 | -36 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | N-2 Albertville-Rondissone / [CH-IT] ROBBIA-FIORANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1330 |  | 6822 | 777 |  | 6838 | 788 | -1909 | -1909 | -1894 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -16 | -11 | -27 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | N-2 Albertville-Rondissone / [CH-IT] ROBBIA-FIORANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1430 |  | 6861 | 793 |  | 6859 | 793 | -1925 | -1925 | -1909 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] ROBBIA-FIORANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1530 |  | 6791 | 764 |  | 6790 | 764 | -3005 | -3005 | -1925 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1630 |  | 6708 | 497 |  | 6703 | 497 | -2950 | -2950 | -3005 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 5 | 0 | 5 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1730 |  | 6638 | 425 |  | 6638 | 418 | -2904 | -2904 | -2950 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 7 | 7 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 6373 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1830 |  | 4896 | 235 |  | 5273 | 235 | -3697 | -3697 | -2904 | ID schedules | ID schedules | 0 | NA | -377 | 0 | -377 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4912 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 1930 |  | 5203 | 235 |  | 5480 | 235 | -4070 | -4070 | -3697 | ID schedules | ID schedules | 0 | NA | -277 | 0 | -277 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5268 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 2030 |  | 5264 | 235 |  | 5501 | 235 | -4150 | -4150 | -4070 | ID schedules | ID schedules | 0 | NA | -237 | 0 | -237 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 2130 |  | 7278 | 381 |  | 7119 | 381 | -2267 | -2267 | -4150 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 159 | 0 | 159 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 2230 |  | 7319 | 381 |  | 7319 | 381 | -2294 | -2294 | -2267 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | None | None | None | None | None | None | None | None | None | None | None | None
2025-09-30 | September | 2330 |  | 6772 | 406 |  | 6731 | 406 | -1648 | -1648 | -2294 | Critical Branch | ID schedules | 0 | NA | 41 | 0 | 41 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-01 | July | 1230 | 5327 |  |  | 5320 |  |  | 0 | 0 | -1648 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 54 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 129 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-01 | July | 1330 | 5327 |  |  | 5320 |  |  | 0 | 0 | -2583 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 54 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 129 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-01 | July | 1430 | 5327 |  |  | 5320 |  |  | 0 | 0 | -2583 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 54 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 129 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-01 | July | 1530 | 6759 |  |  | 6758 |  |  | 11 | 11 | 2 | Adjustment reached | Smoothing ramp | 0 | 1 | NA | NA | NA | 2 | 1 | 54 | None | None | 156 | None | None | None | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-01 | July | 1630 | 6804 |  |  | 6804 |  |  | -77 | -77 | -77 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 54 | None | None | 160 | None | None | None | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-01 | July | 1730 | 6804 |  |  | 6804 |  |  | -77 | -77 | -77 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 54 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-01 | July | 1830 |  | 4488 | 3008 |  | 4488 | 1709 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 0 | 1299 | 1299 | 0 | 1 | 55 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -55 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7995 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-01 | July | 1930 |  | 4488 | 3008 |  | 4488 | 2337 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 671 | 671 | 0 | 1 | 55 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 121 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7995 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-01 | July | 2030 |  | 4488 | 3008 |  | 4488 | 2667 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 341 | 341 | 0 | 1 | 55 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 121 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7995 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-01 | July | 2130 |  | 4923 | 3264 |  | 4875 | 1778 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 48 | 1486 | 1534 | 0 | 1 | 55 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 78 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7995 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-01 | July | 2230 |  | 4923 | 3264 |  | 4875 | 1219 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 48 | 2045 | 2093 | 0 | 1 | 40 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 78 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7995 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-01 | July | 2330 |  | 4600 | 3479 |  | 4424 | 1161 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 176 | 2318 | 2494 | 0 | 1 | 52 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 79 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7415 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-02 | July | 1230 | 5497 |  |  | 5497 |  |  | 0 | 0 | -5062 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 156 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-02 | July | 1330 | 5497 |  |  | 5497 |  |  | 0 | 0 | -5062 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 156 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-02 | July | 1430 | 5497 |  |  | 5497 |  |  | 0 | 0 | -5062 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 156 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-02 | July | 1530 | 8457 |  |  | 6952 |  |  | 0 | 0 | 1205 | Critical Branch | Smoothing ramp | 0 | 1505 | NA | NA | NA | 1205 | 1 | 70 | None | None | 172 | None | None | None | 6649 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-02 | July | 1630 | 8457 |  |  | 8390 |  |  | 0 | 0 | -233 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 67 | NA | NA | NA | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 210 | None | Reduction because NTC over thermal limit on border | None | 8075 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-02 | July | 1730 | 8757 |  |  | 8231 |  |  | -666 | -666 | -140 | Critical Branch | ID schedules | 0 | 526 | NA | NA | NA | 0 | 1 | -162 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 197 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8435 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-02 | July | 1830 |  | 6247 | 612 |  | 6247 | 564 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 0 | 48 | 48 | 0 | 1 | -162 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 172 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-02 | July | 1930 |  | 6247 | 612 |  | 6247 | 101 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 0 | 511 | 511 | 0 | 1 | -107 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 172 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-02 | July | 2030 |  | 6247 | 612 |  | 6247 | 101 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 0 | 511 | 511 | 0 | 1 | -162 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 172 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-02 | July | 2130 |  | 7236 | 160 |  | 7235 | 101 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 59 | 60 | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 190 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-02 | July | 2230 |  | 7236 | 576 |  | 7235 | 541 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 35 | 36 | 0 | 1 | -180 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 190 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-02 | July | 2330 |  | 7728 | 509 |  | 7728 | 600 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -91 | -91 | 0 | 1 | 69 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1230 | 7063 |  |  | 7063 |  |  | 0 | 0 | -2709 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1330 | 7063 |  |  | 7063 |  |  | 0 | 0 | -2709 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6741 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1430 | 7063 |  |  | 7063 |  |  | 0 | 0 | -2709 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6497 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1530 | 8213 |  |  | 7845 |  |  | -2618 | -2618 | -2250 | Critical Branch | ID schedules | 0 | 368 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7435 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1630 | 8213 |  |  | 8213 |  |  | -2618 | -2618 | -2616 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1730 | 8213 |  |  | 8213 |  |  | -2618 | -2618 | -2616 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1830 | 8683 |  |  | 8683 |  |  | -2334 | -2334 | -2334 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 1930 | 8810 |  |  | 8810 |  |  | -2422 | -2422 | -2422 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 8427 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 2030 | 8683 |  |  | 8683 |  |  | -2109 | -2109 | -2108 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 2130 |  | 8426 | 162 |  | 8110 | 134 | -2413 | -2413 | -2413 | Critical Branch | ID schedules | 0 | NA | 316 | 28 | 344 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | 7750 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 2230 |  | 8735 | 395 |  | 8735 | 395 | -2620 | -2620 | -2620 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | 7839 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-03 | July | 2330 |  | 8183 | 187 |  | 8183 | 187 | -2179 | -2179 | -2179 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-04 | July | 1230 | 6385 |  |  | 6321 |  |  | 0 | 0 | -15 | Critical Branch | ID schedules | 0 | 64 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 1330 | 6385 |  |  | 6321 |  |  | 0 | 0 | -15 | Critical Branch | ID schedules | 0 | 64 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 1430 | 6385 |  |  | 6321 |  |  | 0 | 0 | -15 | Critical Branch | ID schedules | 0 | 64 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 1530 | 7411 |  |  | 7353 |  |  | 0 | 0 | -112 | Critical Branch | ID schedules | 0 | 58 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 1630 | 7411 |  |  | 7353 |  |  | 0 | 0 | -112 | Critical Branch | ID schedules | 0 | 58 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 1730 | 7411 |  |  | 7353 |  |  | 0 | 0 | -112 | Critical Branch | ID schedules | 0 | 58 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 1830 |  | 7340 | 458 |  | 7332 | 437 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 8 | 21 | 29 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-04 | July | 1930 |  | 8353 | 332 |  | 8353 | 244 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 88 | 88 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-04 | July | 2030 |  | 7866 | 332 |  | 7950 | 244 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -84 | 88 | 4 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-04 | July | 2130 | 8534 |  |  | 8426 |  |  | -2130 | -2130 | -2045 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 108 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 2230 | 8685 |  |  | 8685 |  |  | -2382 | -2382 | -2382 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-04 | July | 2330 | 8207 |  |  | 8207 |  |  | -1902 | -1902 | -1902 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1230 | 6877 |  |  | 6877 |  |  | -1439 | -1439 | -1439 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -332 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 332 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1330 | 6877 |  |  | 6877 |  |  | -1439 | -1439 | -1439 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -332 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 332 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1430 | 6877 |  |  | 6877 |  |  | -1439 | -1439 | -1439 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -332 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 332 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1530 | 8365 |  |  | 7029 |  |  | -658 | -658 | 678 | Critical Branch | ID schedules | 0 | 1336 | NA | NA | NA | 678 | 1 | -339 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 339 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1630 | 8365 |  |  | 7029 |  |  | -658 | -658 | 678 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1336 | NA | NA | NA | 678 | 1 | 140 | None | None | 395 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1730 | 8365 |  |  | 6750 |  |  | -658 | -658 | 862 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1615 | NA | NA | NA | 862 | 1 | 140 | None | None | 395 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-05 | July | 1830 |  | 8361 | 781 |  | 8244 | 781 | -3377 | -3377 | -3377 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 117 | 0 | 117 | 0 | 1 | 135 | None | None | 419 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-05 | July | 1930 |  | 8361 | 781 |  | 8361 | 781 | -3377 | -3377 | -3377 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 135 | None | None | 419 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-05 | July | 2030 |  | 8361 | 781 |  | 8361 | 781 | -3377 | -3377 | -3377 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 135 | None | None | 419 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-05 | July | 2130 |  | 8497 | 688 |  | 8497 | 688 | -986 | -986 | -986 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 138 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-05 | July | 2230 |  | 8497 | 688 |  | 8497 | 688 | -986 | -986 | -986 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 138 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-05 | July | 2330 |  | 7937 | 713 |  | 7937 | 713 | -559 | -559 | -559 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 158 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-06 | July | 1230 | 4694 |  |  | 4694 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 272 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-06 | July | 1330 | 4639 |  |  | 4639 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 272 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-06 | July | 1430 | 4609 |  |  | 4609 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 272 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-06 | July | 1530 | 6180 |  |  | 5153 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1027 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 304 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-06 | July | 1630 | 6180 |  |  | 5377 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 803 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 304 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-06 | July | 1730 | 6180 |  |  | 5895 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 285 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 324 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-06 | July | 1830 |  | 7436 | 803 |  | 7436 | 803 | -4248 | -4248 | -4248 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 155 | None | None | 345 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-06 | July | 1930 |  | 8266 | 803 |  | 8266 | 803 | -4916 | -4916 | -4916 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 155 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-06 | July | 2030 |  | 7965 | 803 |  | 8004 | 803 | -4631 | -4631 | -4631 | Critical Branch | ID schedules | 0 | NA | -39 | 0 | -39 | 0 | 1 | 155 | None | None | 275 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-06 | July | 2130 |  | 8537 | 721 |  | 8508 | 721 | -6262 | -6262 | -6262 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 29 | 0 | 29 | 0 | 1 | 158 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-06 | July | 2230 |  | 8537 | 721 |  | 8508 | 721 | -6262 | -6262 | -6262 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 29 | 0 | 29 | 0 | 1 | 158 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-06 | July | 2330 |  | 8306 | 721 |  | 8287 | 721 | -6146 | -6146 | -6146 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 19 | 0 | 19 | 0 | 1 | 158 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-07 | July | 1230 | 7066 |  |  | 7066 |  |  | -2775 | -2775 | -2775 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-07 | July | 1330 | 7086 |  |  | 7086 |  |  | -2798 | -2798 | -2798 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-07 | July | 1430 | 7086 |  |  | 7086 |  |  | -2798 | -2798 | -2798 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-07 | July | 1530 | 7695 |  |  | 7695 |  |  | -4525 | -4525 | -4525 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-07 | July | 1630 | 7705 |  |  | 7705 |  |  | -4537 | -4537 | -4537 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-07 | July | 1730 | 7553 |  |  | 7568 |  |  | -4460 | -4460 | -4468 | ID schedules | ID schedules | 0 | -15 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-07 | July | 1830 |  | 6766 | 636 |  | 6766 | 636 | -3327 | -3327 | -3327 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-07 | July | 1930 |  | 6502 | 636 |  | 6506 | 636 | -3109 | -3109 | -3109 | ID schedules | ID schedules | 0 | NA | -4 | 0 | -4 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5991 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-07 | July | 2030 |  | 6227 | 636 |  | 6228 | 636 | -2978 | -2978 | -2978 | ID schedules | ID schedules | 0 | NA | -1 | 0 | -1 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5651 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-07 | July | 2130 |  | 6847 | 584 |  | 6834 | 584 | -3047 | -3047 | -3047 | ID schedules | ID schedules | 0 | NA | 13 | 0 | 13 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-07 | July | 2230 |  | 6744 | 584 |  | 6738 | 566 | -2997 | -2997 | -2997 | ID schedules | ID schedules | 0 | NA | 6 | 18 | 24 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 6237 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-07 | July | 2330 |  | 6066 | 609 |  | 6066 | 609 | -2462 | -2462 | -2462 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-08 | July | 1230 | 6782 |  |  | 6782 |  |  | -3276 | -3276 | -3260 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1330 | 6567 |  |  | 6567 |  |  | -3084 | -3084 | -3084 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1430 | 6581 |  |  | 6581 |  |  | -3100 | -3100 | -3100 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1530 | 6408 |  |  | 6332 |  |  | -2455 | -2455 | -2383 | Critical Branch | ID schedules | 0 | 76 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1630 | 6408 |  |  | 6332 |  |  | -2455 | -2455 | -2383 | Critical Branch | ID schedules | 0 | 76 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1730 | 6623 |  |  | 6539 |  |  | -2620 | -2620 | -2544 | Critical Branch | ID schedules | 0 | 84 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1830 | 5696 |  |  | 5696 |  |  | -2860 | -2860 | -2860 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 1930 | 5696 |  |  | 5696 |  |  | -2860 | -2860 | -2860 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 2030 | 5696 |  |  | 5696 |  |  | -2860 | -2860 | -2860 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 2130 | 5836 |  |  | 5836 |  |  | -3157 | -3157 | -3157 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 2230 | 5836 |  |  | 5836 |  |  | -3157 | -3157 | -3157 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-08 | July | 2330 | 5236 |  |  | 5236 |  |  | -2554 | -2554 | -2554 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-09 | July | 1230 | 7445 |  |  | 7445 |  |  | -4259 | -4259 | -4259 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-09 | July | 1330 | 7458 |  |  | 7458 |  |  | -4273 | -4273 | -4273 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-09 | July | 1430 | 7611 |  |  | 7611 |  |  | -4439 | -4439 | -4439 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-09 | July | 1530 | 6955 |  |  | 6955 |  |  | -3854 | -3854 | -3854 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 1630 | 6955 |  |  | 6955 |  |  | -3854 | -3854 | -3854 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 1730 | 6955 |  |  | 6955 |  |  | -3854 | -3854 | -3854 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6553 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 1830 | 7081 |  |  | 7081 |  |  | -4148 | -4148 | -4148 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 1930 | 6745 |  |  | 6745 |  |  | -3978 | -3978 | -3978 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 2030 | 6302 |  |  | 6302 |  |  | -3750 | -3750 | -3750 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 2130 | 6650 |  |  | 6650 |  |  | -4827 | -4827 | -4827 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 2230 | 6650 |  |  | 6650 |  |  | -4650 | -4650 | -4644 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-09 | July | 2330 | 6452 |  |  | 6452 |  |  | -4443 | -4443 | -4443 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-10 | July | 1230 | 7820 |  |  | 7820 |  |  | -4972 | -4972 | -4972 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1330 | 7820 |  |  | 7820 |  |  | -4972 | -4972 | -4972 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1430 | 7820 |  |  | 7820 |  |  | -4972 | -4972 | -4972 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1530 | 7909 |  |  | 7909 |  |  | 0 | 0 | -5395 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1630 | 7812 |  |  | 7812 |  |  | 0 | 0 | -5296 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1730 | 7811 |  |  | 7811 |  |  | 0 | 0 | -5295 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 410 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1830 | 7332 |  |  | 7332 |  |  | -6449 | -6449 | -6449 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 336 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 1930 | 7396 |  |  | 7396 |  |  | -6481 | -6481 | -6481 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6804 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-10 | July | 2030 | 6571 |  |  | 6575 |  |  | -6066 | -6066 | -6068 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -4 | NA | NA | NA | 0 | 1 | 140 | None | None | 407 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-10 | July | 2130 |  | 6752 | 822 |  | 6752 | 822 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | -34 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5318 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-10 | July | 2230 |  | 6752 | 793 |  | 6752 | 781 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 12 | 12 | 0 | 1 | 140 | None | None | 89 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5698 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-10 | July | 2330 |  | 6314 | 718 |  | 6200 | 718 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 114 | 0 | 114 | 0 | 1 | 131 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-11 | July | 1230 | 7813 |  |  | 7813 |  |  | -4614 | -4614 | -4614 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | 7354 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 1330 | 7813 |  |  | 7813 |  |  | -4614 | -4614 | -4614 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | 7160 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 1430 | 7813 |  |  | 7813 |  |  | -4614 | -4614 | -4614 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 1530 | 7739 |  |  | 7726 |  |  | -4329 | -4329 | -4320 | Critical Branch | ID schedules | 0 | 13 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 1630 | 7739 |  |  | 7726 |  |  | -4329 | -4329 | -4320 | Critical Branch | ID schedules | 0 | 13 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 1730 | 7739 |  |  | 7506 |  |  | -4329 | -4329 | -4101 | Critical Branch | ID schedules | 0 | 233 | NA | NA | NA | 0 | 1 | 140 | None | None | 420 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 1830 |  | 6046 | 640 |  | 6046 | 640 | -4654 | -4654 | -4654 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 353 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-11 | July | 1930 |  | 6046 | 640 |  | 6046 | 640 | -4654 | -4654 | -4654 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 353 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-11 | July | 2030 |  | 6046 | 640 |  | 6046 | 640 | -4654 | -4654 | -4654 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 353 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-11 | July | 2130 | 7034 |  |  | 6961 |  |  | -4453 | -4453 | -4416 | ID schedules | ID schedules | 0 | 73 | NA | NA | NA | 0 | 1 | 140 | None | None | 383 | None | None | None | 6711 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 2230 | 7007 |  |  | 6947 |  |  | -4439 | -4439 | -4409 | ID schedules | ID schedules | 0 | 60 | NA | NA | NA | 0 | 1 | 140 | None | None | 383 | None | None | None | 6695 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-11 | July | 2330 | 6376 |  |  | 6377 |  |  | -3818 | -3818 | -3819 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 1 | 160 | None | None | 370 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-12 | July | 1230 |  | 5431 | 620 |  | 3829 | 620 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1602 | 0 | 1602 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-12 | July | 1330 |  | 4888 | 657 |  | 4503 | 657 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 385 | 0 | 385 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-12 | July | 1430 |  | 5431 | 620 |  | 3917 | 620 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1514 | 0 | 1514 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-12 | July | 1530 |  | 5817 | 284 |  | 4716 | 284 | -4401 | -4401 | -4401 | Critical Branch | ID schedules | 0 | NA | 1101 | 0 | 1101 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-12 | July | 1630 |  | 6352 | 344 |  | 6343 | 344 | -4702 | -4702 | -4702 | ID schedules | ID schedules | 0 | NA | 9 | 0 | 9 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-12 | July | 1730 |  | 6651 | 671 |  | 6651 | 671 | -4874 | -4874 | -4874 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 6085 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-12 | July | 1830 | 6929 |  |  | 6929 |  |  | -5121 | -5121 | -5121 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6044 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-12 | July | 1930 | 6929 |  |  | 6929 |  |  | -5121 | -5121 | -5121 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6113 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-12 | July | 2030 | 6913 |  |  | 6915 |  |  | -5112 | -5112 | -5113 | ID schedules | ID schedules | 0 | -2 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6231 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-12 | July | 2130 | 6832 |  |  | 6832 |  |  | -4507 | -4507 | -4507 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6451 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-12 | July | 2230 | 6831 |  |  | 6832 |  |  | -4507 | -4507 | -4507 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-12 | July | 2330 | 6232 |  |  | 6232 |  |  | -3906 | -3906 | -3906 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 5892 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-13 | July | 1230 | 6246 |  |  | 5507 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 739 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 372 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 1330 | 6246 |  |  | 5503 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 743 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 372 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 1430 | 6246 |  |  | 5539 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 707 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 372 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 1530 |  | 6252 | 1006 |  | 5679 | 980 | -4687 | -4687 | -4687 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 573 | 26 | 599 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-13 | July | 1630 |  | 6370 | 996 |  | 5588 | 972 | -4738 | -4738 | -4738 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 782 | 24 | 806 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-13 | July | 1730 |  | 6272 | 1006 |  | 6176 | 980 | -4714 | -4714 | -4714 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 96 | 26 | 122 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-13 | July | 1830 | 6459 |  |  | 6459 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 395 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 1930 | 6548 |  |  | 6548 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 395 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 2030 | 6249 |  |  | 6249 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 2130 | 6509 |  |  | 6509 |  |  | -5478 | -5478 | -5478 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 2230 | 6431 |  |  | 6431 |  |  | -5436 | -5436 | -5436 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 364 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-13 | July | 2330 | 6531 |  |  | 6531 |  |  | -5491 | -5491 | -5491 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1230 | 7846 |  |  | 7846 |  |  | -4884 | -4884 | -4884 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1330 | 7846 |  |  | 7846 |  |  | -4884 | -4884 | -4884 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6967 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1430 | 7846 |  |  | 7846 |  |  | -4884 | -4884 | -4884 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6823 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1530 | 7526 |  |  | 7526 |  |  | -4600 | -4600 | -4600 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1630 | 7526 |  |  | 7526 |  |  | -4600 | -4600 | -4600 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1730 | 7052 |  |  | 7052 |  |  | -4346 | -4346 | -4346 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1830 | 6286 |  |  | 6286 |  |  | -3801 | -3801 | -3801 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 1930 | 5851 |  |  | 5851 |  |  | -3604 | -3604 | -3604 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-14 | July | 2030 | 5649 |  |  | 5649 |  |  | -3504 | -3504 | -3497 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 252 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-14 | July | 2130 |  | 6490 | 619 |  | 6490 | 619 | -5642 | -5642 | -5642 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 139 | None | None | 315 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-14 | July | 2230 |  | 6566 | 619 |  | 6566 | 619 | -5709 | -5709 | -5709 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 139 | None | None | 391 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-14 | July | 2330 |  | 5987 | 587 |  | 5987 | 520 | -5386 | -5386 | -5386 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 67 | 67 | 0 | 1 | 160 | None | None | 378 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4958 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-15 | July | 1230 | 7499 |  |  | 7499 |  |  | -1441 | -1441 | -1441 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1330 | 7499 |  |  | 7499 |  |  | -1441 | -1441 | -1441 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1430 | 7499 |  |  | 7499 |  |  | -1441 | -1441 | -1441 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1530 | 7461 |  |  | 7412 |  |  | -2807 | -2807 | -2757 | Critical Branch | ID schedules | 0 | 49 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1630 | 7461 |  |  | 7412 |  |  | -2807 | -2807 | -2757 | Critical Branch | ID schedules | 0 | 49 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1730 | 7461 |  |  | 7165 |  |  | -2807 | -2807 | -2511 | Critical Branch | ID schedules | 0 | 296 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1830 | 5578 |  |  | 5578 |  |  | -3566 | -3566 | -3566 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 1930 | 5519 |  |  | 5530 |  |  | -3538 | -3538 | -3543 | ID schedules | ID schedules | 0 | -11 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 2030 | 5206 |  |  | 5206 |  |  | -3386 | -3386 | -3386 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 2130 | 6750 |  |  | 6750 |  |  | -4864 | -4864 | -4864 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 2230 | 6749 |  |  | 6749 |  |  | -4863 | -4863 | -4863 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-15 | July | 2330 | 6150 |  |  | 6150 |  |  | -4262 | -4262 | -4262 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-16 | July | 1230 | 7385 |  |  | 7385 |  |  | -3972 | -3972 | -3970 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 1330 | 7385 |  |  | 7385 |  |  | -3972 | -3972 | -3970 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 1430 | 7385 |  |  | 7385 |  |  | -3972 | -3972 | -3970 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 1530 | 7758 |  |  | 7749 |  |  | -3588 | -3588 | -3582 | Critical Branch | Smoothing ramp | 0 | 9 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 1630 | 7758 |  |  | 7749 |  |  | -3588 | -3588 | -3582 | Critical Branch | ID schedules | 0 | 9 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 1730 | 7758 |  |  | 7533 |  |  | -3588 | -3588 | -3368 | Critical Branch | ID schedules | 0 | 225 | NA | NA | NA | 0 | 1 | 140 | None | None | 419 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 1830 |  | 6152 | 600 |  | 6152 | 471 | -4976 | -4976 | -4976 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 129 | 129 | 0 | 1 | -360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-16 | July | 1930 |  | 6152 | 600 |  | 6152 | 525 | -4883 | -4883 | -4883 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 75 | 75 | 0 | 1 | -360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-16 | July | 2030 |  | 6152 | 600 |  | 6152 | 462 | -4858 | -4858 | -4858 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 138 | 138 | 0 | 1 | -360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-16 | July | 2130 |  | 7042 | 735 |  | 6363 | 277 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 679 | 458 | 1137 | 0 | 1 | -366 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-16 | July | 2230 |  | 7042 | 735 |  | 6363 | 280 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 679 | 455 | 1134 | 0 | 1 | 136 | None | None | 373 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-16 | July | 2330 |  | 6482 | 760 |  | 5695 | -192 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 787 | 952 | 1739 | 0 | 1 | 156 | None | None | 352 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1230 | 7081 |  |  | 7081 |  |  | -704 | -704 | -704 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 200 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1330 | 7081 |  |  | 7081 |  |  | -704 | -704 | -704 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 200 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1430 | 7081 |  |  | 7081 |  |  | -704 | -704 | -704 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 200 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1530 | 7116 |  |  | 7115 |  |  | -2647 | -2647 | -2645 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 70 | None | None | 201 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1630 | 7331 |  |  | 7132 |  |  | -2813 | -2813 | -2690 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 199 | NA | NA | NA | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 210 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1730 | 7331 |  |  | 7330 |  |  | -2813 | -2813 | -2811 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 140 | None | None | 408 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1830 | 7124 |  |  | 7124 |  |  | -5725 | -5725 | -5725 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 403 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 1930 | 7023 |  |  | 7019 |  |  | -5666 | -5666 | -5664 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 4 | NA | NA | NA | 0 | 1 | 140 | None | None | 338 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 2030 | 7023 |  |  | 7023 |  |  | -5671 | -5671 | -5671 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 403 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 2130 | 6876 |  |  | 6876 |  |  | -3898 | -3898 | -3898 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 373 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 2230 | 6853 |  |  | 6853 |  |  | -3886 | -3886 | -3886 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 372 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-17 | July | 2330 | 6277 |  |  | 6277 |  |  | -3293 | -3293 | -3293 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 360 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-18 | July | 1230 | 7792 |  |  | 7340 |  |  | -4083 | -4083 | -3595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 452 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2000 | None | Bilateral - Unplanned outage MERY VIELMOULIN 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 1330 | 7792 |  |  | 7340 |  |  | -4083 | -4083 | -3595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 452 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2000 | None | Bilateral - Unplanned outage MERY VIELMOULIN 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 1430 | 7792 |  |  | 7340 |  |  | -4083 | -4083 | -3595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 452 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2000 | None | Bilateral - Unplanned outage MERY VIELMOULIN 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 1530 | 7059 |  |  | 6890 |  |  | -4513 | -4513 | -4333 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 169 | NA | NA | NA | 0 | 1 | 140 | None | None | 409 | None | None | None | None | None | None | None | None | 2000 | None | Bilateral - Unplanned outage MERY VIELMOULIN 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 1630 | 7059 |  |  | 6890 |  |  | -4513 | -4513 | -4333 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 169 | NA | NA | NA | 0 | 1 | 140 | None | None | 409 | None | None | None | None | None | None | None | None | 2000 | None | Bilateral - Unplanned outage MERY VIELMOULIN 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 1730 | 7059 |  |  | 6803 |  |  | -4562 | -4562 | -4287 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 256 | NA | NA | NA | 0 | 1 | 140 | None | None | 409 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 1830 | 6485 |  |  | 6507 |  |  | -5849 | -5849 | -5860 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -22 | NA | NA | NA | 0 | 1 | 140 | None | None | 400 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-18 | July | 1930 | 6662 |  |  | 6662 |  |  | -5941 | -5941 | -5941 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 400 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-18 | July | 2030 | 6226 |  |  | 6226 |  |  | -5716 | -5716 | -5716 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 139 | None | None | 400 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-18 | July | 2130 | 6311 |  |  | 6329 |  |  | -4017 | -4017 | -4026 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -18 | NA | NA | NA | 0 | 1 | 140 | None | None | 380 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-18 | July | 2230 | 6709 |  |  | 6709 |  |  | -4232 | -4232 | -4232 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 380 | None | None | None | 6291 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-18 | July | 2330 | 6384 |  |  | 6384 |  |  | -3912 | -3912 | -3912 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 367 | None | None | None | 5976 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-19 | July | 1230 | 7813 |  |  | 7813 |  |  | -1366 | -1366 | -1366 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6877 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-19 | July | 1330 | 7813 |  |  | 7813 |  |  | -1366 | -1366 | -1366 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7137 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-19 | July | 1430 | 7813 |  |  | 7813 |  |  | -1366 | -1366 | -1366 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7261 | Missing CNEC in CC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-19 | July | 1530 | 7210 |  |  | 7210 |  |  | -2904 | -2904 | -2904 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -393 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 393 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-19 | July | 1630 | 7210 |  |  | 7210 |  |  | -2904 | -2904 | -2904 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -393 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 393 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-19 | July | 1730 | 7210 |  |  | 7210 |  |  | -2904 | -2904 | -2904 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 393 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-19 | July | 1830 |  | 5921 | 712 |  | 5384 | 712 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 537 | 0 | 537 | 0 | 1 | 137 | None | None | 311 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-19 | July | 1930 |  | 5921 | 712 |  | 5384 | 712 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 537 | 0 | 537 | 0 | 1 | 137 | None | None | 311 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-19 | July | 2030 |  | 5921 | 712 |  | 5384 | 712 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 537 | 0 | 537 | 0 | 1 | 137 | None | None | 311 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-19 | July | 2130 |  | 5396 | 666 |  | 5382 | 666 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 0 | 1 | 139 | None | None | 312 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-19 | July | 2230 |  | 5396 | 666 |  | 5382 | 666 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 0 | 1 | 139 | None | None | 312 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-19 | July | 2330 |  | 4836 | 691 |  | 4822 | 691 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 0 | 1 | 159 | None | None | 294 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-20 | July | 1230 | 5324 |  |  | 4205 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 1119 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 1330 | 5324 |  |  | 4200 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 1124 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 1430 | 5324 |  |  | 5010 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 314 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 1530 | 6405 |  |  | 5103 |  |  | -3653 | -3653 | -2509 | Critical Branch | ID schedules | 0 | 1302 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 1630 | 6700 |  |  | 6700 |  |  | -3983 | -3983 | -3983 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 1730 | 6906 |  |  | 6935 |  |  | -4205 | -4205 | -4220 | ID schedules | ID schedules | 0 | -29 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 1830 |  | 5655 | 593 |  | 5655 | 593 | -5479 | -5479 | -5479 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-20 | July | 1930 |  | 5655 | 593 |  | 5655 | 589 | -5313 | -5313 | -5313 | ID schedules | ID schedules | 0 | NA | 0 | 4 | 4 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5260 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-20 | July | 2030 |  | 5655 | 593 |  | 5655 | 575 | -5427 | -5427 | -5427 | ID schedules | ID schedules | 0 | NA | 0 | 18 | 18 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5233 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-20 | July | 2130 | 5696 |  |  | 5696 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 2230 | 5810 |  |  | 5810 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 5107 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-20 | July | 2330 | 5810 |  |  | 5810 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 4808 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1230 | 7600 |  |  | 7600 |  |  | -5019 | -5019 | -5019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1330 | 7600 |  |  | 7600 |  |  | -5019 | -5019 | -5019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7053 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1430 | 7600 |  |  | 7600 |  |  | -5019 | -5019 | -5019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6769 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1530 | 7600 |  |  | 7600 |  |  | -4719 | -4719 | -4719 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6814 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1630 | 7600 |  |  | 7600 |  |  | -4719 | -4719 | -4719 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6885 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1730 | 6797 |  |  | 6797 |  |  | -4304 | -4304 | -4304 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-21 | July | 1830 |  | 6110 | 723 |  | 6110 | 723 | -5250 | -5250 | -5250 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 137 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-21 | July | 1930 |  | 6047 | 723 |  | 6047 | 723 | -5217 | -5217 | -5217 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 137 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-21 | July | 2030 |  | 6110 | 723 |  | 6110 | 723 | -5250 | -5250 | -5250 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 137 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-21 | July | 2130 | 5916 |  |  | 5916 |  |  | -4143 | -4143 | -4143 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-21 | July | 2230 | 6203 |  |  | 6203 |  |  | -4296 | -4296 | -4296 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-21 | July | 2330 | 5346 |  |  | 5365 |  |  | -3551 | -3551 | -3561 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -19 | NA | NA | NA | 0 | 1 | 160 | None | None | 352 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1230 | 7840 |  |  | 7840 |  |  | -6036 | -6036 | -6036 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7057 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1330 | 7840 |  |  | 7840 |  |  | -6036 | -6036 | -6036 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7484 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1430 | 7840 |  |  | 7840 |  |  | -6036 | -6036 | -6036 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7445 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1530 | 7801 |  |  | 7801 |  |  | -6693 | -6693 | -6693 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1630 | 7548 |  |  | 7601 |  |  | -6567 | -6567 | -6593 | ID schedules | ID schedules | 0 | -53 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7203 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1730 | 7801 |  |  | 7801 |  |  | -6693 | -6693 | -6693 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7466 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1830 | 6745 |  |  | 6753 |  |  | -5520 | -5520 | -5524 | ID schedules | ID schedules | 0 | -8 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6444 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 1930 | 6473 |  |  | 6473 |  |  | -5379 | -5379 | -5379 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 5268 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 2030 | 6474 |  |  | 6474 |  |  | -5379 | -5379 | -5379 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6223 | Calculation Failed, reduction based on IDCF prognose | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 2130 |  | 6564 | 463 |  | 6564 | 429 | -5476 | -5476 | -5476 | ID schedules | ID schedules | 0 | NA | 0 | 34 | 34 | 0 | 1 | None | None | None | None | None | None | None | None | Calculation Failed, reduction based on IDCF prognose | None | 5941 | Calculation Failed, reduction based on IDCF prognose | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 2230 |  | 6564 | 555 |  | 6564 | 558 | -5440 | -5440 | -5440 | ID schedules | ID schedules | 0 | NA | 0 | -3 | -3 | 0 | 1 | None | None | None | None | None | None | None | None | Calculation Failed, reduction based on IDCF prognose | None | 5796 | Calculation Failed, reduction based on IDCF prognose | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-22 | July | 2330 |  | 6005 | 488 |  | 6005 | 488 | -5271 | -5271 | -5271 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Calculation Failed, reduction based on IDCF prognose | None | 6199 | Calculation Failed, reduction based on IDCF prognose | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1230 | 7759 |  |  | 7759 |  |  | -1481 | -1481 | -1481 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1330 | 7759 |  |  | 7759 |  |  | -1481 | -1481 | -1481 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1430 | 7759 |  |  | 7759 |  |  | -1481 | -1481 | -1481 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1530 | 7501 |  |  | 7501 |  |  | -293 | -293 | -293 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1630 | 8801 |  |  | 8801 |  |  | -1417 | -1417 | -1417 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1730 | 8801 |  |  | 8801 |  |  | -1417 | -1417 | -1417 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1830 |  | 7927 | 617 |  | 7927 | 617 | -4576 | -4576 | -4576 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 1930 |  | 7927 | 519 |  | 7927 | 519 | -4563 | -4563 | -4563 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 2030 |  | 7927 | 519 |  | 7927 | 519 | -4563 | -4563 | -4563 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 2130 |  | 7892 | 622 |  | 7892 | 622 | -5030 | -5030 | -5030 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 2230 |  | 7892 | 622 |  | 7892 | 622 | -4978 | -4978 | -4978 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-23 | July | 2330 |  | 7333 | 647 |  | 7333 | 647 | -4378 | -4378 | -4378 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1230 | 8482 |  |  | 8482 |  |  | 0 | 0 | -2964 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1330 | 8482 |  |  | 8482 |  |  | 0 | 0 | -2964 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1430 | 8482 |  |  | 8482 |  |  | 0 | 0 | -2964 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1530 | 8437 |  |  | 8437 |  |  | -3084 | -3084 | -3084 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1630 | 8437 |  |  | 8437 |  |  | -3084 | -3084 | -3084 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1730 | 7864 |  |  | 7864 |  |  | -2802 | -2802 | -2802 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1830 |  | 7749 | 653 |  | 7749 | 651 | -6679 | -6679 | -6679 | ID schedules | ID schedules | 0 | NA | 0 | 2 | 2 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-2 Pradella-Robbia + Pradella-Sils | None | 7431 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-2 Pradella-Robbia + Pradella-Sils | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 1930 |  | 7749 | 653 |  | 7749 | 653 | -6679 | -6679 | -6679 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 2030 |  | 7749 | 653 |  | 7749 | 653 | -6679 | -6679 | -6679 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 2130 |  | 7715 | 630 |  | 7715 | 630 | -5307 | -5307 | -5307 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 2230 |  | 7624 | 651 |  | 7637 | 651 | -5169 | -5169 | -5169 | ID schedules | ID schedules | 0 | NA | -13 | 0 | -13 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-24 | July | 2330 |  | 7407 | 655 |  | 7407 | 655 | -5226 | -5226 | -5226 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-25 | July | 1230 | 8065 |  |  | 7234 |  |  | 0 | 0 | 598 | Critical Branch | ID schedules | 0 | 831 | NA | NA | NA | 598 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-25 | July | 1330 | 8065 |  |  | 7234 |  |  | 0 | 0 | 598 | Critical Branch | ID schedules | 0 | 831 | NA | NA | NA | 598 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-25 | July | 1430 | 8065 |  |  | 7234 |  |  | 0 | 0 | 598 | Critical Branch | ID schedules | 0 | 831 | NA | NA | NA | 598 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-25 | July | 1530 |  | 7998 | 723 |  | 7635 | 723 | -433 | -433 | -433 | Critical Branch | ID schedules | 0 | NA | 363 | 0 | 363 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 1630 |  | 8204 | 723 |  | 7844 | 723 | -498 | -498 | -498 | Critical Branch | ID schedules | 0 | NA | 360 | 0 | 360 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 1730 |  | 8204 | 723 |  | 7844 | 723 | -498 | -498 | -498 | Critical Branch | ID schedules | 0 | NA | 360 | 0 | 360 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 1830 |  | 7702 | 594 |  | 7702 | 594 | -4677 | -4677 | -4677 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 1930 |  | 7702 | 570 |  | 7702 | 570 | -4681 | -4681 | -4681 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 2030 |  | 7702 | 570 |  | 7702 | 570 | -4681 | -4681 | -4681 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 2130 |  | 8140 | 660 |  | 8140 | 660 | -5656 | -5656 | -5656 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 2230 |  | 7995 | 660 |  | 7995 | 660 | -5567 | -5567 | -5567 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-25 | July | 2330 |  | 7580 | 685 |  | 7580 | 685 | -5055 | -5055 | -5055 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-26 | July | 1230 | 8281 |  |  | 8281 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-26 | July | 1330 | 8281 |  |  | 8281 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-26 | July | 1430 | 8095 |  |  | 8132 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -37 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-26 | July | 1530 | 8037 |  |  | 7572 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 465 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-26 | July | 1630 | 8037 |  |  | 7232 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 805 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-26 | July | 1730 | 8037 |  |  | 6925 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1112 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-26 | July | 1830 | 8037 |  |  | 6662 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1375 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-26 | July | 1930 | 8037 |  |  | 8037 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-26 | July | 2030 | 8037 |  |  | 8037 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-26 | July | 2130 | 8037 |  |  | 8037 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-26 | July | 2230 | 8037 |  |  | 8037 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-26 | July | 2330 | 7437 |  |  | 7437 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-27 | July | 1230 |  | 2785 | 727 |  | 2751 | 727 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 34 | 0 | 34 | 0 | 1 | 157 | None | None | -130 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-27 | July | 1330 |  | 2992 | 727 |  | 2967 | 727 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 25 | 0 | 25 | 0 | 1 | 157 | None | None | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-27 | July | 1430 |  | 3220 | 540 |  | 3220 | 540 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 159 | None | None | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-27 | July | 1530 |  | 5864 | 834 |  | 4282 | 880 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1582 | -46 | 1536 | 0 | 1 | 151 | None | None | 415 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-27 | July | 1630 |  | 5793 | 897 |  | 5793 | 892 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 5 | 5 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | -158 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-27 | July | 1730 |  | 6000 | 884 |  | 6000 | 892 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -8 | -8 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-27 | July | 1830 | 7797 |  |  | 7798 |  |  | -2884 | -2884 | -2885 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -1 | NA | NA | NA | 0 | 1 | 160 | None | None | 390 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-27 | July | 1930 | 7825 |  |  | 7825 |  |  | -2899 | -2899 | -2899 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 390 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-27 | July | 2030 | 7556 |  |  | 7556 |  |  | -2763 | -2763 | -2763 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 390 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-27 | July | 2130 |  | 7982 | 734 |  | 7981 | 734 | -3196 | -3196 | -3196 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 157 | None | None | 405 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-27 | July | 2230 |  | 7982 | 734 |  | 7981 | 734 | -3196 | -3196 | -3196 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 157 | None | None | 405 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-27 | July | 2330 |  | 7754 | 734 |  | 7754 | 734 | -2962 | -2962 | -2962 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 0 | 1 | 157 | None | None | 405 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-28 | July | 1230 | 8934 |  |  | 7707 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1227 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 3200 | None | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 1330 | 8934 |  |  | 7707 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1227 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 3200 | None | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 1430 | 8934 |  |  | 7707 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1227 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 3200 | None | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 1530 | 7603 |  |  | 7603 |  |  | 0 | 0 | -3742 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 1630 | 8327 |  |  | 8327 |  |  | -4493 | -4493 | -4493 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 1730 | 8094 |  |  | 8136 |  |  | -4415 | -4415 | -4429 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -42 | NA | NA | NA | 0 | 1 | 140 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 1830 |  | 7686 | 781 |  | 7686 | 781 | -4566 | -4566 | -4566 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 134 | None | None | 425 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-28 | July | 1930 |  | 7736 | 781 |  | 7736 | 781 | -4595 | -4595 | -4595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 134 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-28 | July | 2030 |  | 7736 | 781 |  | 7736 | 781 | -4595 | -4595 | -4595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 134 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 396 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-07-28 | July | 2130 | 7540 |  |  | 7540 |  |  | -4614 | -4614 | -4614 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 2230 | 7883 |  |  | 7883 |  |  | -4667 | -4667 | -4667 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-28 | July | 2330 | 7802 |  |  | 7802 |  |  | -4601 | -4601 | -4601 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-07-29 | July | 1230 | 8039 |  |  | 8039 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1330 | 8039 |  |  | 8039 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1430 | 8039 |  |  | 8039 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1530 | 8222 |  |  | 8222 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1630 | 7901 |  |  | 7914 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -13 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1730 | 8421 |  |  | 8444 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -23 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1830 | 8206 |  |  | 8212 |  |  | -5470 | -5470 | -5473 | ID schedules | ID schedules | 0 | -6 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 1930 | 8805 |  |  | 8805 |  |  | -5794 | -5794 | -5794 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 2030 | 7854 |  |  | 7854 |  |  | -5279 | -5279 | -5279 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 2130 |  | 8878 | 730 |  | 8878 | 730 | -3968 | -3968 | -3968 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 2230 |  | 8878 | 727 |  | 8878 | 727 | -4075 | -4075 | -4075 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-29 | July | 2330 |  | 8298 | 734 |  | 8298 | 714 | -3816 | -3816 | -3816 | ID schedules | ID schedules | 0 | NA | 0 | 20 | 20 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 SOAZZA-BULCIAGO | None | 7795 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 SOAZZA-BULCIAGO | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1230 | 6475 |  |  | 6475 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1330 | 6475 |  |  | 6475 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1430 | 6475 |  |  | 6475 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1530 | 8830 |  |  | 7975 |  |  | 0 | 0 | -142 | Critical Branch | Smoothing ramp | 0 | 855 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1630 | 8830 |  |  | 8830 |  |  | -999 | -999 | -997 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1730 | 8830 |  |  | 8830 |  |  | -999 | -999 | -997 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1830 |  | 7855 | 656 |  | 7855 | 656 | -1623 | -1623 | -1623 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 1930 |  | 7855 | 656 |  | 7855 | 656 | -1623 | -1623 | -1623 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 2030 |  | 7855 | 656 |  | 7855 | 656 | -1623 | -1623 | -1623 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 2130 | 8356 |  |  | 8356 |  |  | -1192 | -1192 | -1192 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 2230 | 8856 |  |  | 8856 |  |  | -1521 | -1521 | -1521 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-30 | July | 2330 | 8119 |  |  | 8128 |  |  | -811 | -811 | -817 | ID schedules | ID schedules | 0 | -9 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1230 | 8163 |  |  | 8163 |  |  | -3271 | -3271 | -3271 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1330 | 8163 |  |  | 8163 |  |  | -3271 | -3271 | -3271 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1430 | 8163 |  |  | 8163 |  |  | -3271 | -3271 | -3271 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1530 | 8470 |  |  | 8470 |  |  | -4218 | -4218 | -4218 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1630 | 8470 |  |  | 8470 |  |  | -4218 | -4218 | -4218 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1730 | 8470 |  |  | 8470 |  |  | -4218 | -4218 | -4218 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1830 |  | 8568 | 672 |  | 8568 | 672 | -2655 | -2655 | -2655 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 1930 |  | 8568 | 672 |  | 8568 | 671 | -2530 | -2530 | -2530 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | 8002 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 2030 |  | 8559 | 513 |  | 8568 | 513 | -2241 | -2241 | -2241 | ID schedules | ID schedules | 0 | NA | -9 | 0 | -9 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 2130 | 8415 |  |  | 8423 |  |  | -6036 | -6036 | -6042 | ID schedules | ID schedules | 0 | -8 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 2230 | 8945 |  |  | 8945 |  |  | -6339 | -6339 | -6339 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-07-31 | July | 2330 | 8387 |  |  | 8387 |  |  | -5749 | -5749 | -5749 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-01 | August | 1230 | 8061 |  |  | 8061 |  |  | 1101 | -81 | 1101 | ID schedules | ID schedules | 1182 | 0 | NA | NA | NA | -81 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-01 | August | 1330 | 8022 |  |  | 8022 |  |  | 1101 | -81 | 1101 | ID schedules | ID schedules | 1182 | 0 | NA | NA | NA | -81 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-01 | August | 1430 | 8069 |  |  | 8069 |  |  | 1101 | -81 | 1101 | ID schedules | ID schedules | 1182 | 0 | NA | NA | NA | -81 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-01 | August | 1530 | 7487 |  |  | 7443 |  |  | 2219 | -88 | 2219 | Critical Branch | ID schedules | 2307 | 44 | NA | NA | NA | -88 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-01 | August | 1630 | 7487 |  |  | 7487 |  |  | 2219 | -88 | 2219 | Critical Branch | ID schedules | 2307 | 0 | NA | NA | NA | -88 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-01 | August | 1730 | 7487 |  |  | 7475 |  |  | 2219 | -88 | 2219 | Critical Branch | ID schedules | 2307 | 12 | NA | NA | NA | -88 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-01 | August | 1830 |  | 8292 | 665 |  | 8045 | 665 | 818 | 247 | 818 | Minimum Margin | ID schedules | 571 | NA | 247 | 0 | 247 | 247 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3633 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-01 | August | 1930 |  | 8292 | 665 |  | 8045 | 665 | 944 | 247 | 944 | Minimum Margin | ID schedules | 697 | NA | 247 | 0 | 247 | 247 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3468 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-01 | August | 2030 |  | 8287 | 686 |  | 7975 | 686 | 943 | 247 | 943 | Minimum Margin | ID schedules | 696 | NA | 312 | 0 | 312 | 247 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3439 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-01 | August | 2130 |  | 8279 | 680 |  | 7905 | 680 | -976 | -976 | -976 | Critical Branch | ID schedules | 0 | NA | 374 | 0 | 374 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-01 | August | 2230 |  | 8274 | 680 |  | 7998 | 680 | -968 | -968 | -968 | Critical Branch | ID schedules | 0 | NA | 276 | 0 | 276 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-01 | August | 2330 |  | 7654 | 705 |  | 7464 | 705 | -317 | -317 | -317 | Critical Branch | ID schedules | 0 | NA | 190 | 0 | 190 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-02 | August | 1230 |  | 3980 | 603 |  | 2648 | 603 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1332 | 0 | 1332 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1330 |  | 3352 | 651 |  | 3280 | 651 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 72 | 0 | 72 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1430 |  | 3980 | 603 |  | 3149 | 603 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 831 | 0 | 831 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1530 |  | 3459 | 804 |  | 3595 | 813 | 3797 | -129 | 3797 | ID schedules | TTC Validation phase - bilateral reduction | 3926 | NA | -136 | -9 | -145 | -129 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -79 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1630 |  | 4704 | 816 |  | 4704 | 816 | 2146 | -129 | 2146 | ID schedules | TTC Validation phase - bilateral reduction | 2275 | NA | 0 | 0 | 0 | -129 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1730 |  | 6204 | 816 |  | 6204 | 816 | 466 | -129 | 466 | ID schedules | TTC Validation phase - bilateral reduction | 595 | NA | 0 | 0 | 0 | -129 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1830 |  | 7902 | 681 |  | 7619 | 681 | -4168 | -4168 | -4168 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 283 | 0 | 283 | 0 | 1 | 138 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 319 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 1930 |  | 7902 | 681 |  | 7865 | 681 | -4168 | -4168 | -4168 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 37 | 0 | 37 | 0 | 1 | 138 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 319 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 2030 |  | 7902 | 681 |  | 7865 | 681 | -4168 | -4168 | -4168 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 37 | 0 | 37 | 0 | 1 | 138 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 319 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 2130 |  | 8221 | 678 |  | 8221 | 678 | -5198 | -5198 | -5198 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 138 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 2230 |  | 8221 | 678 |  | 8221 | 678 | -5198 | -5198 | -5198 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 138 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-02 | August | 2330 |  | 7674 | 703 |  | 7646 | 703 | -4605 | -4605 | -4605 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 28 | 0 | 28 | 0 | 1 | 158 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 405 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-03 | August | 1230 |  | 642 | 596 |  | 642 | 596 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1330 |  | 1113 | 530 |  | 312 | 530 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 801 | 0 | 801 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1430 |  | 1113 | 530 |  | 284 | 530 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 829 | 0 | 829 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1530 |  | 2192 | 723 |  | 649 | 686 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1543 | 37 | 1580 | 0 | 1 | 149 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 157 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1630 |  | 2191 | 753 |  | 2191 | 753 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 156 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1730 |  | 3711 | 773 |  | 3711 | 773 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1830 |  | 6917 | 1004 |  | 5362 | 981 | -3967 | -3967 | -3967 | ID schedules | ID schedules | 0 | NA | 1555 | 23 | 1578 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 1930 |  | 7332 | 1004 |  | 6862 | 981 | -4095 | -4095 | -4095 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 470 | 23 | 493 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 2030 |  | 7201 | 962 |  | 6930 | 942 | -4021 | -4021 | -4021 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 271 | 20 | 291 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-03 | August | 2130 | 8995 |  |  | 7744 |  |  | -4793 | -4793 | -3608 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1251 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-03 | August | 2230 | 8995 |  |  | 7966 |  |  | -4789 | -4789 | -3780 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1029 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-03 | August | 2330 | 8995 |  |  | 7736 |  |  | -4780 | -4780 | -3408 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1259 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-04 | August | 1230 |  | 4813 | 172 |  | 4813 | 172 | -1995 | -1995 | -1995 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-04 | August | 1330 |  | 4813 | 172 |  | 4813 | 172 | -1995 | -1995 | -1995 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 47 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-04 | August | 1430 |  | 4813 | 172 |  | 4813 | 172 | -1995 | -1995 | -1995 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 47 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-04 | August | 1530 |  | 4715 | 172 |  | 4715 | 172 | -1771 | -1771 | -1771 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | -5 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-04 | August | 1630 |  | 4715 | 172 |  | 4715 | 172 | -1771 | -1771 | -1771 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | -5 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-04 | August | 1730 |  | 5726 | 130 |  | 5726 | 129 | -2959 | -2959 | -2959 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 0 | 1 | 97 | None | None | 242 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-04 | August | 1830 | 6257 |  |  | 6257 |  |  | -2796 | -2796 | -2796 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 369 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-04 | August | 1930 | 6257 |  |  | 6257 |  |  | -2796 | -2796 | -2796 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 369 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-04 | August | 2030 | 6257 |  |  | 6257 |  |  | -2796 | -2796 | -2796 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 369 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-04 | August | 2130 | 5676 |  |  | 5676 |  |  | -2346 | -2346 | -2346 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 332 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-04 | August | 2230 | 5377 |  |  | 5377 |  |  | -2039 | -2039 | -2039 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 328 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-04 | August | 2330 | 4817 |  |  | 4817 |  |  | -1473 | -1473 | -1473 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 159 | None | None | 311 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-05 | August | 1230 |  | 5115 | 172 |  | 5115 | 172 | -1225 | -1225 | -1225 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 137 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 1330 |  | 5115 | 172 |  | 5115 | 172 | -1225 | -1225 | -1225 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 137 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 1430 |  | 5115 | 172 |  | 5115 | 172 | -1225 | -1225 | -1225 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 137 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 1530 |  | 5388 | 172 |  | 5388 | 172 | -1929 | -1929 | -1929 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-05 | August | 1630 |  | 5388 | 172 |  | 5388 | 172 | -1929 | -1929 | -1929 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-05 | August | 1730 |  | 5388 | 153 |  | 5388 | -299 | -1929 | -1929 | -1929 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 452 | 452 | 0 | 1 | -331 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-05 | August | 1830 | 5764 |  |  | 5603 |  |  | 158 | 158 | 162 | Adjustment reached | ID schedules | 0 | 161 | NA | NA | NA | 162 | 1 | -311 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 5353 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-05 | August | 1930 | 5764 |  |  | 5603 |  |  | 158 | 158 | 162 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 161 | NA | NA | NA | 162 | 1 | 140 | None | None | 338 | None | None | None | None | None | None | None | None | None | 5353 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 2030 | 5764 |  |  | 5603 |  |  | 158 | 158 | 162 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 161 | NA | NA | NA | 162 | 1 | 140 | None | None | 338 | None | None | None | None | None | None | None | None | None | 5353 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 2130 | 5828 |  |  | 5828 |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 342 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 2230 | 5528 |  |  | 5528 |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 338 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-05 | August | 2330 | 4968 |  |  | 4968 |  |  | 0 | 0 | 0 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 159 | None | None | 322 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-06 | August | 1230 | 7088 |  |  | 7088 |  |  | -1035 | -1035 | -1035 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6722 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1330 | 7100 |  |  | 7100 |  |  | -1047 | -1047 | -1047 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6785 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1430 | 7106 |  |  | 7106 |  |  | -1053 | -1053 | -1053 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6705 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1530 | 7100 |  |  | 7100 |  |  | -4302 | -4302 | -4302 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6041 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1630 | 7106 |  |  | 7106 |  |  | -4308 | -4308 | -4308 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 419 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6684 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1730 | 7116 |  |  | 7116 |  |  | -4318 | -4318 | -4318 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1830 | 5614 |  |  | 5614 |  |  | -4187 | -4187 | -4187 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 328 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-06 | August | 1930 | 5614 |  |  | 5614 |  |  | -4187 | -4187 | -4187 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 328 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-06 | August | 2030 | 5146 |  |  | 5146 |  |  | -3877 | -3877 | -3877 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | -140 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-06 | August | 2130 | 5688 |  |  | 5643 |  |  | -4001 | -4001 | -3955 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 45 | NA | NA | NA | 0 | 1 | 140 | None | None | 35 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-06 | August | 2230 | 5739 |  |  | 5739 |  |  | -4057 | -4057 | -4057 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 20 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-06 | August | 2330 | 5570 |  |  | 5570 |  |  | -3775 | -3775 | -3775 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 159 | None | None | 347 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 1230 | 6000 |  |  | 6000 |  |  | -1081 | -1081 | -1081 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5458 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-07 | August | 1330 | 6000 |  |  | 6000 |  |  | -1081 | -1081 | -1081 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5469 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-07 | August | 1430 | 6000 |  |  | 6000 |  |  | -1081 | -1081 | -1081 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5344 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-07 | August | 1530 | 6000 |  |  | 6000 |  |  | -2880 | -2880 | -2880 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5605 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-07 | August | 1630 | 6455 |  |  | 6455 |  |  | -3345 | -3345 | -3345 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 382 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-07 | August | 1730 | 6455 |  |  | 6455 |  |  | -3345 | -3345 | -3345 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 382 | None | None | None | 6031 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 1830 | 5676 |  |  | 5676 |  |  | -4072 | -4072 | -4072 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 332 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 1930 | 5676 |  |  | 5676 |  |  | -4072 | -4072 | -4072 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 332 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 2030 | 5441 |  |  | 5441 |  |  | -3906 | -3906 | -3906 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 97 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 2130 | 6244 |  |  | 6243 |  |  | -1054 | -1054 | -1052 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 140 | None | None | 368 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 2230 | 6244 |  |  | 6243 |  |  | -1054 | -1054 | -1052 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 140 | None | None | 368 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-07 | August | 2330 | 5684 |  |  | 5684 |  |  | -495 | -495 | -493 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 159 | None | None | 355 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-08 | August | 1230 | 6139 |  |  | 6139 |  |  | -4796 | -4796 | -4796 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 1330 | 6179 |  |  | 6179 |  |  | -4834 | -4834 | -4834 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 1430 | 6213 |  |  | 6213 |  |  | -4866 | -4866 | -4866 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 1530 | 6269 |  |  | 6269 |  |  | -829 | -829 | -829 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 1630 | 6269 |  |  | 6269 |  |  | -829 | -829 | -829 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-08 | August | 1730 | 6269 |  |  | 6269 |  |  | -829 | -829 | -829 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-08 | August | 1830 | 6104 |  |  | 6104 |  |  | -478 | -478 | -478 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 1930 | 6104 |  |  | 6104 |  |  | -478 | -478 | -478 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 2030 | 5771 |  |  | 5771 |  |  | -52 | -52 | -52 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 2130 | 5911 |  |  | 5439 |  |  | -776 | -776 | -203 | Critical Branch | ID schedules | 0 | 472 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 2230 | 5911 |  |  | 5733 |  |  | -776 | -776 | -560 | Critical Branch | ID schedules | 0 | 178 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-08 | August | 2330 | 5367 |  |  | 5367 |  |  | -240 | -240 | -240 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1230 | 5123 |  |  | 5123 |  |  | -4816 | -4816 | -4816 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 297 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1330 | 5123 |  |  | 5123 |  |  | -4816 | -4816 | -4816 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 297 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1430 | 5123 |  |  | 5123 |  |  | -4816 | -4816 | -4816 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 297 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1530 | 5700 |  |  | 5700 |  |  | -809 | -809 | -809 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 158 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1630 | 5461 |  |  | 5275 |  |  | -536 | -536 | -345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 186 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 172 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1730 | 5461 |  |  | 5119 |  |  | -530 | -530 | -174 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 342 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 158 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1830 | 5417 |  |  | 5100 |  |  | -2804 | -2804 | -2515 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 317 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 135 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 1930 | 5417 |  |  | 5068 |  |  | -2809 | -2809 | -2496 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 349 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 92 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 2030 | 5417 |  |  | 4977 |  |  | -2810 | -2810 | -2419 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 440 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 49 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-09 | August | 2130 |  | 5919 | 172 |  | 4807 | 172 | -135 | -135 | -135 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1112 | 0 | 1112 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -33 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-09 | August | 2230 |  | 5919 | 172 |  | 4868 | 172 | -135 | -135 | -135 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1051 | 0 | 1051 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -33 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-09 | August | 2330 |  | 5300 | 181 |  | 4733 | 180 | 443 | 4 | 443 | Minimum Margin | ID schedules | 439 | NA | 567 | 1 | 568 | 4 | 1 | 146 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 241 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 1230 | 3938 |  |  | 3500 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 438 | NA | NA | NA | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 311 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-10 | August | 1330 | 3938 |  |  | 3500 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 438 | NA | NA | NA | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 311 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-10 | August | 1430 | 3938 |  |  | 3500 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 438 | NA | NA | NA | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 311 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-10 | August | 1530 |  | 4593 | 194 |  | 3626 | 194 | -987 | -987 | -987 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 967 | 0 | 967 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 1630 |  | 4593 | 194 |  | 3626 | 194 | -987 | -987 | -987 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 967 | 0 | 967 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 1730 |  | 4402 | 169 |  | 4098 | 168 | -970 | -970 | -970 | Critical Branch | ID schedules | 0 | NA | 304 | 1 | 305 | 0 | 1 | 134 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 1830 |  | 5336 | 194 |  | 4314 | 194 | -537 | -537 | -537 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1022 | 0 | 1022 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 1930 |  | 5336 | 194 |  | 4286 | 194 | -537 | -537 | -537 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1050 | 0 | 1050 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 2030 |  | 5325 | 194 |  | 4141 | 194 | -542 | -542 | -542 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1184 | 0 | 1184 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 2130 |  | 5531 | 194 |  | 4241 | 194 | -615 | -615 | -615 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1290 | 0 | 1290 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 2230 |  | 5540 | 194 |  | 4376 | 194 | -613 | -613 | -613 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1164 | 0 | 1164 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-10 | August | 2330 |  | 5540 | 194 |  | 4386 | 194 | -613 | -613 | -613 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1154 | 0 | 1154 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-11 | August | 1230 | 4500 |  |  | 4500 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -254 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 254 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 1330 | 4500 |  |  | 4500 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 62 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -62 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 1430 | 4400 |  |  | 4400 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 1530 | 5628 |  |  | 3750 |  |  | -2593 | -2593 | -752 | Critical Branch | ID schedules | 0 | 1878 | NA | NA | NA | 0 | 1 | -285 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 285 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 1630 | 5628 |  |  | 3660 |  |  | -2593 | -2593 | -616 | Critical Branch | ID schedules | 0 | 1968 | NA | NA | NA | 0 | 1 | -93 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 93 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 1730 | 5628 |  |  | 3840 |  |  | -2593 | -2593 | -775 | Critical Branch | ID schedules | 0 | 1788 | NA | NA | NA | 0 | 1 | -50 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 50 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 1830 |  | 4774 | 172 |  | 4774 | 172 | -3259 | -3259 | -3259 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-11 | August | 1930 |  | 4755 | 172 |  | 4308 | 172 | -3252 | -3252 | -3252 | ID schedules | ID schedules | 0 | NA | 447 | 0 | 447 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 3481 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-11 | August | 2030 |  | 4732 | 172 |  | 4732 | 172 | -3243 | -3243 | -3243 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-11 | August | 2130 | 5602 |  |  | 5134 |  |  | -2828 | -2828 | -2499 | Critical Branch | ID schedules | 0 | 468 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 2230 | 5602 |  |  | 5322 |  |  | -2828 | -2828 | -2631 | Critical Branch | ID schedules | 0 | 280 | NA | NA | NA | 0 | 1 | -48 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 48 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-11 | August | 2330 | 5042 |  |  | 4731 |  |  | -2265 | -2265 | -2046 | Critical Branch | ID schedules | 0 | 311 | NA | NA | NA | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 1230 | 4110 |  |  | 4110 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 365 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 1330 | 4110 |  |  | 4110 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 365 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 1430 | 4010 |  |  | 4010 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 365 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 1530 | 4200 |  |  | 4200 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 82 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 1630 | 4100 |  |  | 4100 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 1730 | 4400 |  |  | 4400 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | -140 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-12 | August | 1830 | 4300 |  |  | 4300 |  |  | -3407 | -3407 | -3407 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | -81 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-12 | August | 1930 | 4182 |  |  | 4182 |  |  | -3184 | -3184 | -3183 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 222 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-12 | August | 2030 | 4182 |  |  | 4094 |  |  | -3180 | -3180 | -3120 | Critical Branch | ID schedules | 0 | 88 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 76 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 2130 | 5902 |  |  | 5598 |  |  | -1631 | -1631 | -1338 | Critical Branch | ID schedules | 0 | 304 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -37 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-12 | August | 2230 | 5902 |  |  | 5902 |  |  | -1631 | -1631 | -1630 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 347 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-12 | August | 2330 | 5342 |  |  | 5341 |  |  | -1071 | -1071 | -1069 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 159 | None | None | 331 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-13 | August | 1230 | 3640 |  |  | 3640 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-13 | August | 1330 | 3650 |  |  | 3650 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 2931 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 PRADELLA-NAUDERS 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-13 | August | 1430 | 3624 |  |  | 3624 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-13 | August | 1530 |  | 5801 | 0 |  | 3864 | 0 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1937 | 0 | 1937 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-13 | August | 1630 |  | 5566 | 160 |  | 5174 | 196 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 392 | -36 | 356 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-13 | August | 1730 |  | 5581 | 657 |  | 5581 | 657 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-13 | August | 1830 |  | 4464 | 576 |  | 4258 | 456 | -626 | -626 | -626 | Critical Branch | ID schedules | 0 | NA | 206 | 120 | 326 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-13 | August | 1930 |  | 4520 | 576 |  | 2822 | 574 | -680 | -680 | -680 | Critical Branch | ID schedules | 0 | NA | 1698 | 2 | 1700 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 2484 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-13 | August | 2030 |  | 4520 | 576 |  | 2543 | 574 | -680 | -680 | -680 | Critical Branch | ID schedules | 0 | NA | 1977 | 2 | 1979 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 1613 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-13 | August | 2130 | 6593 |  |  | 3664 |  |  | -1363 | -1363 | 1567 | Critical Branch | ID schedules | 0 | 2929 | NA | NA | NA | 1567 | 1 | None | None | None | None | None | None | None | 5959 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-13 | August | 2230 | 6593 |  |  | 5215 |  |  | -1363 | -1363 | 38 | Critical Branch | ID schedules | 0 | 1378 | NA | NA | NA | 38 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-13 | August | 2330 | 5993 |  |  | 5993 |  |  | -754 | -754 | -753 | Critical Branch | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-14 | August | 1230 |  | 2717 | 160 |  | 2717 | 160 | -6045 | -6045 | -6045 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-14 | August | 1330 |  | 3219 | 170 |  | 3136 | 170 | -5772 | -5772 | -5772 | ID schedules | ID schedules | 0 | NA | 83 | 0 | 83 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-14 | August | 1430 |  | 2817 | 160 |  | 2817 | 160 | -6158 | -6158 | -6158 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-14 | August | 1530 |  | 3453 | 48 |  | 3382 | 48 | -1654 | -1654 | -1654 | Critical Branch | ID schedules | 0 | NA | 71 | 0 | 71 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-14 | August | 1630 |  | 4435 | 609 |  | 4435 | 609 | -2625 | -2625 | -2625 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1200 | None | Tripping HVDC PISA 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-14 | August | 1730 |  | 4456 | 657 |  | 4456 | 657 | -2408 | -2408 | -2408 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | 3653 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | 1200 | None | Tripping HVDC PISA 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-14 | August | 1830 |  | 3955 | 634 |  | 3955 | 590 | -3343 | -3343 | -3343 | ID schedules | ID schedules | 0 | NA | 0 | 44 | 44 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | 3382 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-14 | August | 1930 |  | 3902 | 705 |  | 3902 | 677 | -3112 | -3112 | -3112 | ID schedules | ID schedules | 0 | NA | 0 | 28 | 28 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-14 | August | 2030 |  | 2981 | 705 |  | 2981 | 677 | -2573 | -2573 | -2573 | ID schedules | ID schedules | 0 | NA | 0 | 28 | 28 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-14 | August | 2130 |  | 3020 | 667 |  | 3023 | 657 | 105 | 105 | 105 | Adjustment reached | ID schedules | 0 | NA | -3 | 10 | 7 | 105 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 2708 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-14 | August | 2230 |  | 4073 | 657 |  | 4223 | 657 | -1385 | -1385 | -1385 | ID schedules | ID schedules | 0 | NA | -150 | 0 | -150 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1200 | None | Tripping HVDC PISA 1 and 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-14 | August | 2330 |  | 3706 | 645 |  | 3682 | 374 | -283 | -283 | -283 | ID schedules | ID schedules | 0 | NA | 24 | 271 | 295 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-15 | August | 1230 | 2312 |  |  | 508 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 1804 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-15 | August | 1330 | 2312 |  |  | 506 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 1806 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-15 | August | 1430 | 2312 |  |  | 1602 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 710 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-15 | August | 1530 |  | 4571 | 623 |  | 3059 | 623 | -1480 | -1480 | -1480 | Critical Branch | ID schedules | 0 | NA | 1512 | 0 | 1512 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 1630 |  | 4556 | 623 |  | 2991 | 623 | -1388 | -1388 | -1388 | Critical Branch | ID schedules | 0 | NA | 1565 | 0 | 1565 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 1730 |  | 4569 | 623 |  | 3158 | 623 | -1481 | -1481 | -1481 | Critical Branch | ID schedules | 0 | NA | 1411 | 0 | 1411 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 1830 |  | 5286 | 676 |  | 3610 | 676 | -1090 | -1090 | -1090 | Critical Branch | ID schedules | 0 | NA | 1676 | 0 | 1676 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 1930 |  | 5287 | 676 |  | 3460 | 676 | -1089 | -1089 | -1089 | Critical Branch | ID schedules | 0 | NA | 1827 | 0 | 1827 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 2030 |  | 5286 | 676 |  | 3418 | 676 | -1090 | -1090 | -1090 | Critical Branch | ID schedules | 0 | NA | 1868 | 0 | 1868 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 2130 |  | 5497 | 179 |  | 2870 | 179 | 998 | 347 | 998 | Minimum Margin | ID schedules | 651 | NA | 2627 | 0 | 2627 | 347 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 2230 |  | 5544 | 195 |  | 3422 | 195 | 1000 | 347 | 1000 | Minimum Margin | ID schedules | 653 | NA | 2122 | 0 | 2122 | 347 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-15 | August | 2330 |  | 5544 | 195 |  | 3427 | 195 | 995 | 347 | 995 | Minimum Margin | ID schedules | 648 | NA | 2117 | 0 | 2117 | 347 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-16 | August | 1230 |  | 3292 | 979 |  | 1922 | 979 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1370 | 0 | 1370 | 0 | 1 | 140 | None | None | 396 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1330 |  | 3292 | 979 |  | 2093 | 979 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1199 | 0 | 1199 | 0 | 1 | 140 | None | None | 396 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1430 |  | 3292 | 979 |  | 2646 | 979 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 646 | 0 | 646 | 0 | 1 | 140 | None | None | 395 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1530 |  | 6200 | 964 |  | 5201 | 940 | 741 | 366 | 741 | Minimum Margin | ID schedules | 375 | NA | 999 | 24 | 1023 | 366 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 140 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 1778 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1630 |  | 6209 | 964 |  | 6123 | 940 | 738 | 366 | 738 | Minimum Margin | ID schedules | 372 | NA | 86 | 24 | 110 | 366 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 186 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 1778 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1730 |  | 6209 | 964 |  | 6130 | 940 | 737 | 366 | 737 | Minimum Margin | TTC Validation phase - bilateral reduction | 371 | NA | 79 | 24 | 103 | 366 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 188 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 1778 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1830 |  | 5593 | 704 |  | 5566 | 698 | 169 | 169 | 169 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 27 | 6 | 33 | 169 | 1 | 138 | None | None | 314 | None | None | None | None | Reduction due to missing redispatch potential | None | 5285 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 1930 |  | 5593 | 704 |  | 5566 | 698 | 169 | 169 | 169 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 27 | 6 | 33 | 169 | 1 | 138 | None | None | 314 | None | None | None | None | Reduction due to missing redispatch potential | None | 5285 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 2030 |  | 5593 | 704 |  | 5566 | 698 | 169 | 169 | 169 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 27 | 6 | 33 | 169 | 1 | 138 | None | None | 314 | None | None | None | None | Reduction due to missing redispatch potential | None | 5285 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 2130 |  | 6296 | 696 |  | 6283 | 696 | 371 | 345 | 371 | Minimum Margin | Min import NTC Threshold | 26 | NA | 13 | 0 | 13 | 345 | 1 | 139 | None | None | 411 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 2230 |  | 6300 | 696 |  | 6283 | 696 | 371 | 345 | 371 | Minimum Margin | Min import NTC Threshold | 26 | NA | 17 | 0 | 17 | 345 | 1 | 139 | None | None | 411 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-16 | August | 2330 |  | 5745 | 720 |  | 5703 | 720 | 965 | 345 | 965 | Minimum Margin | TTC Validation phase - bilateral reduction | 620 | NA | 42 | 0 | 42 | 345 | 1 | 160 | None | None | 400 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 1230 |  | 5980 | 2984 |  | 1519 | 2984 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 4461 | 0 | 4461 | 0 | 1 | 110 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 404 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-17 | August | 1330 |  | 5980 | 2984 |  | 1519 | 2984 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 4461 | 0 | 4461 | 0 | 1 | 110 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 404 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-17 | August | 1430 |  | 5980 | 2984 |  | 1783 | 2984 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 4197 | 0 | 4197 | 0 | 1 | 110 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 404 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-17 | August | 1530 |  | 4827 | 880 |  | 3540 | 879 | -1915 | -1915 | -1915 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1287 | 1 | 1288 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 135 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-17 | August | 1630 |  | 5117 | 1031 |  | 4992 | 1012 | -1651 | -1651 | -1651 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 125 | 19 | 144 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 95 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 1730 |  | 5117 | 998 |  | 5117 | 978 | -1639 | -1639 | -1639 | ID schedules | ID schedules | 0 | NA | 0 | 20 | 20 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 88 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 1830 |  | 5613 | 1036 |  | 5557 | 1004 | 1363 | 247 | 1363 | Minimum Margin | TTC Validation phase - bilateral reduction | 1116 | NA | 56 | 32 | 88 | 247 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 135 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 1930 |  | 5613 | 1038 |  | 5557 | 1005 | 1363 | 247 | 1363 | Minimum Margin | TTC Validation phase - bilateral reduction | 1116 | NA | 56 | 33 | 89 | 247 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 135 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 2030 |  | 5613 | 1036 |  | 5557 | 1004 | 1363 | 247 | 1363 | Minimum Margin | TTC Validation phase - bilateral reduction | 1116 | NA | 56 | 32 | 88 | 247 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 135 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 2130 |  | 6004 | 1051 |  | 5930 | 1016 | 394 | 394 | 394 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 74 | 35 | 109 | 394 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 168 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 2230 |  | 6004 | 1013 |  | 5930 | 985 | 394 | 394 | 394 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 74 | 28 | 102 | 394 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 167 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-17 | August | 2330 |  | 6004 | 1013 |  | 5930 | 985 | 394 | 394 | 394 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 74 | 28 | 102 | 394 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 167 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-18 | August | 1230 | 3501 |  |  | 2986 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 515 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-18 | August | 1330 | 3501 |  |  | 3035 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 466 | NA | NA | NA | 0 | 1 | -335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-18 | August | 1430 | 3501 |  |  | 3168 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 333 | NA | NA | NA | 0 | 1 | -182 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 182 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-18 | August | 1530 |  | 5442 | 133 |  | 5168 | 30 | 739 | 154 | 739 | Minimum Margin | ID schedules | 585 | NA | 274 | 103 | 377 | 154 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-18 | August | 1630 |  | 5487 | 171 |  | 5589 | 168 | 818 | 154 | 818 | Minimum Margin | ID schedules | 664 | NA | -102 | 3 | -99 | 154 | 1 | 138 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 235 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-18 | August | 1730 |  | 5413 | 133 |  | 5481 | -53 | 708 | 154 | 708 | Minimum Margin | TTC Validation phase - bilateral reduction | 554 | NA | -68 | 186 | 118 | 154 | 1 | -83 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 268 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-18 | August | 1830 |  | 5323 | 737 |  | 5317 | 743 | -621 | -621 | -621 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 6 | -6 | 0 | 0 | 1 | 123 | None | None | 167 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-18 | August | 1930 |  | 5307 | 745 |  | 5309 | 745 | -595 | -595 | -595 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -2 | 0 | -2 | 0 | 1 | 125 | None | None | 36 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-18 | August | 2030 |  | 5360 | 745 |  | 5360 | 745 | -653 | -653 | -653 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 125 | None | None | 63 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-18 | August | 2130 |  | 5986 | 802 |  | 5986 | 802 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 135 | None | None | 174 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-18 | August | 2230 |  | 6114 | 796 |  | 5986 | 796 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 128 | 0 | 128 | 0 | 1 | 135 | None | None | 174 | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | Bilateral - Planned outage of Albertville-Rondissone 1&2 and limitation on PISA 1 | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-18 | August | 2330 |  | 5564 | 841 |  | 5542 | 847 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 22 | -6 | 16 | 0 | 1 | 160 | None | None | 104 | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | Bilateral - Planned outage of Albertville-Rondissone 1&2 and limitation on PISA 1 | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 1230 | 6013 |  |  | 6013 |  |  | -1942 | -1942 | -1936 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-19 | August | 1330 | 5945 |  |  | 5988 |  |  | -1830 | -1830 | -1912 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -43 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-19 | August | 1430 | 5972 |  |  | 5977 |  |  | -1874 | -1874 | -1883 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -5 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-19 | August | 1530 |  | 5849 | 26 |  | 5849 | 26 | -3561 | -3561 | -3561 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 1630 |  | 5795 | 273 |  | 5795 | 273 | -3376 | -3376 | -3376 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 1730 |  | 5849 | 619 |  | 5849 | 619 | -3458 | -3458 | -3458 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 139 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 1830 |  | 5298 | 631 |  | 5298 | 629 | 3506 | -52 | 3506 | ID schedules | TTC Validation phase - bilateral reduction | 3558 | NA | 0 | 2 | 2 | -52 | 1 | 102 | None | None | 338 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 1930 |  | 5321 | 666 |  | 5321 | 666 | 6219 | -52 | 6219 | ID schedules | TTC Validation phase - bilateral reduction | 6271 | NA | 0 | 0 | 0 | -52 | 1 | 110 | None | None | -110 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 2030 |  | 5051 | 666 |  | 5051 | 666 | 5833 | -52 | 5833 | ID schedules | TTC Validation phase - bilateral reduction | 5885 | NA | 0 | 0 | 0 | -52 | 1 | 110 | None | None | -65 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 2130 | 6087 |  |  | 6087 |  |  | -4023 | -4023 | -4023 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 243 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 2230 | 6085 |  |  | 6085 |  |  | -4000 | -4000 | -4000 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 243 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-19 | August | 2330 | 6081 |  |  | 6081 |  |  | -3910 | -3910 | -3910 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 227 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-20 | August | 1230 | 6514 |  |  | 6006 |  |  | 106 | 106 | 451 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 508 | NA | NA | NA | 451 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 282 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 1330 | 6514 |  |  | 6006 |  |  | 106 | 106 | 451 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 508 | NA | NA | NA | 451 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 282 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 1430 | 6514 |  |  | 6006 |  |  | 106 | 106 | 451 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 508 | NA | NA | NA | 451 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 282 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 1530 | 6450 |  |  | 6450 |  |  | -2780 | -2780 | -2780 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 254 | None | None | None | 6162 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 1630 | 6350 |  |  | 6350 |  |  | -2697 | -2697 | -2697 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 191 | None | None | None | 5838 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 1730 | 6528 |  |  | 6500 |  |  | -2860 | -2860 | -2846 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 28 | NA | NA | NA | 0 | 1 | 140 | None | None | 266 | None | None | None | 5241 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 1830 |  | 6377 | 522 |  | 6377 | 464 | -5097 | -5097 | -5097 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 58 | 58 | 0 | 1 | 140 | None | None | 299 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | 5512 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-20 | August | 1930 |  | 5919 | 627 |  | 5919 | 627 | -4430 | -4430 | -4430 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 41 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | 5305 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-20 | August | 2030 |  | 6222 | 627 |  | 6222 | 627 | -4508 | -4508 | -4508 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | None | 285 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | 5505 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-20 | August | 2130 | 6734 |  |  | 6734 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 380 | None | None | None | 4952 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 2230 | 6734 |  |  | 6734 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | None | 380 | None | None | None | 4659 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-20 | August | 2330 | 6132 |  |  | 6132 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | None | 367 | None | None | None | 5351 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-21 | August | 1230 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1330 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1430 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1530 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1630 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1730 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1830 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 1930 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 2030 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 2130 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 2230 | 6781 |  |  | 6781 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-21 | August | 2330 | 6181 |  |  | 6181 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-22 | August | 1230 | 5643 |  |  | 3936 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1707 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 252 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1330 | 5643 |  |  | 4305 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1338 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 252 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1430 | 5643 |  |  | 4303 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1340 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 252 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1530 | 7766 |  |  | 5076 |  |  | -3614 | -3614 | -962 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2690 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 355 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7336 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1630 | 7766 |  |  | 5828 |  |  | -3614 | -3614 | -1710 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1938 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1730 | 7766 |  |  | 5962 |  |  | -3614 | -3614 | -1843 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1804 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1830 | 8824 |  |  | 7520 |  |  | -2088 | -2088 | -792 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1304 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 383 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-22 | August | 1930 | 8824 |  |  | 8754 |  |  | -2088 | -2088 | -2032 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 70 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-22 | August | 2030 | 8824 |  |  | 8754 |  |  | -2088 | -2088 | -2032 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 70 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-22 | August | 2130 | 8822 |  |  | 8752 |  |  | -4856 | -4856 | -4776 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 70 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-22 | August | 2230 | 8822 |  |  | 8752 |  |  | -4856 | -4856 | -4776 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 70 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-22 | August | 2330 | 8222 |  |  | 8148 |  |  | -4258 | -4258 | -4172 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 74 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-23 | August | 1230 | 3552 |  |  | 2675 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 877 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 309 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 1330 | 3552 |  |  | 2675 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 877 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 309 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 1430 | 3552 |  |  | 2716 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 836 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 309 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 1530 | 5817 |  |  | 4642 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1175 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 101 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 1630 | 5817 |  |  | 5495 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 322 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 1730 | 6751 |  |  | 6751 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 1830 |  | 7023 | 651 |  | 7023 | 651 | -4300 | -4300 | -4300 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 400 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-23 | August | 1930 |  | 7063 | 559 |  | 7063 | 559 | -4319 | -4319 | -4319 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 141 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-23 | August | 2030 |  | 7050 | 651 |  | 6491 | 651 | -4409 | -4409 | -4409 | ID schedules | ID schedules | 0 | NA | 559 | 0 | 559 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -34 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-23 | August | 2130 | 7626 |  |  | 5868 |  |  | -4824 | -4824 | -3495 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1758 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 2230 | 7626 |  |  | 7341 |  |  | -4716 | -4716 | -4419 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 285 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 368 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-23 | August | 2330 | 7026 |  |  | 7008 |  |  | -4227 | -4227 | -4212 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 18 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 349 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1230 | 4001 |  |  | 4001 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 323 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1330 | 4000 |  |  | 4000 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 323 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1430 | 4000 |  |  | 4000 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 323 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1530 | 6502 |  |  | 5000 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1502 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1630 | 6732 |  |  | 6732 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1730 | 6749 |  |  | 6749 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 376 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1830 | 7080 |  |  | 7017 |  |  | -4192 | -4192 | -4118 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 63 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 1930 | 7082 |  |  | 7082 |  |  | -4194 | -4194 | -4194 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 366 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 2030 | 7080 |  |  | 6415 |  |  | -4314 | -4314 | -3794 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 665 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 129 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 2130 | 7500 |  |  | 7242 |  |  | -3672 | -3672 | -3358 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 258 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 354 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 2230 | 7500 |  |  | 7239 |  |  | -3667 | -3667 | -3350 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 261 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-24 | August | 2330 | 7500 |  |  | 7085 |  |  | -3722 | -3722 | -3216 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 415 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-25 | August | 1230 | 6216 |  |  | 6216 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 155 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-25 | August | 1330 | 6216 |  |  | 6216 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-25 | August | 1430 | 6216 |  |  | 6216 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-25 | August | 1530 | 8195 |  |  | 7716 |  |  | -3109 | -3109 | -2633 | Critical Branch | ID schedules | 0 | 479 | NA | NA | NA | 0 | 1 | -156 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 195 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-25 | August | 1630 | 8195 |  |  | 8194 |  |  | -3109 | -3109 | -3107 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | -196 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 208 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-25 | August | 1730 | 8345 |  |  | 7711 |  |  | -3269 | -3269 | -2637 | Critical Branch | ID schedules | 0 | 634 | NA | NA | NA | 0 | 1 | -186 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 202 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-25 | August | 1830 |  | 6089 | 722 |  | 5417 | 722 | -3858 | -3858 | -3858 | Critical Branch | ID schedules | 0 | NA | 672 | 0 | 672 | 0 | 1 | 68 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 153 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-25 | August | 1930 |  | 6283 | 724 |  | 5389 | 725 | -3950 | -3950 | -3950 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 894 | -1 | 893 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-25 | August | 2030 |  | 6283 | 724 |  | 5092 | 725 | -3950 | -3950 | -3950 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1191 | -1 | 1190 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-25 | August | 2130 |  | 6606 | 847 |  | 5125 | 836 | -5274 | -5274 | -5274 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1481 | 11 | 1492 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-25 | August | 2230 |  | 6606 | 847 |  | 5634 | 836 | -5274 | -5274 | -5274 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 972 | 11 | 983 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-25 | August | 2330 |  | 5822 | 872 |  | 5185 | 861 | -4564 | -4564 | -4564 | Critical Branch | ID schedules | 0 | NA | 637 | 11 | 648 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-26 | August | 1230 | 4749 |  |  | 4749 |  |  | -5769 | -5769 | -5769 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-26 | August | 1330 | 4749 |  |  | 4749 |  |  | -5769 | -5769 | -5769 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-26 | August | 1430 | 4749 |  |  | 4749 |  |  | -5769 | -5769 | -5769 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 115 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-26 | August | 1530 | 8208 |  |  | 6288 |  |  | -3439 | -3439 | -1518 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1920 | NA | NA | NA | 0 | 1 | 70 | None | None | 156 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-26 | August | 1630 | 8208 |  |  | 7510 |  |  | -3439 | -3439 | -2741 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 698 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 190 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7886 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-26 | August | 1730 | 8358 |  |  | 7659 |  |  | -3598 | -3598 | -2900 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 699 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 190 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7074 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-26 | August | 1830 |  | 5743 | 666 |  | 5743 | 665 | -3807 | -3807 | -3807 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 0 | 1 | 62 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-26 | August | 1930 |  | 5911 | 673 |  | 5911 | 679 | -3837 | -3837 | -3837 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -6 | -6 | 0 | 1 | 70 | None | None | 76 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-26 | August | 2030 |  | 5911 | 673 |  | 5911 | 679 | -3837 | -3837 | -3837 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -6 | -6 | 0 | 1 | 70 | None | None | 76 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-26 | August | 2130 | 8008 |  |  | 7656 |  |  | -4682 | -4682 | -4329 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 352 | NA | NA | NA | 0 | 1 | 70 | None | None | 192 | None | None | None | 7406 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-26 | August | 2230 | 8008 |  |  | 8007 |  |  | -4682 | -4682 | -4681 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 70 | None | None | 199 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-26 | August | 2330 | 7418 |  |  | 7418 |  |  | -4086 | -4086 | -4085 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | 69 | None | None | 199 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-27 | August | 1230 | 4334 |  |  | 4333 |  |  | 4307 | -118 | 4310 | Critical Branch | Validation phase | 4425 | 1 | NA | NA | NA | -115 | 1 | 70 | None | None | 104 | None | None | None | 4083 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-27 | August | 1330 | 4334 |  |  | 4333 |  |  | 4307 | -118 | 4310 | Critical Branch | Validation phase | 4425 | 1 | NA | NA | NA | -115 | 1 | 70 | None | None | 104 | None | None | None | 4083 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-27 | August | 1430 | 4334 |  |  | 4333 |  |  | 4307 | -118 | 4310 | Critical Branch | Validation phase | 4425 | 1 | NA | NA | NA | -115 | 1 | 70 | None | None | 104 | None | None | None | 4083 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-27 | August | 1530 | 7864 |  |  | 5866 |  |  | -3308 | -3308 | -1312 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1998 | NA | NA | NA | 0 | 1 | 70 | None | None | 144 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-27 | August | 1630 | 7864 |  |  | 7338 |  |  | -3308 | -3308 | -2785 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 526 | NA | NA | NA | 0 | 1 | 70 | None | None | 185 | None | None | None | 7581 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-08-27 | August | 1730 | 8014 |  |  | 7913 |  |  | -3474 | -3474 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 101 | NA | NA | NA | 0 | 1 | -128 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 197 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6579 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-27 | August | 1830 |  | 5760 | 558 |  | 5760 | 572 | -4037 | -4037 | -4037 | Critical Branch | ID schedules | 0 | NA | 0 | -14 | -14 | 0 | 1 | 51 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 80 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5394 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-27 | August | 1930 |  | 5927 | 576 |  | 5927 | 575 | -3789 | -3789 | -3789 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 0 | 1 | 53 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -53 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5407 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-27 | August | 2030 |  | 5943 | 576 |  | 5943 | 575 | -3808 | -3808 | -3808 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 0 | 1 | 53 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -53 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-27 | August | 2130 | 7015 |  |  | 7015 |  |  | -4117 | -4117 | -4117 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 19 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-27 | August | 2230 | 7189 |  |  | 7188 |  |  | -4235 | -4235 | -4234 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 177 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-27 | August | 2330 | 6602 |  |  | 6602 |  |  | -3640 | -3640 | -3640 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 69 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 175 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1230 | 4627 |  |  | 4610 |  |  | 3449 | -68 | 3455 | Critical Branch | TTC Validation phase - bilateral reduction | 3517 | 17 | NA | NA | NA | -62 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 96 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 4376 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1330 | 4627 |  |  | 4610 |  |  | 3449 | -68 | 3455 | Critical Branch | TTC Validation phase - bilateral reduction | 3517 | 17 | NA | NA | NA | -62 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 96 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 4376 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1430 | 4627 |  |  | 4610 |  |  | 3449 | -68 | 3455 | Critical Branch | TTC Validation phase - bilateral reduction | 3517 | 17 | NA | NA | NA | -62 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 96 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 4376 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1530 | 6738 |  |  | 5550 |  |  | -2919 | -2919 | -1731 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1188 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1630 | 6738 |  |  | 6602 |  |  | -2864 | -2864 | -2704 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 136 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 177 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1730 | 7103 |  |  | 6975 |  |  | -3200 | -3200 | -3053 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 128 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 275 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 1830 |  | 5761 | 724 |  | 5571 | 726 | -4702 | -4702 | -4702 | Critical Branch | ID schedules | 0 | NA | 190 | -2 | 188 | 0 | 1 | 122 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -17 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-28 | August | 1930 |  | 5779 | 727 |  | 5331 | 727 | -4713 | -4713 | -4713 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 448 | 0 | 448 | 0 | 1 | 123 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -123 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-28 | August | 2030 |  | 5760 | 727 |  | 5381 | 727 | -4700 | -4700 | -4700 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 379 | 0 | 379 | 0 | 1 | 123 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -123 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-28 | August | 2130 | 7453 |  |  | 6383 |  |  | -4178 | -4178 | -3034 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1070 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 342 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6615 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 2230 | 7453 |  |  | 6458 |  |  | -4178 | -4178 | -3106 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 995 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 340 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-28 | August | 2330 | 6853 |  |  | 5934 |  |  | -3570 | -3570 | -2576 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 919 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 328 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1230 | 6653 |  |  | 5802 |  |  | -2365 | -2365 | -1514 | Critical Branch | ID schedules | 0 | 851 | NA | NA | NA | 0 | 1 | -330 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 330 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1330 | 6653 |  |  | 5802 |  |  | -2365 | -2365 | -1514 | Critical Branch | ID schedules | 0 | 851 | NA | NA | NA | 0 | 1 | -330 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 330 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1430 | 6653 |  |  | 5802 |  |  | -2365 | -2365 | -1514 | Critical Branch | ID schedules | 0 | 851 | NA | NA | NA | 0 | 1 | -330 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 330 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1530 | 6663 |  |  | 6428 |  |  | -2951 | -2951 | -2710 | Critical Branch | ID schedules | 0 | 235 | NA | NA | NA | 0 | 1 | -392 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 392 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1630 | 6713 |  |  | 6479 |  |  | -3003 | -3003 | -2763 | Critical Branch | ID schedules | 0 | 234 | NA | NA | NA | 0 | 1 | -392 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 392 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1730 | 8513 |  |  | 6871 |  |  | -4851 | -4851 | -3393 | Critical Branch | ID schedules | 0 | 1642 | NA | NA | NA | 0 | 1 | -384 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 384 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 1830 |  | 6061 | 689 |  | 5328 | 255 | -5319 | -5319 | -5319 | Critical Branch | ID schedules | 0 | NA | 733 | 434 | 1167 | 0 | 1 | -318 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 318 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-29 | August | 1930 |  | 6141 | 713 |  | 5351 | 732 | -5360 | -5360 | -5360 | Critical Branch | ID schedules | 0 | NA | 790 | -19 | 771 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-29 | August | 2030 |  | 6095 | 689 |  | 5357 | 255 | -5339 | -5339 | -5339 | Critical Branch | ID schedules | 0 | NA | 738 | 434 | 1172 | 0 | 1 | -318 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 318 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-29 | August | 2130 | 8098 |  |  | 6548 |  |  | -2568 | -2568 | -942 | Critical Branch | ID schedules | 0 | 1550 | NA | NA | NA | 0 | 1 | -338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 2230 | 8098 |  |  | 6513 |  |  | -2568 | -2568 | -901 | Critical Branch | ID schedules | 0 | 1585 | NA | NA | NA | 0 | 1 | -338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-29 | August | 2330 | 7498 |  |  | 5952 |  |  | -1954 | -1954 | -331 | Critical Branch | ID schedules | 0 | 1546 | NA | NA | NA | 0 | 1 | -324 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 324 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-30 | August | 1230 |  | 5932 | 166 |  | 5866 | 166 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 66 | 0 | 66 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1330 |  | 5845 | 166 |  | 5578 | 166 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 267 | 0 | 267 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1430 |  | 5520 | 157 |  | 5009 | -245 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 511 | 402 | 913 | 0 | 1 | -271 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 271 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1530 |  | 6568 | 741 |  | 6391 | 512 | 1091 | 177 | 1091 | Minimum Margin | ID schedules | 914 | NA | 177 | 229 | 406 | 177 | 1 | -103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2973 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1630 |  | 5973 | 780 |  | 5796 | 787 | 1766 | 177 | 1766 | Minimum Margin | ID schedules | 1589 | NA | 177 | -7 | 170 | 177 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2346 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1730 |  | 6381 | 780 |  | 6204 | 787 | 1526 | 177 | 1526 | Minimum Margin | ID schedules | 1349 | NA | 177 | -7 | 170 | 177 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2552 | None | Bilateral - Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1830 |  | 6915 | 557 |  | 5644 | 553 | -5608 | -5608 | -5608 | Critical Branch | ID schedules | 0 | NA | 1271 | 4 | 1275 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 6618 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 1930 |  | 6915 | 557 |  | 5616 | 519 | -5608 | -5608 | -5608 | Critical Branch | ID schedules | 0 | NA | 1299 | 38 | 1337 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 6193 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 2030 |  | 6915 | 557 |  | 4871 | 557 | -5608 | -5608 | -5608 | Critical Branch | ID schedules | 0 | NA | 2044 | 0 | 2044 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-30 | August | 2130 | 7932 |  |  | 5383 |  |  | 1645 | 531 | 3801 | Minimum Margin | ID schedules | 1114 | 2549 | NA | NA | NA | 2687 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -100 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 7148 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-30 | August | 2230 | 7932 |  |  | 5830 |  |  | 1645 | 531 | 3539 | Minimum Margin | ID schedules | 1114 | 2102 | NA | NA | NA | 2425 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 303 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 7148 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-30 | August | 2330 | 7339 |  |  | 5289 |  |  | 2360 | 538 | 4206 | Minimum Margin | ID schedules | 1822 | 2050 | NA | NA | NA | 2384 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 286 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | 6549 | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-31 | August | 1230 |  | 5076 | 2993 |  | 1399 | 2993 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 3677 | 0 | 3677 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1330 |  | 5076 | 2993 |  | 1399 | 2993 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 3677 | 0 | 3677 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1430 |  | 5076 | 2993 |  | 1399 | 2993 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 3677 | 0 | 3677 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1530 |  | 4677 | 805 |  | 2359 | 817 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 2318 | -12 | 2306 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1630 |  | 4313 | 865 |  | 4245 | 865 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 68 | 0 | 68 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1730 |  | 5675 | 865 |  | 5675 | 865 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 5352 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1830 |  | 6205 | 811 |  | 5709 | 381 | -3973 | -3973 | -3973 | Critical Branch | ID schedules | 0 | NA | 496 | 430 | 926 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 1930 |  | 6252 | 822 |  | 5734 | 826 | -3990 | -3990 | -3990 | Critical Branch | ID schedules | 0 | NA | 518 | -4 | 514 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 6016 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 2030 |  | 6252 | 822 |  | 5457 | 809 | -3990 | -3990 | -3990 | Critical Branch | ID schedules | 0 | NA | 795 | 13 | 808 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5845 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-08-31 | August | 2130 | 6764 |  |  | 5419 |  |  | -3789 | -3789 | -2325 | Critical Branch | ID schedules | 0 | 1345 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6204 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-31 | August | 2230 | 6764 |  |  | 5438 |  |  | -3789 | -3789 | -2348 | Critical Branch | ID schedules | 0 | 1326 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-08-31 | August | 2330 | 6764 |  |  | 5469 |  |  | -3789 | -3789 | -2385 | Critical Branch | ID schedules | 0 | 1295 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None

## ID 70% reduction
ID 70% reduction results
|  |  | TTC Adjustment |  |  | ANTC |  | LimitedBy
BD | Month | TS | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | Adjustment | 70% reduction | % reduction | Category
2025-09-02 | September | 1230 | 6526 |  |  | 689 | 210 | Minimum Margin | 479 | 69.52% | [500-1000] MW
2025-09-02 | September | 1330 | 6496 |  |  | 710 | 210 | Minimum Margin | 500 | 70.42% | [500-1000] MW
2025-09-02 | September | 1430 | 6496 |  |  | 710 | 210 | Minimum Margin | 500 | 70.42% | [500-1000] MW
2025-09-04 | September | 1230 | 7349 |  |  | 933 | 208 | Minimum Margin | 725 | 77.71% | [500-1000] MW
2025-09-04 | September | 1330 | 7365 |  |  | 922 | 208 | Minimum Margin | 714 | 77.44% | [500-1000] MW
2025-09-04 | September | 1430 | 7564 |  |  | 784 | 208 | Minimum Margin | 576 | 73.47% | [500-1000] MW
2025-09-05 | September | 1530 | 7391 |  |  | 1484 | 203 | Minimum Margin | 1281 | 86.32% | above 1000 MW
2025-09-05 | September | 1630 | 7391 |  |  | 1484 | 203 | Minimum Margin | 1281 | 86.32% | above 1000 MW
2025-09-05 | September | 1730 | 7023 |  |  | 1687 | 203 | Minimum Margin | 1484 | 87.97% | above 1000 MW
2025-09-10 | September | 1230 | 7907 |  |  | 682 | 207 | Minimum Margin | 475 | 69.65% | [500-1000] MW
2025-09-10 | September | 1330 | 7907 |  |  | 682 | 207 | Minimum Margin | 475 | 69.65% | [500-1000] MW
2025-09-10 | September | 1430 | 7907 |  |  | 682 | 207 | Minimum Margin | 475 | 69.65% | [500-1000] MW
2025-09-11 | September | 1230 | 7434 |  |  | 252 | 248 | Minimum Margin | 4 | 1.587% | below 500 MW
2025-09-11 | September | 1330 | 7434 |  |  | 252 | 248 | Minimum Margin | 4 | 1.587% | below 500 MW
2025-09-20 | September | 1530 | 7687 |  |  | 1354 | 199 | Minimum Margin | 1155 | 85.3% | above 1000 MW
2025-09-20 | September | 1630 | 7687 |  |  | 1354 | 199 | Minimum Margin | 1155 | 85.3% | above 1000 MW
2025-09-20 | September | 1730 | 7990 |  |  | 1173 | 202 | Minimum Margin | 971 | 82.78% | above 1000 MW
2025-09-21 | September | 1530 | 7501 |  |  | 435 | 360 | Minimum Margin | 75 | 17.24% | below 500 MW
2025-09-21 | September | 1630 | 7501 |  |  | 435 | 360 | Minimum Margin | 75 | 17.24% | below 500 MW
2025-08-01 | August | 1530 | 7487 |  |  | 2219 | -88 | Critical Branch | 2307 | 104% | above 1000 MW
2025-08-01 | August | 1630 | 7487 |  |  | 2219 | -88 | Critical Branch | 2307 | 104% | above 1000 MW
2025-08-01 | August | 1730 | 7487 |  |  | 2219 | -88 | Critical Branch | 2307 | 104% | above 1000 MW
2025-08-01 | August | 1830 |  | 8292 | 665 | 818 | 247 | Minimum Margin | 571 | 69.8% | [500-1000] MW
2025-08-01 | August | 1930 |  | 8292 | 665 | 944 | 247 | Minimum Margin | 697 | 73.83% | [500-1000] MW
2025-08-01 | August | 2030 |  | 8287 | 686 | 943 | 247 | Minimum Margin | 696 | 73.81% | [500-1000] MW
2025-08-09 | August | 2330 |  | 5300 | 181 | 443 | 4 | Minimum Margin | 439 | 99.1% | below 500 MW
2025-08-15 | August | 2130 |  | 5497 | 179 | 998 | 347 | Minimum Margin | 651 | 65.23% | [500-1000] MW
2025-08-15 | August | 2230 |  | 5544 | 195 | 1000 | 347 | Minimum Margin | 653 | 65.3% | [500-1000] MW
2025-08-15 | August | 2330 |  | 5544 | 195 | 995 | 347 | Minimum Margin | 648 | 65.13% | [500-1000] MW
2025-08-16 | August | 1530 |  | 6200 | 964 | 741 | 366 | Minimum Margin | 375 | 50.61% | [500-1000] MW
2025-08-16 | August | 1630 |  | 6209 | 964 | 738 | 366 | Minimum Margin | 372 | 50.41% | [500-1000] MW
2025-08-16 | August | 1730 |  | 6209 | 964 | 737 | 366 | Minimum Margin | 371 | 50.34% | [500-1000] MW
2025-08-16 | August | 2130 |  | 6296 | 696 | 371 | 345 | Minimum Margin | 26 | 7.008% | below 500 MW
2025-08-16 | August | 2230 |  | 6300 | 696 | 371 | 345 | Minimum Margin | 26 | 7.008% | below 500 MW
2025-08-16 | August | 2330 |  | 5745 | 720 | 965 | 345 | Minimum Margin | 620 | 64.25% | [500-1000] MW
2025-08-17 | August | 1830 |  | 5613 | 1036 | 1363 | 247 | Minimum Margin | 1116 | 81.88% | above 1000 MW
2025-08-17 | August | 1930 |  | 5613 | 1038 | 1363 | 247 | Minimum Margin | 1116 | 81.88% | above 1000 MW
2025-08-17 | August | 2030 |  | 5613 | 1036 | 1363 | 247 | Minimum Margin | 1116 | 81.88% | above 1000 MW
2025-08-18 | August | 1530 |  | 5442 | 133 | 739 | 154 | Minimum Margin | 585 | 79.16% | [500-1000] MW
2025-08-18 | August | 1630 |  | 5487 | 171 | 818 | 154 | Minimum Margin | 664 | 81.17% | [500-1000] MW
2025-08-18 | August | 1730 |  | 5413 | 133 | 708 | 154 | Minimum Margin | 554 | 78.25% | [500-1000] MW
2025-08-27 | August | 1230 | 4334 |  |  | 4307 | -118 | Critical Branch | 4425 | 102.7% | above 1000 MW
2025-08-27 | August | 1330 | 4334 |  |  | 4307 | -118 | Critical Branch | 4425 | 102.7% | above 1000 MW
2025-08-27 | August | 1430 | 4334 |  |  | 4307 | -118 | Critical Branch | 4425 | 102.7% | above 1000 MW
2025-08-28 | August | 1230 | 4627 |  |  | 3449 | -68 | Critical Branch | 3517 | 102% | above 1000 MW
2025-08-28 | August | 1330 | 4627 |  |  | 3449 | -68 | Critical Branch | 3517 | 102% | above 1000 MW
2025-08-28 | August | 1430 | 4627 |  |  | 3449 | -68 | Critical Branch | 3517 | 102% | above 1000 MW
2025-08-30 | August | 1530 |  | 6568 | 741 | 1091 | 177 | Minimum Margin | 914 | 83.78% | above 1000 MW
2025-08-30 | August | 1630 |  | 5973 | 780 | 1766 | 177 | Minimum Margin | 1589 | 89.98% | above 1000 MW
2025-08-30 | August | 1730 |  | 6381 | 780 | 1526 | 177 | Minimum Margin | 1349 | 88.4% | above 1000 MW
2025-08-30 | August | 2130 | 7932 |  |  | 1645 | 531 | Minimum Margin | 1114 | 67.72% | above 1000 MW
2025-08-30 | August | 2230 | 7932 |  |  | 1645 | 531 | Minimum Margin | 1114 | 67.72% | above 1000 MW
2025-08-30 | August | 2330 | 7339 |  |  | 2360 | 538 | Minimum Margin | 1822 | 77.2% | above 1000 MW

## ID validation reduction
ID Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | NTC-Import | NTC-Export | ANTC |  |  | LimitedBy |  | TTC Validation Reduction |  |  | Reason for TTC Reduction |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | AT-IT FR-IT | IT-AT IT-FR | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | Smoothing | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason
2025-09-01 | September | 1230 | 6531 |  |  | 6524 |  |  |  |  | -1640 | -1640 | -1635 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-01 | September | 1330 | 6531 |  |  | 6524 |  |  |  |  | -1640 | -1640 | -1635 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-01 | September | 1430 | 6531 |  |  | 6530 |  |  |  |  | -1640 | -1640 | -1638 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-02 | September | 1230 | 6526 |  |  | 6316 |  |  |  |  | 689 | 210 | 689 | Minimum Margin | TTC Validation phase - bilateral reduction | 210 | NA | 210 | [8 empty] | FR | 6064 | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR]
2025-09-02 | September | 1330 | 6496 |  |  | 6286 |  |  |  |  | 710 | 210 | 710 | Minimum Margin | TTC Validation phase - bilateral reduction | 210 | NA | 210 | [8 empty] | FR | 6035 | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR]
2025-09-02 | September | 1430 | 6496 |  |  | 6286 |  |  |  |  | 710 | 210 | 710 | Minimum Margin | TTC Validation phase - bilateral reduction | 210 | NA | 210 | [8 empty] | FR | 6035 | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR]
2025-09-02 | September | 1530 | 6807 |  |  | 6308 |  |  |  |  | -2749 | -2749 | -2096 | Critical Branch | TTC Validation phase - bilateral reduction | 499 | NA | 0 | [8 empty] | FR | 1900 | Bilateral - Test GRANDE ILE PIOSSASCO 1
2025-09-02 | September | 1630 | 6807 |  |  | 6307 |  |  |  |  | -2749 | -2749 | -2096 | Critical Branch | TTC Validation phase - bilateral reduction | 500 | NA | 0 | [5 empty] | CH | 6507 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 1900 | Bilateral - Test GRANDE ILE PIOSSASCO 1
2025-09-02 | September | 1730 | 6807 |  |  | 5460 |  |  |  |  | -2750 | -2750 | -1920 | Critical Branch | TTC Validation phase - bilateral reduction | 1347 | NA | 0 | [5 empty] | CH | 5210 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 1900 | Bilateral - Test GRANDE ILE PIOSSASCO 1
2025-09-03 | September | 1230 | 7543 |  |  | 7537 |  |  |  |  | -3765 | -3765 | -3760 | Critical Branch | TTC Validation phase - bilateral reduction | 6 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-09-03 | September | 1330 | 7543 |  |  | 7450 |  |  |  |  | -3765 | -3765 | -3672 | Critical Branch | Validation phase | 93 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border | CH | 7200 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
2025-09-03 | September | 1430 | 7543 |  |  | 7537 |  |  |  |  | -3765 | -3765 | -3760 | Critical Branch | TTC Validation phase - bilateral reduction | 6 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-09-03 | September | 1730 | 7289 |  |  | 7003 |  |  |  |  | -4024 | -4024 | -3868 | Critical Branch | TTC Validation phase - bilateral reduction | 286 | NA | 0 | [5 empty] | CH | 6753 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
2025-09-03 | September | 2130 | 7680 |  |  | 6169 |  |  |  |  | -2348 | -2348 | -976 | Critical Branch | TTC Validation phase - bilateral reduction | 1511 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 |  |  |  | IT | -10000 | ATC blocked
2025-09-03 | September | 2230 | 7680 |  |  | 6630 |  |  |  |  | -2348 | -2348 | -1244 | Critical Branch | TTC Validation phase - bilateral reduction | 1050 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7412 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | FR | 2500 | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 |  |  |  | IT | -10000 | ATC blocked
2025-09-03 | September | 2330 | 7080 |  |  | 5935 |  |  |  |  | -1737 | -1737 | -621 | Critical Branch | TTC Validation phase - bilateral reduction | 1145 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-04 | September | 1230 | 7349 |  |  | 7141 |  |  |  |  | 933 | 208 | 933 | Minimum Margin | TTC Validation phase - bilateral reduction | 208 | NA | 208 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 6890 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-09-04 | September | 1330 | 7365 |  |  | 7157 |  |  |  |  | 922 | 208 | 922 | Minimum Margin | TTC Validation phase - bilateral reduction | 208 | NA | 208 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 6905 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-09-04 | September | 1430 | 7564 |  |  | 7356 |  |  |  |  | 784 | 208 | 784 | Minimum Margin | TTC Validation phase - bilateral reduction | 208 | NA | 208 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 7105 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-09-05 | September | 1530 | 7391 |  |  | 7188 |  |  |  |  | 1484 | 203 | 1484 | Minimum Margin | TTC Validation phase - bilateral reduction | 203 | NA | 203 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 6937 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-09-05 | September | 1630 | 7391 |  |  | 7188 |  |  |  |  | 1484 | 203 | 1484 | Minimum Margin | TTC Validation phase - bilateral reduction | 203 | NA | 203 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 6937 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-09-05 | September | 1730 | 7023 |  |  | 5768 |  |  |  |  | 1687 | 203 | 2263 | Minimum Margin | TTC Validation phase - bilateral reduction | 1255 | NA | 779 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5950 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | FR | 6569 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-09-06 | September | 2230 | 5842 |  |  | 5839 |  |  |  |  | -3872 | -3872 | -3871 | ID schedules | TTC Validation phase - bilateral reduction | 3 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-08 | September | 1230 | 7619 |  |  | 7502 |  |  |  |  | -988 | -988 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 117 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-08 | September | 1330 | 7619 |  |  | 7498 |  |  |  |  | -987 | -987 | -874 | Critical Branch | TTC Validation phase - bilateral reduction | 121 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-08 | September | 1430 | 7619 |  |  | 7501 |  |  |  |  | -988 | -988 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | 118 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7166 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-08 | September | 1530 | 8009 |  |  | 7711 |  |  |  |  | -3477 | -3477 | -3184 | Critical Branch | TTC Validation phase - bilateral reduction | 298 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2
2025-09-08 | September | 1630 | 8009 |  |  | 7711 |  |  |  |  | -3477 | -3477 | -3184 | Critical Branch | TTC Validation phase - bilateral reduction | 298 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2
2025-09-08 | September | 1730 | 8009 |  |  | 7496 |  |  |  |  | -3477 | -3477 | -2970 | Critical Branch | TTC Validation phase - bilateral reduction | 513 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border | CH | 7383 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2
2025-09-10 | September | 1230 | 7907 |  |  | 7628 |  |  |  |  | 682 | 207 | 894 | Minimum Margin | TTC Validation phase - bilateral reduction | 279 | NA | 419 |  |  | AT | 120 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - N-2 Albertville-Rondissone
2025-09-10 | September | 1330 | 7907 |  |  | 7628 |  |  |  |  | 682 | 207 | 894 | Minimum Margin | TTC Validation phase - bilateral reduction | 279 | NA | 419 |  |  | AT | 120 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - N-2 Albertville-Rondissone
2025-09-10 | September | 1430 | 7907 |  |  | 7628 |  |  |  |  | 682 | 207 | 894 | Minimum Margin | TTC Validation phase - bilateral reduction | 279 | NA | 419 |  |  | AT | 120 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - N-2 Albertville-Rondissone
2025-09-11 | September | 1230 | 7434 |  |  | 7419 |  |  |  |  | 252 | 248 | 61 | Minimum Margin | TTC Validation phase - bilateral reduction | 15 | NA | 57 | [8 empty] | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-11 | September | 1330 | 7434 |  |  | 7419 |  |  |  |  | 252 | 248 | 61 | Minimum Margin | TTC Validation phase - bilateral reduction | 15 | NA | 57 |  |  | AT | -355 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-11 | September | 1430 | 7469 |  |  | 7441 |  |  |  |  | 102 | 102 | 0 | Adjustment reached | ID schedules | 28 | NA | 0 |  |  | AT | -355 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-11 | September | 2130 | 8391 |  |  | 7907 |  |  |  |  | -1933 | -1933 | -1319 | Critical Branch | TTC Validation phase - bilateral reduction | 484 | NA | 0 |  |  | AT | 120 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-11 | September | 2230 | 8391 |  |  | 7907 |  |  |  |  | -1933 | -1933 | -1319 | Critical Branch | TTC Validation phase - bilateral reduction | 484 | NA | 0 |  |  | AT | 120 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-11 | September | 2330 | 7791 |  |  | 7532 |  |  |  |  | -1326 | -1326 | -1011 | Critical Branch | TTC Validation phase - bilateral reduction | 259 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 1230 | 7093 |  |  | 7077 |  |  |  |  | -4400 | -4400 | -4384 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - RDCR FIL 1 & 2
2025-09-12 | September | 2130 | 7966 |  |  | 7686 |  |  |  |  | -1710 | -1710 | -1328 | Critical Branch | TTC Validation phase - bilateral reduction | 280 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 2230 | 7966 |  |  | 7686 |  |  |  |  | -1710 | -1710 | -1328 | Critical Branch | TTC Validation phase - bilateral reduction | 280 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 2330 | 7366 |  |  | 7312 |  |  |  |  | -1103 | -1103 | -1041 | Critical Branch | TTC Validation phase - bilateral reduction | 54 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-13 | September | 1230 | 6639 |  |  | 5511 |  |  |  |  | -3817 | -3817 | -2709 | Critical Branch | TTC Validation phase - bilateral reduction | 1128 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-13 | September | 1330 | 6639 |  |  | 5566 |  |  |  |  | -3817 | -3817 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 1073 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-13 | September | 1430 | 6639 |  |  | 5350 |  |  |  |  | -3817 | -3817 | -2550 | Critical Branch | TTC Validation phase - bilateral reduction | 1289 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-17 | September | 1530 | 7814 |  |  | 7600 |  |  |  |  | -1810 | -1810 | -1622 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 1630 | 7814 |  |  | 7600 |  |  |  |  | -1810 | -1810 | -1622 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 1730 | 7814 |  |  | 7600 |  |  |  |  | -1810 | -1810 | -1622 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 2130 | 7706 |  |  | 7538 |  |  |  |  | -2049 | -2049 | -1885 | Critical Branch | TTC Validation phase - bilateral reduction | 168 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 2230 | 7706 |  |  | 7538 |  |  |  |  | -2049 | -2049 | -1885 | Critical Branch | TTC Validation phase - bilateral reduction | 168 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 2330 | 7106 |  |  | 7102 |  |  |  |  | -1440 | -1440 | -1436 | Critical Branch | TTC Validation phase - bilateral reduction | 4 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border
2025-09-18 | September | 1530 | 7455 |  |  | 7270 |  |  |  |  | -3271 | -3271 | -3028 | Critical Branch | TTC Validation phase - bilateral reduction | 185 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-18 | September | 1630 | 7455 |  |  | 7270 |  |  |  |  | -3271 | -3271 | -3028 | Critical Branch | TTC Validation phase - bilateral reduction | 185 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-18 | September | 1730 | 7755 |  |  | 7572 |  |  |  |  | -3553 | -3553 | -3312 | Critical Branch | TTC Validation phase - bilateral reduction | 183 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2
2025-09-18 | September | 2130 | 7735 |  |  | 7560 |  |  |  |  | -3789 | -3789 | -3560 | Critical Branch | ID schedules | 175 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-18 | September | 2230 | 7735 |  |  | 7560 |  |  |  |  | -3789 | -3789 | -3560 | Critical Branch | ID schedules | 175 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-19 | September | 1230 | 7352 |  |  | 7111 |  |  |  |  | -5052 | -5052 | -4787 | Critical Branch | TTC Validation phase - bilateral reduction | 241 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-19 | September | 1330 | 7352 |  |  | 7111 |  |  |  |  | -5052 | -5052 | -4787 | Critical Branch | TTC Validation phase - bilateral reduction | 241 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-19 | September | 1430 | 7352 |  |  | 7207 |  |  |  |  | -5052 | -5052 | -4905 | Critical Branch | TTC Validation phase - bilateral reduction | 145 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2
2025-09-19 | September | 1530 | 7862 |  |  | 7489 |  |  |  |  | -1319 | -1319 | -809 | Critical Branch | TTC Validation phase - bilateral reduction | 373 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2
2025-09-19 | September | 1630 | 7862 |  |  | 7489 |  |  |  |  | -1319 | -1319 | -809 | Critical Branch | TTC Validation phase - bilateral reduction | 373 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2
2025-09-19 | September | 1730 | 8162 |  |  | 7356 |  |  |  |  | -1560 | -1560 | -665 | Critical Branch | ID schedules | 806 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - N-2 Albertville-Rondissone / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR]
2025-09-19 | September | 2130 | 6805 |  |  | 6804 |  |  |  |  | -1676 | -1676 | -1674 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 |  |  | AT | -361 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-19 | September | 2230 | 6805 |  |  | 6804 |  |  |  |  | -1676 | -1676 | -1674 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 |  |  | AT | -361 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-20 | September | 1530 | 7687 |  |  | 6302 |  |  |  |  | 1354 | 199 | 2427 | Minimum Margin | TTC Validation phase - bilateral reduction | 1385 | NA | 1272 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-20 | September | 1630 | 7687 |  |  | 7392 |  |  |  |  | 1354 | 199 | 1601 | Minimum Margin | TTC Validation phase - bilateral reduction | 295 | NA | 446 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-20 | September | 1730 | 7990 |  |  | 7637 |  |  |  |  | 1173 | 202 | 1477 | Minimum Margin | TTC Validation phase - bilateral reduction | 353 | NA | 506 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-20 | September | 2130 | 7629 |  |  | 7492 |  |  |  |  | -5132 | -5132 | -4999 | Critical Branch | TTC Validation phase - bilateral reduction | 137 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-20 | September | 2230 | 7629 |  |  | 7492 |  |  |  |  | -5132 | -5132 | -4999 | Critical Branch | TTC Validation phase - bilateral reduction | 137 | NA | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-20 | September | 2330 | 7029 |  |  | 7028 |  |  |  |  | -4534 | -4534 | -4532 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-21 | September | 1230 | 3959 |  |  | 3500 |  |  |  |  | -4549 | -4549 | -4201 | Critical Branch | TTC Validation phase - bilateral reduction | 459 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-21 | September | 1330 | 3959 |  |  | 3500 |  |  |  |  | -4549 | -4549 | -4201 | Critical Branch | TTC Validation phase - bilateral reduction | 459 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-21 | September | 1530 | 7501 |  |  | 4972 |  |  |  |  | 435 | 360 | 2803 | Minimum Margin | TTC Validation phase - bilateral reduction | 2529 | NA | 2728 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-21 | September | 1630 | 7501 |  |  | 6671 |  |  |  |  | 435 | 360 | 942 | Minimum Margin | TTC Validation phase - bilateral reduction | 830 | NA | 867 |  |  | AT | 160 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-21 | September | 1730 | 7534 |  |  | 7498 |  |  |  |  | 193 | 193 | 27 | Adjustment reached | TTC Validation phase - bilateral reduction | 36 | NA | 27 |  |  | AT | 160 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-21 | September | 2130 | 6708 |  |  | 6707 |  |  |  |  | -1452 | -1452 | -1451 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-21 | September | 2230 | 6708 |  |  | 6707 |  |  |  |  | -1452 | -1452 | -1451 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-21 | September | 2330 | 6708 |  |  | 6707 |  |  |  |  | -1452 | -1452 | -1451 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-25 | September | 2130 | 8258 |  |  | 7921 |  |  |  |  | -1912 | -1912 | -1640 | Critical Branch | TTC Validation phase - bilateral reduction | 337 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-25 | September | 2230 | 8258 |  |  | 7921 |  |  |  |  | -1912 | -1912 | -1640 | Critical Branch | TTC Validation phase - bilateral reduction | 337 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-25 | September | 2330 | 7658 |  |  | 7464 |  |  |  |  | 0 | 0 | -1148 | Critical Branch | TTC Validation phase - bilateral reduction | 194 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-26 | September | 1230 | 7688 |  |  | 6879 |  |  |  |  | -411 | -411 | 133 | Critical Branch | TTC Validation phase - bilateral reduction | 809 | NA | 133 | [5 empty] | CH | 6629 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 2500 | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2
2025-09-26 | September | 1330 | 7688 |  |  | 7018 |  |  |  |  | -411 | -411 | 39 | Critical Branch | TTC Validation phase - bilateral reduction | 670 | NA | 39 | [5 empty] | CH | 6768 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 2500 | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2
2025-09-26 | September | 1430 | 7688 |  |  | 7375 |  |  |  |  | -296 | -296 | -85 | Critical Branch | TTC Validation phase - bilateral reduction | 313 | NA | 0 | [5 empty] | CH | 7337 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 2500 | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2
2025-09-27 | September | 2130 | 8586 |  |  | 8585 |  |  |  |  | -4038 | -4038 | -4035 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-27 | September | 2230 | 8586 |  |  | 8585 |  |  |  |  | -4038 | -4038 | -4035 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-27 | September | 2330 | 7986 |  |  | 7985 |  |  |  |  | -3438 | -3438 | -3435 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-09-28 | September | 2130 | 8555 |  |  | 8485 |  |  |  |  | -254 | -254 | -189 | Critical Branch | ID schedules | 70 | NA | 0 |  |  | AT | -415 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 3600 | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT |  |  |  | IT | -10000 | ATC blocked
2025-09-28 | September | 2230 | 8555 |  |  | 8485 |  |  |  |  | -254 | -254 | -189 | Critical Branch | ID schedules | 70 | NA | 0 |  |  | AT | -415 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 3600 | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT |  |  |  | IT | -10000 | ATC blocked
2025-09-28 | September | 2330 | 8555 |  |  | 8302 |  |  |  |  | -254 | -254 | -69 | Critical Branch | ID schedules | 253 | NA | 0 |  |  | AT | -232 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 3600 | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT |  |  |  | IT | -10000 | ATC blocked
2025-07-01 | July | 1230 | 5327 |  |  | 5320 |  |  |  |  | 0 | 0 | -1648 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 54 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [6 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 1330 | 5327 |  |  | 5320 |  |  |  |  | 0 | 0 | -2583 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 54 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [6 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 1430 | 5327 |  |  | 5320 |  |  |  |  | 0 | 0 | -2583 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 54 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [6 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 1530 | 6759 |  |  | 6758 |  |  |  |  | 11 | 11 | 2 | Adjustment reached | Smoothing ramp | 1 | NA | 2 | Smoothing ramp | Smoothing ramp |  |  |  | CH | 7845 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
2025-07-02 | July | 1530 | 8457 |  |  | 6952 |  |  |  |  | 0 | 0 | 1205 | Critical Branch | Smoothing ramp | 1505 | NA | 1205 | Smoothing ramp | Smoothing ramp |  |  |  | CH | 6649 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano
2025-07-02 | July | 1630 | 8457 |  |  | 8390 |  |  |  |  | 0 | 0 | -233 | Critical Branch | TTC Validation phase - bilateral reduction | 67 | NA | 0 |  |  | AT | 70 | Reduction because NTC over thermal limit on border | CH | 8075 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
2025-07-02 | July | 1730 | 8757 |  |  | 8231 |  |  |  |  | -666 | -666 | -140 | Critical Branch | ID schedules | 526 | NA | 0 |  |  | AT | -162 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 8435 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | [6 empty] | IT | -10000 | ATC blocked
2025-07-03 | July | 1530 | 8213 |  |  | 7845 |  |  |  |  | -2618 | -2618 | -2250 | Critical Branch | ID schedules | 368 | NA | 0 | [5 empty] | CH | 7435 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
2025-07-04 | July | 1230 | 6385 |  |  | 6321 |  |  |  |  | 0 | 0 | -15 | Critical Branch | ID schedules | 64 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 1330 | 6385 |  |  | 6321 |  |  |  |  | 0 | 0 | -15 | Critical Branch | ID schedules | 64 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 1430 | 6385 |  |  | 6321 |  |  |  |  | 0 | 0 | -15 | Critical Branch | ID schedules | 64 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 1530 | 7411 |  |  | 7353 |  |  |  |  | 0 | 0 | -112 | Critical Branch | ID schedules | 58 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 1630 | 7411 |  |  | 7353 |  |  |  |  | 0 | 0 | -112 | Critical Branch | ID schedules | 58 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 1730 | 7411 |  |  | 7353 |  |  |  |  | 0 | 0 | -112 | Critical Branch | ID schedules | 58 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 2130 | 8534 |  |  | 8426 |  |  |  |  | -2130 | -2130 | -2045 | Critical Branch | TTC Validation phase - bilateral reduction | 108 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-05 | July | 1530 | 8365 |  |  | 7029 |  |  |  |  | -658 | -658 | 678 | Critical Branch | ID schedules | 1336 | NA | 678 |  |  | AT | -339 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-05 | July | 1630 | 8365 |  |  | 7029 |  |  |  |  | -658 | -658 | 678 | Critical Branch | TTC Validation phase - bilateral reduction | 1336 | NA | 678 | [14 empty] | IT | -10000 | ATC blocked
2025-07-05 | July | 1730 | 8365 |  |  | 6750 |  |  |  |  | -658 | -658 | 862 | Critical Branch | TTC Validation phase - bilateral reduction | 1615 | NA | 862 | [14 empty] | IT | -10000 | ATC blocked
2025-07-06 | July | 1530 | 6180 |  |  | 5153 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1027 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-06 | July | 1630 | 6180 |  |  | 5377 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 803 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-06 | July | 1730 | 6180 |  |  | 5895 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 285 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-08 | July | 1530 | 6408 |  |  | 6332 |  |  |  |  | -2455 | -2455 | -2383 | Critical Branch | ID schedules | 76 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-08 | July | 1630 | 6408 |  |  | 6332 |  |  |  |  | -2455 | -2455 | -2383 | Critical Branch | ID schedules | 76 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-08 | July | 1730 | 6623 |  |  | 6539 |  |  |  |  | -2620 | -2620 | -2544 | Critical Branch | ID schedules | 84 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-11 | July | 1530 | 7739 |  |  | 7726 |  |  |  |  | -4329 | -4329 | -4320 | Critical Branch | ID schedules | 13 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-07-11 | July | 1630 | 7739 |  |  | 7726 |  |  |  |  | -4329 | -4329 | -4320 | Critical Branch | ID schedules | 13 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-07-11 | July | 1730 | 7739 |  |  | 7506 |  |  |  |  | -4329 | -4329 | -4101 | Critical Branch | ID schedules | 233 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-11 | July | 2130 | 7034 |  |  | 6961 |  |  |  |  | -4453 | -4453 | -4416 | ID schedules | ID schedules | 73 | NA | 0 | [5 empty] | CH | 6711 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-07-11 | July | 2230 | 7007 |  |  | 6947 |  |  |  |  | -4439 | -4439 | -4409 | ID schedules | ID schedules | 60 | NA | 0 | [5 empty] | CH | 6695 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-07-13 | July | 1230 | 6246 |  |  | 5507 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 739 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-13 | July | 1330 | 6246 |  |  | 5503 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 743 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-13 | July | 1430 | 6246 |  |  | 5539 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 707 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-15 | July | 1530 | 7461 |  |  | 7412 |  |  |  |  | -2807 | -2807 | -2757 | Critical Branch | ID schedules | 49 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-15 | July | 1630 | 7461 |  |  | 7412 |  |  |  |  | -2807 | -2807 | -2757 | Critical Branch | ID schedules | 49 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-15 | July | 1730 | 7461 |  |  | 7165 |  |  |  |  | -2807 | -2807 | -2511 | Critical Branch | ID schedules | 296 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-16 | July | 1530 | 7758 |  |  | 7749 |  |  |  |  | -3588 | -3588 | -3582 | Critical Branch | Smoothing ramp | 9 | NA | 0 | Smoothing ramp | Smoothing ramp | AT | 140 | Reduction because NTC over thermal limit on border
2025-07-16 | July | 1630 | 7758 |  |  | 7749 |  |  |  |  | -3588 | -3588 | -3582 | Critical Branch | ID schedules | 9 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-07-16 | July | 1730 | 7758 |  |  | 7533 |  |  |  |  | -3588 | -3588 | -3368 | Critical Branch | ID schedules | 225 | NA | 0
2025-07-17 | July | 1530 | 7116 |  |  | 7115 |  |  |  |  | -2647 | -2647 | -2645 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-07-17 | July | 1630 | 7331 |  |  | 7132 |  |  |  |  | -2813 | -2813 | -2690 | Critical Branch | TTC Validation phase - bilateral reduction | 199 | NA | 0 |  |  | AT | 70 | Reduction because NTC over thermal limit on border
2025-07-17 | July | 1730 | 7331 |  |  | 7330 |  |  |  |  | -2813 | -2813 | -2811 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-07-17 | July | 1930 | 7023 |  |  | 7019 |  |  |  |  | -5666 | -5666 | -5664 | ID schedules | TTC Validation phase - bilateral reduction | 4 | NA | 0
2025-07-18 | July | 1230 | 7792 |  |  | 7340 |  |  |  |  | -4083 | -4083 | -3595 | Critical Branch | TTC Validation phase - bilateral reduction | 452 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2000 | Bilateral - Unplanned outage MERY VIELMOULIN 1 |  |  |  | IT | -10000 | ATC blocked
2025-07-18 | July | 1330 | 7792 |  |  | 7340 |  |  |  |  | -4083 | -4083 | -3595 | Critical Branch | TTC Validation phase - bilateral reduction | 452 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2000 | Bilateral - Unplanned outage MERY VIELMOULIN 1 |  |  |  | IT | -10000 | ATC blocked
2025-07-18 | July | 1430 | 7792 |  |  | 7340 |  |  |  |  | -4083 | -4083 | -3595 | Critical Branch | TTC Validation phase - bilateral reduction | 452 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2000 | Bilateral - Unplanned outage MERY VIELMOULIN 1 |  |  |  | IT | -10000 | ATC blocked
2025-07-18 | July | 1530 | 7059 |  |  | 6890 |  |  |  |  | -4513 | -4513 | -4333 | Critical Branch | TTC Validation phase - bilateral reduction | 169 | NA | 0 | [8 empty] | FR | 2000 | Bilateral - Unplanned outage MERY VIELMOULIN 1 |  |  |  | IT | -10000 | ATC blocked
2025-07-18 | July | 1630 | 7059 |  |  | 6890 |  |  |  |  | -4513 | -4513 | -4333 | Critical Branch | TTC Validation phase - bilateral reduction | 169 | NA | 0 | [8 empty] | FR | 2000 | Bilateral - Unplanned outage MERY VIELMOULIN 1 |  |  |  | IT | -10000 | ATC blocked
2025-07-18 | July | 1730 | 7059 |  |  | 6803 |  |  |  |  | -4562 | -4562 | -4287 | Critical Branch | TTC Validation phase - bilateral reduction | 256 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-20 | July | 1230 | 5324 |  |  | 4205 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 1119 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-20 | July | 1330 | 5324 |  |  | 4200 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 1124 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-20 | July | 1430 | 5324 |  |  | 5010 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 314 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-20 | July | 1530 | 6405 |  |  | 5103 |  |  |  |  | -3653 | -3653 | -2509 | Critical Branch | ID schedules | 1302 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-25 | July | 1230 | 8065 |  |  | 7234 |  |  |  |  | 0 | 0 | 598 | Critical Branch | ID schedules | 831 | NA | 598 | [14 empty] | IT | -10000 | ATC blocked
2025-07-25 | July | 1330 | 8065 |  |  | 7234 |  |  |  |  | 0 | 0 | 598 | Critical Branch | ID schedules | 831 | NA | 598 | [14 empty] | IT | -10000 | ATC blocked
2025-07-25 | July | 1430 | 8065 |  |  | 7234 |  |  |  |  | 0 | 0 | 598 | Critical Branch | ID schedules | 831 | NA | 598 | [14 empty] | IT | -10000 | ATC blocked
2025-07-26 | July | 1530 | 8037 |  |  | 7572 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 465 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-26 | July | 1630 | 8037 |  |  | 7232 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 805 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-26 | July | 1730 | 8037 |  |  | 6925 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1112 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-26 | July | 1830 | 8037 |  |  | 6662 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1375 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-28 | July | 1230 | 8934 |  |  | 7707 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1227 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 |  |  |  | IT | -10000 | ATC blocked
2025-07-28 | July | 1330 | 8934 |  |  | 7707 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1227 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 |  |  |  | IT | -10000 | ATC blocked
2025-07-28 | July | 1430 | 8934 |  |  | 7707 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1227 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 |  |  |  | IT | -10000 | ATC blocked
2025-07-30 | July | 1530 | 8830 |  |  | 7975 |  |  |  |  | 0 | 0 | -142 | Critical Branch | Smoothing ramp | 855 | NA | 0 | Smoothing ramp | Smoothing ramp
2025-08-01 | August | 1530 | 7487 |  |  | 7443 |  |  |  |  | 2219 | -88 | 2219 | Critical Branch | ID schedules | 44 | NA | -88 | [14 empty] | IT | -10000 | ATC blocked
2025-08-01 | August | 1730 | 7487 |  |  | 7475 |  |  |  |  | 2219 | -88 | 2219 | Critical Branch | ID schedules | 12 | NA | -88 | [14 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 2130 | 8995 |  |  | 7744 |  |  |  |  | -4793 | -4793 | -3608 | Critical Branch | TTC Validation phase - bilateral reduction | 1251 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 2230 | 8995 |  |  | 7966 |  |  |  |  | -4789 | -4789 | -3780 | Critical Branch | TTC Validation phase - bilateral reduction | 1029 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 2330 | 8995 |  |  | 7736 |  |  |  |  | -4780 | -4780 | -3408 | Critical Branch | TTC Validation phase - bilateral reduction | 1259 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-05 | August | 1830 | 5764 |  |  | 5603 |  |  |  |  | 158 | 158 | 162 | Adjustment reached | ID schedules | 161 | NA | 162 |  |  | AT | -311 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 5353 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-05 | August | 1930 | 5764 |  |  | 5603 |  |  |  |  | 158 | 158 | 162 | Adjustment reached | TTC Validation phase - bilateral reduction | 161 | NA | 162 | [8 empty] | FR | 5353 | Process fail during TSO validation phase
2025-08-05 | August | 2030 | 5764 |  |  | 5603 |  |  |  |  | 158 | 158 | 162 | Adjustment reached | TTC Validation phase - bilateral reduction | 161 | NA | 162 | [8 empty] | FR | 5353 | Process fail during TSO validation phase
2025-08-06 | August | 2130 | 5688 |  |  | 5643 |  |  |  |  | -4001 | -4001 | -3955 | Critical Branch | TTC Validation phase - bilateral reduction | 45 | NA | 0
2025-08-07 | August | 2130 | 6244 |  |  | 6243 |  |  |  |  | -1054 | -1054 | -1052 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-08-07 | August | 2230 | 6244 |  |  | 6243 |  |  |  |  | -1054 | -1054 | -1052 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-08-08 | August | 2130 | 5911 |  |  | 5439 |  |  |  |  | -776 | -776 | -203 | Critical Branch | ID schedules | 472 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-08 | August | 2230 | 5911 |  |  | 5733 |  |  |  |  | -776 | -776 | -560 | Critical Branch | ID schedules | 178 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 1630 | 5461 |  |  | 5275 |  |  |  |  | -536 | -536 | -345 | Critical Branch | TTC Validation phase - bilateral reduction | 186 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 1730 | 5461 |  |  | 5119 |  |  |  |  | -530 | -530 | -174 | Critical Branch | TTC Validation phase - bilateral reduction | 342 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 1830 | 5417 |  |  | 5100 |  |  |  |  | -2804 | -2804 | -2515 | Critical Branch | TTC Validation phase - bilateral reduction | 317 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 1930 | 5417 |  |  | 5068 |  |  |  |  | -2809 | -2809 | -2496 | Critical Branch | TTC Validation phase - bilateral reduction | 349 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 2030 | 5417 |  |  | 4977 |  |  |  |  | -2810 | -2810 | -2419 | Critical Branch | TTC Validation phase - bilateral reduction | 440 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1230 | 3938 |  |  | 3500 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 438 | NA | 0 |  |  | AT | 159 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1330 | 3938 |  |  | 3500 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 438 | NA | 0 |  |  | AT | 159 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1430 | 3938 |  |  | 3500 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 438 | NA | 0 |  |  | AT | 159 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 1530 | 5628 |  |  | 3750 |  |  |  |  | -2593 | -2593 | -752 | Critical Branch | ID schedules | 1878 | NA | 0 |  |  | AT | -285 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 1630 | 5628 |  |  | 3660 |  |  |  |  | -2593 | -2593 | -616 | Critical Branch | ID schedules | 1968 | NA | 0 |  |  | AT | -93 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 1730 | 5628 |  |  | 3840 |  |  |  |  | -2593 | -2593 | -775 | Critical Branch | ID schedules | 1788 | NA | 0 |  |  | AT | -50 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 2130 | 5602 |  |  | 5134 |  |  |  |  | -2828 | -2828 | -2499 | Critical Branch | ID schedules | 468 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 2230 | 5602 |  |  | 5322 |  |  |  |  | -2828 | -2828 | -2631 | Critical Branch | ID schedules | 280 | NA | 0 |  |  | AT | -48 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 2330 | 5042 |  |  | 4731 |  |  |  |  | -2265 | -2265 | -2046 | Critical Branch | ID schedules | 311 | NA | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-12 | August | 2030 | 4182 |  |  | 4094 |  |  |  |  | -3180 | -3180 | -3120 | Critical Branch | ID schedules | 88 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-12 | August | 2130 | 5902 |  |  | 5598 |  |  |  |  | -1631 | -1631 | -1338 | Critical Branch | ID schedules | 304 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-12 | August | 2330 | 5342 |  |  | 5341 |  |  |  |  | -1071 | -1071 | -1069 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-08-13 | August | 2130 | 6593 |  |  | 3664 |  |  |  |  | -1363 | -1363 | 1567 | Critical Branch | ID schedules | 2929 | NA | 1567 | [5 empty] | CH | 5959 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | [6 empty] | IT | -10000 | ATC blocked
2025-08-13 | August | 2230 | 6593 |  |  | 5215 |  |  |  |  | -1363 | -1363 | 38 | Critical Branch | ID schedules | 1378 | NA | 38
2025-08-15 | August | 1230 | 2312 |  |  | 508 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 1804 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 1330 | 2312 |  |  | 506 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 1806 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 1430 | 2312 |  |  | 1602 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 710 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-18 | August | 1230 | 3501 |  |  | 2986 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 515 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-18 | August | 1330 | 3501 |  |  | 3035 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 466 | NA | 0 |  |  | AT | -335 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-18 | August | 1430 | 3501 |  |  | 3168 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 333 | NA | 0 |  |  | AT | -182 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-20 | August | 1230 | 6514 |  |  | 6006 |  |  |  |  | 106 | 106 | 451 | Adjustment reached | TTC Validation phase - bilateral reduction | 508 | NA | 451 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-20 | August | 1330 | 6514 |  |  | 6006 |  |  |  |  | 106 | 106 | 451 | Adjustment reached | TTC Validation phase - bilateral reduction | 508 | NA | 451 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-20 | August | 1430 | 6514 |  |  | 6006 |  |  |  |  | 106 | 106 | 451 | Adjustment reached | TTC Validation phase - bilateral reduction | 508 | NA | 451 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-20 | August | 1730 | 6528 |  |  | 6500 |  |  |  |  | -2860 | -2860 | -2846 | ID schedules | TTC Validation phase - bilateral reduction | 28 | NA | 0 | [5 empty] | CH | 5241 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | [6 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1230 | 5643 |  |  | 3936 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1707 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1330 | 5643 |  |  | 4305 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1338 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1430 | 5643 |  |  | 4303 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1340 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1530 | 7766 |  |  | 5076 |  |  |  |  | -3614 | -3614 | -962 | Critical Branch | TTC Validation phase - bilateral reduction | 2690 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7336 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | [6 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1630 | 7766 |  |  | 5828 |  |  |  |  | -3614 | -3614 | -1710 | Critical Branch | TTC Validation phase - bilateral reduction | 1938 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1730 | 7766 |  |  | 5962 |  |  |  |  | -3614 | -3614 | -1843 | Critical Branch | TTC Validation phase - bilateral reduction | 1804 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1830 | 8824 |  |  | 7520 |  |  |  |  | -2088 | -2088 | -792 | Critical Branch | TTC Validation phase - bilateral reduction | 1304 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-22 | August | 1930 | 8824 |  |  | 8754 |  |  |  |  | -2088 | -2088 | -2032 | Critical Branch | TTC Validation phase - bilateral reduction | 70 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-08-22 | August | 2030 | 8824 |  |  | 8754 |  |  |  |  | -2088 | -2088 | -2032 | Critical Branch | TTC Validation phase - bilateral reduction | 70 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-08-22 | August | 2130 | 8822 |  |  | 8752 |  |  |  |  | -4856 | -4856 | -4776 | Critical Branch | TTC Validation phase - bilateral reduction | 70 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-08-22 | August | 2230 | 8822 |  |  | 8752 |  |  |  |  | -4856 | -4856 | -4776 | Critical Branch | TTC Validation phase - bilateral reduction | 70 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-08-22 | August | 2330 | 8222 |  |  | 8148 |  |  |  |  | -4258 | -4258 | -4172 | Critical Branch | TTC Validation phase - bilateral reduction | 74 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border
2025-08-23 | August | 1230 | 3552 |  |  | 2675 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 877 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 1330 | 3552 |  |  | 2675 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 877 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 1430 | 3552 |  |  | 2716 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 836 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 1530 | 5817 |  |  | 4642 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1175 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 1630 | 5817 |  |  | 5495 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 322 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 2130 | 7626 |  |  | 5868 |  |  |  |  | -4824 | -4824 | -3495 | Critical Branch | TTC Validation phase - bilateral reduction | 1758 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 2230 | 7626 |  |  | 7341 |  |  |  |  | -4716 | -4716 | -4419 | Critical Branch | TTC Validation phase - bilateral reduction | 285 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 2330 | 7026 |  |  | 7008 |  |  |  |  | -4227 | -4227 | -4212 | Critical Branch | TTC Validation phase - bilateral reduction | 18 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-24 | August | 1530 | 6502 |  |  | 5000 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1502 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-24 | August | 1830 | 7080 |  |  | 7017 |  |  |  |  | -4192 | -4192 | -4118 | Critical Branch | TTC Validation phase - bilateral reduction | 63 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-24 | August | 2030 | 7080 |  |  | 6415 |  |  |  |  | -4314 | -4314 | -3794 | Critical Branch | TTC Validation phase - bilateral reduction | 665 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-24 | August | 2130 | 7500 |  |  | 7242 |  |  |  |  | -3672 | -3672 | -3358 | Critical Branch | TTC Validation phase - bilateral reduction | 258 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-24 | August | 2230 | 7500 |  |  | 7239 |  |  |  |  | -3667 | -3667 | -3350 | Critical Branch | TTC Validation phase - bilateral reduction | 261 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-24 | August | 2330 | 7500 |  |  | 7085 |  |  |  |  | -3722 | -3722 | -3216 | Critical Branch | TTC Validation phase - bilateral reduction | 415 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 1530 | 8195 |  |  | 7716 |  |  |  |  | -3109 | -3109 | -2633 | Critical Branch | ID schedules | 479 | NA | 0 |  |  | AT | -156 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 1630 | 8195 |  |  | 8194 |  |  |  |  | -3109 | -3109 | -3107 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 |  |  | AT | -196 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 1730 | 8345 |  |  | 7711 |  |  |  |  | -3269 | -3269 | -2637 | Critical Branch | ID schedules | 634 | NA | 0 |  |  | AT | -186 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-26 | August | 1530 | 8208 |  |  | 6288 |  |  |  |  | -3439 | -3439 | -1518 | Critical Branch | TTC Validation phase - bilateral reduction | 1920 | NA | 0
2025-08-26 | August | 1630 | 8208 |  |  | 7510 |  |  |  |  | -3439 | -3439 | -2741 | Critical Branch | TTC Validation phase - bilateral reduction | 698 | NA | 0 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7886 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-26 | August | 1730 | 8358 |  |  | 7659 |  |  |  |  | -3598 | -3598 | -2900 | Critical Branch | TTC Validation phase - bilateral reduction | 699 | NA | 0 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7074 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-26 | August | 2130 | 8008 |  |  | 7656 |  |  |  |  | -4682 | -4682 | -4329 | Critical Branch | TTC Validation phase - bilateral reduction | 352 | NA | 0 | [5 empty] | CH | 7406 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
2025-08-26 | August | 2230 | 8008 |  |  | 8007 |  |  |  |  | -4682 | -4682 | -4681 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-08-27 | August | 1230 | 4334 |  |  | 4333 |  |  |  |  | 4307 | -118 | 4310 | Critical Branch | Validation phase | 1 | NA | -115 | [5 empty] | CH | 4083 | Reduction due to missing redispatch potential
2025-08-27 | August | 1330 | 4334 |  |  | 4333 |  |  |  |  | 4307 | -118 | 4310 | Critical Branch | Validation phase | 1 | NA | -115 | [5 empty] | CH | 4083 | Reduction due to missing redispatch potential
2025-08-27 | August | 1430 | 4334 |  |  | 4333 |  |  |  |  | 4307 | -118 | 4310 | Critical Branch | Validation phase | 1 | NA | -115 | [5 empty] | CH | 4083 | Reduction due to missing redispatch potential
2025-08-27 | August | 1530 | 7864 |  |  | 5866 |  |  |  |  | -3308 | -3308 | -1312 | Critical Branch | TTC Validation phase - bilateral reduction | 1998 | NA | 0
2025-08-27 | August | 1630 | 7864 |  |  | 7338 |  |  |  |  | -3308 | -3308 | -2785 | Critical Branch | TTC Validation phase - bilateral reduction | 526 | NA | 0 | [5 empty] | CH | 7581 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
2025-08-27 | August | 1730 | 8014 |  |  | 7913 |  |  |  |  | -3474 | -3474 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | 101 | NA | 0 |  |  | AT | -128 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 6579 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-27 | August | 2230 | 7189 |  |  | 7188 |  |  |  |  | -4235 | -4235 | -4234 | ID schedules | TTC Validation phase - bilateral reduction | 1 | NA | 0 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1230 | 4627 |  |  | 4610 |  |  |  |  | 3449 | -68 | 3455 | Critical Branch | TTC Validation phase - bilateral reduction | 17 | NA | -62 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4376 | Reduction due to missing redispatch potential | [6 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1330 | 4627 |  |  | 4610 |  |  |  |  | 3449 | -68 | 3455 | Critical Branch | TTC Validation phase - bilateral reduction | 17 | NA | -62 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4376 | Reduction due to missing redispatch potential | [6 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1430 | 4627 |  |  | 4610 |  |  |  |  | 3449 | -68 | 3455 | Critical Branch | TTC Validation phase - bilateral reduction | 17 | NA | -62 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4376 | Reduction due to missing redispatch potential | [6 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1530 | 6738 |  |  | 5550 |  |  |  |  | -2919 | -2919 | -1731 | Critical Branch | TTC Validation phase - bilateral reduction | 1188 | NA | 0 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1630 | 6738 |  |  | 6602 |  |  |  |  | -2864 | -2864 | -2704 | Critical Branch | TTC Validation phase - bilateral reduction | 136 | NA | 0 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1730 | 7103 |  |  | 6975 |  |  |  |  | -3200 | -3200 | -3053 | Critical Branch | TTC Validation phase - bilateral reduction | 128 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 2130 | 7453 |  |  | 6383 |  |  |  |  | -4178 | -4178 | -3034 | Critical Branch | TTC Validation phase - bilateral reduction | 1070 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 6615 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 2230 | 7453 |  |  | 6458 |  |  |  |  | -4178 | -4178 | -3106 | Critical Branch | TTC Validation phase - bilateral reduction | 995 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 2330 | 6853 |  |  | 5934 |  |  |  |  | -3570 | -3570 | -2576 | Critical Branch | TTC Validation phase - bilateral reduction | 919 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1230 | 6653 |  |  | 5802 |  |  |  |  | -2365 | -2365 | -1514 | Critical Branch | ID schedules | 851 | NA | 0 |  |  | AT | -330 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1330 | 6653 |  |  | 5802 |  |  |  |  | -2365 | -2365 | -1514 | Critical Branch | ID schedules | 851 | NA | 0 |  |  | AT | -330 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1430 | 6653 |  |  | 5802 |  |  |  |  | -2365 | -2365 | -1514 | Critical Branch | ID schedules | 851 | NA | 0 |  |  | AT | -330 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1530 | 6663 |  |  | 6428 |  |  |  |  | -2951 | -2951 | -2710 | Critical Branch | ID schedules | 235 | NA | 0 |  |  | AT | -392 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1630 | 6713 |  |  | 6479 |  |  |  |  | -3003 | -3003 | -2763 | Critical Branch | ID schedules | 234 | NA | 0 |  |  | AT | -392 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1730 | 8513 |  |  | 6871 |  |  |  |  | -4851 | -4851 | -3393 | Critical Branch | ID schedules | 1642 | NA | 0 |  |  | AT | -384 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 2130 | 8098 |  |  | 6548 |  |  |  |  | -2568 | -2568 | -942 | Critical Branch | ID schedules | 1550 | NA | 0 |  |  | AT | -338 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 2230 | 8098 |  |  | 6513 |  |  |  |  | -2568 | -2568 | -901 | Critical Branch | ID schedules | 1585 | NA | 0 |  |  | AT | -338 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 2330 | 7498 |  |  | 5952 |  |  |  |  | -1954 | -1954 | -331 | Critical Branch | ID schedules | 1546 | NA | 0 |  |  | AT | -324 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 2130 | 7932 |  |  | 5383 |  |  |  |  | 1645 | 531 | 3801 | Minimum Margin | ID schedules | 2549 | NA | 2687 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 7148 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-30 | August | 2230 | 7932 |  |  | 5830 |  |  |  |  | 1645 | 531 | 3539 | Minimum Margin | ID schedules | 2102 | NA | 2425 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 7148 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-30 | August | 2330 | 7339 |  |  | 5289 |  |  |  |  | 2360 | 538 | 4206 | Minimum Margin | ID schedules | 2050 | NA | 2384 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 6549 | Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-31 | August | 2130 | 6764 |  |  | 5419 |  |  |  |  | -3789 | -3789 | -2325 | Critical Branch | ID schedules | 1345 | NA | 0 | [5 empty] | CH | 6204 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 2230 | 6764 |  |  | 5438 |  |  |  |  | -3789 | -3789 | -2348 | Critical Branch | ID schedules | 1326 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 2330 | 6764 |  |  | 5469 |  |  |  |  | -3789 | -3789 | -2385 | Critical Branch | ID schedules | 1295 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-01 | September | 1830 |  | 4588 | 688 |  | 4550 | 605 |  |  | -2793 | -2793 | -2793 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 121 | 0 | [5 empty] | CH | 3747 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-09-01 | September | 1930 |  | 4601 | 714 |  | 4550 | 658 |  |  | -2789 | -2789 | -2789 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 107 | 0 | [5 empty] | CH | 3669 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-09-01 | September | 2030 |  | 4601 | 714 |  | 4550 | 676 |  |  | -2789 | -2789 | -2789 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 89 | 0 | [5 empty] | CH | 3839 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-09-02 | September | 1830 |  | 5666 | 785 |  | 4477 | 683 |  |  | -3656 | -3656 | -3656 | Critical Branch | ID schedules | NA | 1291 | 0 |  |  | AT | -99 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4674 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-02 | September | 1930 |  | 5666 | 785 |  | 4477 | 728 |  |  | -3656 | -3656 | -3656 | Critical Branch | ID schedules | NA | 1246 | 0 |  |  | AT | -99 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5028 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-02 | September | 2030 |  | 5666 | 785 |  | 4461 | 724 |  |  | -3656 | -3656 | -3656 | Critical Branch | ID schedules | NA | 1266 | 0 |  |  | AT | -99 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4998 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-02 | September | 2130 |  | 4355 | 505 |  | 4276 | 545 |  |  | -3243 | -3243 | -3243 | ID schedules | TTC Validation phase - bilateral reduction | NA | 39 | 0 |  |  | AT | 227 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 3626 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-02 | September | 2230 |  | 4433 | 56 |  | 4321 | 56 |  |  | -3305 | -3305 | -3305 | ID schedules | ID schedules | NA | 112 | 0 |  |  | AT | 276 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 2905 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-02 | September | 2330 |  | 3829 | 32 |  | 3761 | 32 |  |  | -2669 | -2669 | -2669 | ID schedules | ID schedules | NA | 68 | 0 |  |  | AT | 256 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-03 | September | 1830 |  | 6416 | 857 |  | 6202 | 852 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 219 | 0 |  |  | AT | 384 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2
2025-09-03 | September | 1930 |  | 6416 | 857 |  | 6096 | 816 |  |  | 0 | 0 | 0 | GSK Limitation | Validation phase | NA | 361 | 0 |  |  | AT | 194 | Reduction because NTC over thermal limit on border | CH | 5906 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2
2025-09-03 | September | 2030 |  | 6416 | 857 |  | 6242 | 852 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 179 | 0 |  |  | AT | 194 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2
2025-09-04 | September | 1830 |  | 5917 | 798 |  | 5831 | 798 |  |  | -5140 | -5140 | -5140 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 86 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-04 | September | 1930 |  | 5917 | 798 |  | 5831 | 798 |  |  | -5140 | -5140 | -5140 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 86 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-04 | September | 2030 |  | 5917 | 798 |  | 5831 | 798 |  |  | -5140 | -5140 | -5140 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 86 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-05 | September | 1830 |  | 6283 | 965 |  | 6276 | 947 |  |  | -4596 | -4596 | -4596 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 25 | 0 |  |  | AT | 223 | Reduction because NTC over thermal limit on border
2025-09-05 | September | 1930 |  | 6292 | 969 |  | 6142 | 947 |  |  | -4598 | -4598 | -4598 | ID schedules | TTC Validation phase - bilateral reduction | NA | 172 | 0 |  |  | AT | 192 | Reduction because NTC over thermal limit on border | CH | 5952 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-09-05 | September | 2030 |  | 6292 | 969 |  | 6231 | 947 |  |  | -4598 | -4598 | -4598 | ID schedules | TTC Validation phase - bilateral reduction | NA | 83 | 0 |  |  | AT | 192 | Reduction because NTC over thermal limit on border | CH | 6041 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-09-05 | September | 2130 |  | 6826 | 680 |  | 6671 | 665 |  |  | -2082 | -2082 | -2082 | Critical Branch | ID schedules | NA | 170 | 0 | [5 empty] | CH | 6421 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE
2025-09-05 | September | 2230 |  | 6827 | 680 |  | 6761 | 673 |  |  | -2081 | -2081 | -2081 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 73 | 0 | [5 empty] | CH | 6506 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE
2025-09-05 | September | 2330 |  | 6291 | 705 |  | 6274 | 705 |  |  | -1503 | -1503 | -1503 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 17 | 0
2025-09-06 | September | 1530 |  | 5683 | 554 |  | 5510 | 554 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 173 | 0 |  |  | AT | 343 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2 |  |  |  | IT | -10000 | ATC blocked
2025-09-06 | September | 1630 |  | 5683 | 554 |  | 5682 | 554 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1 | 0 |  |  | AT | 345 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2 |  |  |  | IT | -10000 | ATC blocked
2025-09-06 | September | 1730 |  | 5683 | 554 |  | 5682 | 554 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2
2025-09-06 | September | 1830 |  | 5073 | 626 |  | 5073 | 625 |  |  | -3813 | -3813 | -3813 | ID schedules | ID schedules | NA | 1 | 0 |  |  | AT | 182 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-07 | September | 1230 |  | 2134 | 335 |  | 1834 | 335 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 300 | 0
2025-09-07 | September | 1330 |  | 2134 | 335 |  | 1760 | 335 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 374 | 0
2025-09-07 | September | 1430 |  | 2134 | 335 |  | 1262 | 335 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 872 | 0
2025-09-07 | September | 1530 |  | 4411 | 923 |  | 3287 | 906 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1141 | 0 |  |  | AT | 64 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-07 | September | 1630 |  | 3434 | 1026 |  | 3434 | 995 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 31 | 0 |  |  | AT | 38 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-07 | September | 1730 |  | 4339 | 1025 |  | 4317 | 993 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 54 | 0 |  |  | AT | -152 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-07 | September | 1830 |  | 6510 | 726 |  | 5191 | 726 |  |  | -3552 | -3552 | -3552 | Critical Branch | ID schedules | NA | 1319 | 0 |  |  | AT | 413 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-07 | September | 1930 |  | 6510 | 726 |  | 5961 | 726 |  |  | -3552 | -3552 | -3552 | Critical Branch | ID schedules | NA | 549 | 0 |  |  | AT | 413 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-07 | September | 2030 |  | 6510 | 726 |  | 6163 | 726 |  |  | -3552 | -3552 | -3552 | Critical Branch | ID schedules | NA | 347 | 0 |  |  | AT | 413 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-08 | September | 1830 |  | 6495 | 739 |  | 6406 | 660 |  |  | -877 | -877 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 168 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-08 | September | 1930 |  | 6495 | 739 |  | 6406 | 660 |  |  | -877 | -877 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 168 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-08 | September | 2030 |  | 6495 | 739 |  | 5689 | 660 |  |  | -877 | -877 | -877 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 885 | 0 | [5 empty] | CH | 5306 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 2500 | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-08 | September | 2130 |  | 5999 | 620 |  | 6063 | 521 |  |  | -4091 | -4091 | -4091 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 35 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-08 | September | 2230 |  | 6009 | 657 |  | 5988 | 657 |  |  | -4076 | -4076 | -4076 | ID schedules | ID schedules | NA | 21 | 0 | [5 empty] | CH | 5649 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-09 | September | 1730 |  | 7176 | 703 |  | 6959 | 703 |  |  | -205 | -205 | -205 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 217 | 0 |  |  | AT | 365 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2
2025-09-09 | September | 1830 |  | 5815 | 799 |  | 5654 | 798 |  |  | -3831 | -3831 | -3831 | ID schedules | TTC Validation phase - bilateral reduction | NA | 162 | 0 | [5 empty] | CH | 5322 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2
2025-09-09 | September | 1930 |  | 5828 | 799 |  | 4976 | 798 |  |  | -3839 | -3839 | -3839 | ID schedules | TTC Validation phase - bilateral reduction | NA | 853 | 0 |  |  | AT | -119 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5522 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-09 | September | 2030 |  | 5837 | 799 |  | 5076 | 799 |  |  | -3845 | -3845 | -3845 | ID schedules | TTC Validation phase - bilateral reduction | NA | 761 | 0 |  |  | AT | -119 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-09 | September | 2130 |  | 6469 | 849 |  | 5102 | 799 |  |  | -3825 | -3825 | -3825 | Critical Branch | ID schedules | NA | 1417 | 0 |  |  | AT | 232 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5853 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-09 | September | 2230 |  | 6512 | 849 |  | 6172 | 842 |  |  | -3846 | -3846 | -3846 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 347 | 0 |  |  | AT | 166 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned Outage G.ILE PIOSSASCO 1 and 2
2025-09-09 | September | 2330 |  | 5904 | 894 |  | 5845 | 886 |  |  | -3235 | -3235 | -3235 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 67 | 0 |  |  | AT | 335 | Reduction because NTC over thermal limit on border
2025-09-10 | September | 1530 |  | 6912 | 667 |  | 6874 | 667 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 38 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - N-2 Albertville-Rondissone
2025-09-10 | September | 1630 |  | 6912 | 667 |  | 6808 | 667 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 104 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - N-2 Albertville-Rondissone
2025-09-10 | September | 1730 |  | 6912 | 667 |  | 5324 | 557 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1698 | 0 | [5 empty] | CH | 5503 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 2500 | Bilateral - Outage - N-2 Albertville-Rondissone
2025-09-11 | September | 1530 |  | 6818 | 644 |  | 6800 | 644 |  |  | -1847 | -1847 | -1847 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 18 | 0 |  |  | AT | 358 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-11 | September | 1630 |  | 6856 | 658 |  | 6800 | 658 |  |  | -1882 | -1882 | -1882 | ID schedules | TTC Validation phase - bilateral reduction | NA | 56 | 0 |  |  | AT | 358 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-11 | September | 1730 |  | 6856 | 658 |  | 6800 | 658 |  |  | -1882 | -1882 | -1882 | ID schedules | TTC Validation phase - bilateral reduction | NA | 56 | 0 |  |  | AT | 358 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-11 | September | 1830 |  | 7508 | 919 |  | 6959 | 900 |  |  | -3142 | -3142 | -3142 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 568 | 0 |  |  | AT | 365 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-11 | September | 1930 |  | 7592 | 919 |  | 7036 | 900 |  |  | -3134 | -3134 | -3134 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 575 | 0 |  |  | AT | 208 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-11 | September | 2030 |  | 7507 | 919 |  | 6958 | 900 |  |  | -3142 | -3142 | -3142 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 568 | 0 |  |  | AT | 365 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 1530 |  | 7399 | 717 |  | 6910 | 717 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 489 | 0 |  |  | AT | 365 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - RDCR FIL 1 & 2
2025-09-12 | September | 1630 |  | 7399 | 717 |  | 6969 | 717 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 430 | 0 |  |  | AT | 365 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 1730 |  | 7459 | 717 |  | 7049 | 717 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 410 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 1830 |  | 6384 | 890 |  | 6225 | 879 |  |  | -1206 | -1206 | -1206 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 170 | 0 |  |  | AT | 311 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-12 | September | 1930 |  | 6676 | 890 |  | 5743 | 785 |  |  | -1415 | -1415 | -1415 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1038 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5553 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-12 | September | 2030 |  | 6676 | 890 |  | 5736 | 784 |  |  | -1415 | -1415 | -1415 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1046 | 0 |  |  | AT | 198 | Reduction because NTC over thermal limit on border | CH | 5546 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2
2025-09-14 | September | 1230 |  | 4441 | 387 |  | 4333 | 387 |  |  | -715 | -715 | -715 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 108 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-14 | September | 1530 |  | 5042 | 645 |  | 5020 | 645 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 22 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-14 | September | 1730 |  | 5985 | 645 |  | 5985 | 581 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 64 | 0 |  |  | AT | -27 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5154 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-14 | September | 2030 |  | 5547 | 671 |  | 5547 | 613 |  |  | -4570 | -4570 | -4570 | ID schedules | ID schedules | NA | 58 | 0 |  |  | AT | 376 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4949 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-15 | September | 1830 |  | 6956 | 657 |  | 6935 | 657 |  |  | -4580 | -4580 | -4580 | ID schedules | ID schedules | NA | 21 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - HVDC FIL 1 & 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-15 | September | 1930 |  | 6956 | 657 |  | 6935 | 657 |  |  | -4580 | -4580 | -4580 | ID schedules | ID schedules | NA | 21 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - HVDC FIL 1 & 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-15 | September | 2030 |  | 6955 | 559 |  | 6935 | 559 |  |  | -4579 | -4579 | -4579 | ID schedules | ID schedules | NA | 20 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - HVDC FIL 1 & 2 |  |  |  | IT | -10000 | ATC blocked
2025-09-16 | September | 1630 |  | 7007 | 661 |  | 6926 | 661 |  |  | -2737 | -2737 | -2737 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 81 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - HVDC FIL 1 & 2
2025-09-16 | September | 1730 |  | 7022 | 661 |  | 6926 | 661 |  |  | -2744 | -2744 | -2744 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 96 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - HVDC FIL 1 & 2
2025-09-17 | September | 1830 |  | 6513 | 851 |  | 6380 | 847 |  |  | -3159 | -3159 | -3159 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 137 | 0 |  |  | AT | 363 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 1930 |  | 6602 | 851 |  | 6456 | 845 |  |  | -3206 | -3206 | -3206 | Critical Branch | Validation phase | NA | 152 | 0 |  |  | AT | 196 | Reduction because NTC over thermal limit on border | CH | 6393 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-17 | September | 2030 |  | 6512 | 851 |  | 6259 | 827 |  |  | -3158 | -3158 | -3158 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 277 | 0 |  |  | AT | 363 | Reduction because NTC over thermal limit on border | CH | 6123 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | FR | 2500 | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2
2025-09-18 | September | 1830 |  | 6398 | 953 |  | 6336 | 950 |  |  | -974 | -974 | -974 | Critical Branch | Validation phase | NA | 65 | 0 | [5 empty] | CH | 6183 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2
2025-09-18 | September | 1930 |  | 6398 | 953 |  | 5968 | 900 |  |  | -974 | -974 | -974 | Critical Branch | Validation phase | NA | 483 | 0 | [5 empty] | CH | 5778 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 2500 | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2
2025-09-18 | September | 2030 |  | 6317 | 953 |  | 6061 | 928 |  |  | -938 | -938 | -938 | Critical Branch | ID schedules | NA | 281 | 0 | [5 empty] | CH | 5921 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-09-19 | September | 1830 |  | 5342 | 913 |  | 5342 | 827 |  |  | -1084 | -1084 | -1084 | Critical Branch | ID schedules | NA | 86 | 0 |  |  | AT | 156 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-19 | September | 1930 |  | 5342 | 913 |  | 5342 | 827 |  |  | -1084 | -1084 | -1084 | Critical Branch | ID schedules | NA | 86 | 0 |  |  | AT | 156 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-19 | September | 2030 |  | 5342 | 913 |  | 5342 | 827 |  |  | -1084 | -1084 | -1084 | Critical Branch | ID schedules | NA | 86 | 0 |  |  | AT | 156 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 1530 |  | 6270 | 648 |  | 6270 | 351 |  |  | -3715 | -3715 | -3005 | ID schedules | TTC Validation phase - bilateral reduction | NA | 297 | -3005 | [14 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 1630 |  | 6270 | 680 |  | 6270 | 465 |  |  | -3356 | -3356 | -2950 | ID schedules | TTC Validation phase - bilateral reduction | NA | 215 | -2950 | [5 empty] | CH | 5766 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 1730 |  | 5897 | 814 |  | 5897 | 766 |  |  | -2583 | -2583 | -2904 | ID schedules | TTC Validation phase - bilateral reduction | NA | 48 | -2904 | [5 empty] | CH | 5400 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 2030 |  | 4818 | 529 |  | 4818 | 291 |  |  | -2646 | -2646 | -4150 | ID schedules | TTC Validation phase - bilateral reduction | NA | 238 | -4150 |  |  | AT | 178 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4196 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 2130 |  | 6199 | 657 |  | 6197 | 657 |  |  | -2124 | -2124 | -2267 | ID schedules | ID schedules | NA | 2 | -2267 | [14 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 2230 |  | 6262 | 626 |  | 6261 | 222 |  |  | -2187 | -2187 | -2294 | ID schedules | TTC Validation phase - bilateral reduction | NA | 405 | -2294 | [5 empty] | CH | 5968 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-09-23 | September | 2330 |  | 5701 | 651 |  | 5701 | 97 |  |  | -1649 | -1649 | -1648 | ID schedules | TTC Validation phase - bilateral reduction | NA | 554 | -1648 | [14 empty] | IT | -10000 | ATC blocked
2025-09-24 | September | 1530 |  | 6173 | 819 |  | 6107 | 391 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 494 | 0 |  |  | AT | 289 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-24 | September | 1630 |  | 6173 | 819 |  | 6107 | 708 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 177 | 0 |  |  | AT | -27 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-24 | September | 1730 |  | 6173 | 819 |  | 6107 | 824 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 61 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-25 | September | 1230 |  | 6083 | 842 |  | 6082 | 839 |  |  | -39 | -39 | -39 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4 | 0 |  |  | AT | 170 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-09-25 | September | 1330 |  | 6084 | 842 |  | 6084 | 839 |  |  | -39 | -39 | -39 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 3 | 0 |  |  | AT | 170 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-09-25 | September | 1430 |  | 5943 | 842 |  | 5890 | 839 |  |  | -28 | -28 | -28 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 56 | 0 |  |  | AT | 385 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-09-25 | September | 1530 |  | 7117 | 712 |  | 7016 | 712 |  |  | -413 | -413 | -413 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 101 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-25 | September | 1630 |  | 7136 | 712 |  | 7031 | 712 |  |  | -417 | -417 | -417 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 105 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-25 | September | 1730 |  | 7132 | 712 |  | 7025 | 712 |  |  | -417 | -417 | -417 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 107 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-25 | September | 1830 |  | 7040 | 725 |  | 7038 | 725 |  |  | -489 | -489 | -489 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2 | 0 | [8 empty] | FR | 2500 | Bilateral - Outage - Retrait HVDC |  |  |  | IT | -10000 | ATC blocked
2025-09-25 | September | 1930 |  | 7058 | 725 |  | 6972 | 725 |  |  | -493 | -493 | -493 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 86 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-09-26 | September | 1530 |  | 5661 | 125 |  | 5656 | 125 |  |  | -579 | -579 | -579 | ID schedules | TTC Validation phase - bilateral reduction | NA | 5 | 0
2025-09-26 | September | 1830 |  | 7869 | 893 |  | 7762 | 880 |  |  | -1490 | -1490 | -1490 | Critical Branch | ID schedules | NA | 120 | 0 |  |  | AT | 181 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3600 | Bilateral - Outage - GENISSIAT S1.2
2025-09-26 | September | 1930 |  | 7873 | 893 |  | 7873 | 880 |  |  | -1492 | -1492 | -1492 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 13 | 0 |  |  | AT | 187 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3600 | Bilateral - Outage - GENISSIAT S1.2
2025-09-26 | September | 2030 |  | 7739 | 892 |  | 7676 | 880 |  |  | -1490 | -1490 | -1490 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 75 | 0 |  |  | AT | 360 | Reduction because NTC over thermal limit on border
2025-09-27 | September | 1530 |  | 6212 | -223 |  | 6178 | -224 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 35 | 0 | [5 empty] | CH | 5619 | Reduction due to missing redispatch potential
2025-09-27 | September | 1630 |  | 7173 | 654 |  | 7096 | 654 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 77 | 0 | [5 empty] | CH | 6589 | Reduction due to missing redispatch potential
2025-09-27 | September | 1730 |  | 6322 | -296 |  | 6289 | -296 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 33 | 0 | [5 empty] | CH | 5727 | Reduction due to missing redispatch potential
2025-09-27 | September | 1830 |  | 7679 | 907 |  | 7284 | 856 |  |  | -1955 | -1955 | -1955 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 446 | 0 |  |  | AT | 174 | Reduction because NTC over thermal limit on border | CH | 7067 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 3800 | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH]
2025-09-27 | September | 1930 |  | 7740 | 924 |  | 7654 | 907 |  |  | -1987 | -1987 | -1987 | ID schedules | TTC Validation phase - bilateral reduction | NA | 103 | 0 |  |  | AT | 176 | Reduction because NTC over thermal limit on border | CH | 7387 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 3800 | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH]
2025-09-27 | September | 2030 |  | 7655 | 907 |  | 7356 | 867 |  |  | -1952 | -1952 | -1952 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 339 | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border | CH | 7175 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | FR | 3800 | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH]
2025-09-28 | September | 1230 |  | 2273 | 347 |  | 2110 | 347 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 163 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-28 | September | 1330 |  | 2530 | 205 |  | 1830 | 205 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 700 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-28 | September | 1530 |  | 4722 | 801 |  | 3642 | 813 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 1068 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-28 | September | 1630 |  | 5146 | 801 |  | 5034 | 813 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 100 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-28 | September | 1730 |  | 6125 | 729 |  | 4882 | 265 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1707 | 0 |  |  | AT | 361 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-09-28 | September | 1830 |  | 7403 | 780 |  | 6924 | 780 |  |  | -1162 | -1162 | -1162 | ID schedules | TTC Validation phase - bilateral reduction | NA | 479 | 0 |  |  | AT | 415 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 3600 | Bilateral - N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] |  |  |  | IT | -10000 | ATC blocked
2025-09-29 | September | 1230 |  | 6597 | 651 |  | 6592 | 651 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 5 | 0
2025-09-29 | September | 1530 |  | 7109 | 800 |  | 7109 | 699 |  |  | -3055 | -3055 | -3055 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 101 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-29 | September | 1630 |  | 7076 | 803 |  | 7076 | 705 |  |  | -3032 | -3032 | -3032 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 98 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-29 | September | 1730 |  | 7059 | 803 |  | 6778 | 793 |  |  | -3022 | -3022 | -3022 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 291 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-29 | September | 1830 |  | 5713 | 894 |  | 5410 | 882 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 315 | 0 |  |  | AT | 157 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4700 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-09-29 | September | 1930 |  | 5750 | 894 |  | 5659 | 882 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 103 | 0 |  |  | AT | 139 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4991 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-09-29 | September | 2030 |  | 5761 | 894 |  | 5556 | 882 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 217 | 0 |  |  | AT | 134 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 4829 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-09-29 | September | 2130 |  | 7347 | 651 |  | 7092 | 651 |  |  | -2654 | -2654 | -2654 | ID schedules | TTC Validation phase - bilateral reduction | NA | 255 | 0
2025-09-29 | September | 2330 |  | 6724 | 664 |  | 6686 | 278 |  |  | -2003 | -2003 | -2003 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 424 | 0
2025-09-30 | September | 1430 |  | 6861 | 793 |  | 6859 | 793 |  |  | -1925 | -1925 | -1909 | ID schedules | TTC Validation phase - bilateral reduction | NA | 2 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] ROBBIA-FIORANO [DIR] [CH]
2025-09-30 | September | 1530 |  | 6791 | 764 |  | 6790 | 764 |  |  | -3005 | -3005 | -1925 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-30 | September | 1630 |  | 6708 | 497 |  | 6703 | 497 |  |  | -2950 | -2950 | -3005 | ID schedules | TTC Validation phase - bilateral reduction | NA | 5 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-30 | September | 1730 |  | 6638 | 425 |  | 6638 | 418 |  |  | -2904 | -2904 | -2950 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 7 | 0 | [5 empty] | CH | 6373 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-30 | September | 2130 |  | 7278 | 381 |  | 7119 | 381 |  |  | -2267 | -2267 | -4150 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 159 | 0 | [8 empty] | FR | 3600 | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT]
2025-09-30 | September | 2330 |  | 6772 | 406 |  | 6731 | 406 |  |  | -1648 | -1648 | -2294 | Critical Branch | ID schedules | NA | 41 | 0
2025-07-01 | July | 1830 |  | 4488 | 3008 |  | 4488 | 1709 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1299 | 0 |  |  | AT | -55 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 1930 |  | 4488 | 3008 |  | 4488 | 2337 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 671 | 0 |  |  | AT | 121 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 2030 |  | 4488 | 3008 |  | 4488 | 2667 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 341 | 0 |  |  | AT | 121 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 2130 |  | 4923 | 3264 |  | 4875 | 1778 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1534 | 0 |  |  | AT | 78 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 2230 |  | 4923 | 3264 |  | 4875 | 1219 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 2093 | 0 |  |  | AT | 78 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-01 | July | 2330 |  | 4600 | 3479 |  | 4424 | 1161 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 2494 | 0 |  |  | AT | 79 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-02 | July | 1830 |  | 6247 | 612 |  | 6247 | 564 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 48 | 0 |  |  | AT | 172 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-02 | July | 1930 |  | 6247 | 612 |  | 6247 | 101 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 511 | 0 |  |  | AT | 172 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-02 | July | 2030 |  | 6247 | 612 |  | 6247 | 101 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 511 | 0 |  |  | AT | 172 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-02 | July | 2130 |  | 7236 | 160 |  | 7235 | 101 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 60 | 0 |  |  | AT | 190 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-02 | July | 2230 |  | 7236 | 576 |  | 7235 | 541 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 36 | 0 |  |  | AT | 190 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-03 | July | 2130 |  | 8426 | 162 |  | 8110 | 134 |  |  | -2413 | -2413 | -2413 | Critical Branch | ID schedules | NA | 344 | 0 | [5 empty] | CH | 7750 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
2025-07-04 | July | 1830 |  | 7340 | 458 |  | 7332 | 437 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 29 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 1930 |  | 8353 | 332 |  | 8353 | 244 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 88 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-04 | July | 2030 |  | 7866 | 332 |  | 7950 | 244 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 4 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-05 | July | 1830 |  | 8361 | 781 |  | 8244 | 781 |  |  | -3377 | -3377 | -3377 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 117 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-06 | July | 2130 |  | 8537 | 721 |  | 8508 | 721 |  |  | -6262 | -6262 | -6262 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 29 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
2025-07-06 | July | 2230 |  | 8537 | 721 |  | 8508 | 721 |  |  | -6262 | -6262 | -6262 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 29 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
2025-07-06 | July | 2330 |  | 8306 | 721 |  | 8287 | 721 |  |  | -6146 | -6146 | -6146 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 19 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
2025-07-07 | July | 2130 |  | 6847 | 584 |  | 6834 | 584 |  |  | -3047 | -3047 | -3047 | ID schedules | ID schedules | NA | 13 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-07 | July | 2230 |  | 6744 | 584 |  | 6738 | 566 |  |  | -2997 | -2997 | -2997 | ID schedules | ID schedules | NA | 24 | 0 | [5 empty] | CH | 6237 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-07-10 | July | 2230 |  | 6752 | 793 |  | 6752 | 781 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 12 | 0 | [5 empty] | CH | 5698 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-07-10 | July | 2330 |  | 6314 | 718 |  | 6200 | 718 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 114 | 0
2025-07-12 | July | 1230 |  | 5431 | 620 |  | 3829 | 620 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1602 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-12 | July | 1330 |  | 4888 | 657 |  | 4503 | 657 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 385 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-12 | July | 1430 |  | 5431 | 620 |  | 3917 | 620 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1514 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-12 | July | 1530 |  | 5817 | 284 |  | 4716 | 284 |  |  | -4401 | -4401 | -4401 | Critical Branch | ID schedules | NA | 1101 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-12 | July | 1630 |  | 6352 | 344 |  | 6343 | 344 |  |  | -4702 | -4702 | -4702 | ID schedules | ID schedules | NA | 9 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-13 | July | 1530 |  | 6252 | 1006 |  | 5679 | 980 |  |  | -4687 | -4687 | -4687 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 599 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-13 | July | 1630 |  | 6370 | 996 |  | 5588 | 972 |  |  | -4738 | -4738 | -4738 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 806 | 0 |  |  | AT | -152 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-13 | July | 1730 |  | 6272 | 1006 |  | 6176 | 980 |  |  | -4714 | -4714 | -4714 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 122 | 0 |  |  | AT | 347 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-14 | July | 2330 |  | 5987 | 587 |  | 5987 | 520 |  |  | -5386 | -5386 | -5386 | ID schedules | TTC Validation phase - bilateral reduction | NA | 67 | 0 | [5 empty] | CH | 4958 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-07-16 | July | 1830 |  | 6152 | 600 |  | 6152 | 471 |  |  | -4976 | -4976 | -4976 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 129 | 0 |  |  | AT | 360 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-16 | July | 1930 |  | 6152 | 600 |  | 6152 | 525 |  |  | -4883 | -4883 | -4883 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 75 | 0 |  |  | AT | 360 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-16 | July | 2030 |  | 6152 | 600 |  | 6152 | 462 |  |  | -4858 | -4858 | -4858 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 138 | 0 |  |  | AT | 360 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-16 | July | 2130 |  | 7042 | 735 |  | 6363 | 277 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1137 | 0 |  |  | AT | 373 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-07-16 | July | 2230 |  | 7042 | 735 |  | 6363 | 280 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1134 | 0
2025-07-16 | July | 2330 |  | 6482 | 760 |  | 5695 | -192 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1739 | 0
2025-07-19 | July | 1830 |  | 5921 | 712 |  | 5384 | 712 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 537 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-19 | July | 1930 |  | 5921 | 712 |  | 5384 | 712 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 537 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-19 | July | 2030 |  | 5921 | 712 |  | 5384 | 712 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 537 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-19 | July | 2130 |  | 5396 | 666 |  | 5382 | 666 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 14 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-19 | July | 2230 |  | 5396 | 666 |  | 5382 | 666 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 14 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-19 | July | 2330 |  | 4836 | 691 |  | 4822 | 691 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 14 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-20 | July | 1930 |  | 5655 | 593 |  | 5655 | 589 |  |  | -5313 | -5313 | -5313 | ID schedules | ID schedules | NA | 4 | 0 | [5 empty] | CH | 5260 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-07-20 | July | 2030 |  | 5655 | 593 |  | 5655 | 575 |  |  | -5427 | -5427 | -5427 | ID schedules | ID schedules | NA | 18 | 0 | [5 empty] | CH | 5233 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-07-22 | July | 2130 |  | 6564 | 463 |  | 6564 | 429 |  |  | -5476 | -5476 | -5476 | ID schedules | ID schedules | NA | 34 | 0 | [5 empty] | CH | 5941 | Calculation Failed, reduction based on IDCF prognose
2025-07-24 | July | 1830 |  | 7749 | 653 |  | 7749 | 651 |  |  | -6679 | -6679 | -6679 | ID schedules | ID schedules | NA | 2 | 0 | [5 empty] | CH | 7431 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-2 Pradella-Robbia + Pradella-Sils
2025-07-25 | July | 1530 |  | 7998 | 723 |  | 7635 | 723 |  |  | -433 | -433 | -433 | Critical Branch | ID schedules | NA | 363 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-25 | July | 1630 |  | 8204 | 723 |  | 7844 | 723 |  |  | -498 | -498 | -498 | Critical Branch | ID schedules | NA | 360 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-25 | July | 1730 |  | 8204 | 723 |  | 7844 | 723 |  |  | -498 | -498 | -498 | Critical Branch | ID schedules | NA | 360 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-27 | July | 1230 |  | 2785 | 727 |  | 2751 | 727 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 34 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-27 | July | 1330 |  | 2992 | 727 |  | 2967 | 727 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 25 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-27 | July | 1530 |  | 5864 | 834 |  | 4282 | 880 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1536 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-07-27 | July | 1630 |  | 5793 | 897 |  | 5793 | 892 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 5 | 0 |  |  | AT | -158 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-07-27 | July | 2130 |  | 7982 | 734 |  | 7981 | 734 |  |  | -3196 | -3196 | -3196 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-07-27 | July | 2230 |  | 7982 | 734 |  | 7981 | 734 |  |  | -3196 | -3196 | -3196 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-07-29 | July | 2330 |  | 8298 | 734 |  | 8298 | 714 |  |  | -3816 | -3816 | -3816 | ID schedules | ID schedules | NA | 20 | 0 | [5 empty] | CH | 7795 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 SOAZZA-BULCIAGO
2025-07-31 | July | 1930 |  | 8568 | 672 |  | 8568 | 671 |  |  | -2530 | -2530 | -2530 | ID schedules | ID schedules | NA | 1 | 0 | [5 empty] | CH | 8002 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
2025-08-01 | August | 1830 |  | 8292 | 665 |  | 8045 | 665 |  |  | 818 | 247 | 818 | Minimum Margin | ID schedules | NA | 247 | 247 | [8 empty] | FR | 3633 | Bilateral - Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-01 | August | 1930 |  | 8292 | 665 |  | 8045 | 665 |  |  | 944 | 247 | 944 | Minimum Margin | ID schedules | NA | 247 | 247 | [8 empty] | FR | 3468 | Bilateral - Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-01 | August | 2030 |  | 8287 | 686 |  | 7975 | 686 |  |  | 943 | 247 | 943 | Minimum Margin | ID schedules | NA | 312 | 247 | [8 empty] | FR | 3439 | Bilateral - Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-01 | August | 2130 |  | 8279 | 680 |  | 7905 | 680 |  |  | -976 | -976 | -976 | Critical Branch | ID schedules | NA | 374 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-01 | August | 2230 |  | 8274 | 680 |  | 7998 | 680 |  |  | -968 | -968 | -968 | Critical Branch | ID schedules | NA | 276 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-01 | August | 2330 |  | 7654 | 705 |  | 7464 | 705 |  |  | -317 | -317 | -317 | Critical Branch | ID schedules | NA | 190 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-02 | August | 1230 |  | 3980 | 603 |  | 2648 | 603 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1332 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-02 | August | 1330 |  | 3352 | 651 |  | 3280 | 651 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 72 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-02 | August | 1430 |  | 3980 | 603 |  | 3149 | 603 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 831 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-02 | August | 1830 |  | 7902 | 681 |  | 7619 | 681 |  |  | -4168 | -4168 | -4168 | ID schedules | TTC Validation phase - bilateral reduction | NA | 283 | 0 |  |  | AT | 319 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-02 | August | 1930 |  | 7902 | 681 |  | 7865 | 681 |  |  | -4168 | -4168 | -4168 | ID schedules | TTC Validation phase - bilateral reduction | NA | 37 | 0 |  |  | AT | 319 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-02 | August | 2030 |  | 7902 | 681 |  | 7865 | 681 |  |  | -4168 | -4168 | -4168 | ID schedules | TTC Validation phase - bilateral reduction | NA | 37 | 0 |  |  | AT | 319 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-02 | August | 2330 |  | 7674 | 703 |  | 7646 | 703 |  |  | -4605 | -4605 | -4605 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 28 | 0 |  |  | AT | 405 | Because of high redispatch the leftover intraday capacity was set to 0
2025-08-03 | August | 1330 |  | 1113 | 530 |  | 312 | 530 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 801 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 1430 |  | 1113 | 530 |  | 284 | 530 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 829 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 1530 |  | 2192 | 723 |  | 649 | 686 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1580 | 0 |  |  | AT | 157 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 1830 |  | 6917 | 1004 |  | 5362 | 981 |  |  | -3967 | -3967 | -3967 | ID schedules | ID schedules | NA | 1578 | 0 |  |  | AT | -155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 1930 |  | 7332 | 1004 |  | 6862 | 981 |  |  | -4095 | -4095 | -4095 | ID schedules | TTC Validation phase - bilateral reduction | NA | 493 | 0 |  |  | AT | -155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-03 | August | 2030 |  | 7201 | 962 |  | 6930 | 942 |  |  | -4021 | -4021 | -4021 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 291 | 0 |  |  | AT | 415 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-04 | August | 1730 |  | 5726 | 130 |  | 5726 | 129 |  |  | -2959 | -2959 | -2959 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-05 | August | 1730 |  | 5388 | 153 |  | 5388 | -299 |  |  | -1929 | -1929 | -1929 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 452 | 0 |  |  | AT | 347 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 2130 |  | 5919 | 172 |  | 4807 | 172 |  |  | -135 | -135 | -135 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1112 | 0 |  |  | AT | -33 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 2230 |  | 5919 | 172 |  | 4868 | 172 |  |  | -135 | -135 | -135 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1051 | 0 |  |  | AT | -33 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-09 | August | 2330 |  | 5300 | 181 |  | 4733 | 180 |  |  | 443 | 4 | 443 | Minimum Margin | ID schedules | NA | 568 | 4 |  |  | AT | 241 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1530 |  | 4593 | 194 |  | 3626 | 194 |  |  | -987 | -987 | -987 | ID schedules | TTC Validation phase - bilateral reduction | NA | 967 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1630 |  | 4593 | 194 |  | 3626 | 194 |  |  | -987 | -987 | -987 | ID schedules | TTC Validation phase - bilateral reduction | NA | 967 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1730 |  | 4402 | 169 |  | 4098 | 168 |  |  | -970 | -970 | -970 | Critical Branch | ID schedules | NA | 305 | 0 |  |  | AT | 338 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1830 |  | 5336 | 194 |  | 4314 | 194 |  |  | -537 | -537 | -537 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1022 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 1930 |  | 5336 | 194 |  | 4286 | 194 |  |  | -537 | -537 | -537 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1050 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 2030 |  | 5325 | 194 |  | 4141 | 194 |  |  | -542 | -542 | -542 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1184 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 2130 |  | 5531 | 194 |  | 4241 | 194 |  |  | -615 | -615 | -615 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1290 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 2230 |  | 5540 | 194 |  | 4376 | 194 |  |  | -613 | -613 | -613 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1164 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-10 | August | 2330 |  | 5540 | 194 |  | 4386 | 194 |  |  | -613 | -613 | -613 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1154 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-11 | August | 1930 |  | 4755 | 172 |  | 4308 | 172 |  |  | -3252 | -3252 | -3252 | ID schedules | ID schedules | NA | 447 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 3481 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-08-13 | August | 1530 |  | 5801 | 0 |  | 3864 | 0 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 1937 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-13 | August | 1630 |  | 5566 | 160 |  | 5174 | 196 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 356 | 0
2025-08-13 | August | 1830 |  | 4464 | 576 |  | 4258 | 456 |  |  | -626 | -626 | -626 | Critical Branch | ID schedules | NA | 326 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-13 | August | 1930 |  | 4520 | 576 |  | 2822 | 574 |  |  | -680 | -680 | -680 | Critical Branch | ID schedules | NA | 1700 | 0 | [5 empty] | CH | 2484 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-08-13 | August | 2030 |  | 4520 | 576 |  | 2543 | 574 |  |  | -680 | -680 | -680 | Critical Branch | ID schedules | NA | 1979 | 0 | [5 empty] | CH | 1613 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-08-14 | August | 1330 |  | 3219 | 170 |  | 3136 | 170 |  |  | -5772 | -5772 | -5772 | ID schedules | ID schedules | NA | 83 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-14 | August | 1530 |  | 3453 | 48 |  | 3382 | 48 |  |  | -1654 | -1654 | -1654 | Critical Branch | ID schedules | NA | 71 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-14 | August | 1830 |  | 3955 | 634 |  | 3955 | 590 |  |  | -3343 | -3343 | -3343 | ID schedules | ID schedules | NA | 44 | 0 | [5 empty] | CH | 3382 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
2025-08-14 | August | 1930 |  | 3902 | 705 |  | 3902 | 677 |  |  | -3112 | -3112 | -3112 | ID schedules | ID schedules | NA | 28 | 0
2025-08-14 | August | 2030 |  | 2981 | 705 |  | 2981 | 677 |  |  | -2573 | -2573 | -2573 | ID schedules | ID schedules | NA | 28 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-14 | August | 2130 |  | 3020 | 667 |  | 3023 | 657 |  |  | 105 | 105 | 105 | Adjustment reached | ID schedules | NA | 7 | 105 | [5 empty] | CH | 2708 | Reduction due to missing redispatch potential | [6 empty] | IT | -10000 | ATC blocked
2025-08-14 | August | 2330 |  | 3706 | 645 |  | 3682 | 374 |  |  | -283 | -283 | -283 | ID schedules | ID schedules | NA | 295 | 0
2025-08-15 | August | 1530 |  | 4571 | 623 |  | 3059 | 623 |  |  | -1480 | -1480 | -1480 | Critical Branch | ID schedules | NA | 1512 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 1630 |  | 4556 | 623 |  | 2991 | 623 |  |  | -1388 | -1388 | -1388 | Critical Branch | ID schedules | NA | 1565 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 1730 |  | 4569 | 623 |  | 3158 | 623 |  |  | -1481 | -1481 | -1481 | Critical Branch | ID schedules | NA | 1411 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 1830 |  | 5286 | 676 |  | 3610 | 676 |  |  | -1090 | -1090 | -1090 | Critical Branch | ID schedules | NA | 1676 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 1930 |  | 5287 | 676 |  | 3460 | 676 |  |  | -1089 | -1089 | -1089 | Critical Branch | ID schedules | NA | 1827 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 2030 |  | 5286 | 676 |  | 3418 | 676 |  |  | -1090 | -1090 | -1090 | Critical Branch | ID schedules | NA | 1868 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 2130 |  | 5497 | 179 |  | 2870 | 179 |  |  | 998 | 347 | 998 | Minimum Margin | ID schedules | NA | 2627 | 347 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 2230 |  | 5544 | 195 |  | 3422 | 195 |  |  | 1000 | 347 | 1000 | Minimum Margin | ID schedules | NA | 2122 | 347 | [14 empty] | IT | -10000 | ATC blocked
2025-08-15 | August | 2330 |  | 5544 | 195 |  | 3427 | 195 |  |  | 995 | 347 | 995 | Minimum Margin | ID schedules | NA | 2117 | 347 | [14 empty] | IT | -10000 | ATC blocked
2025-08-16 | August | 1230 |  | 3292 | 979 |  | 1922 | 979 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1370 | 0
2025-08-16 | August | 1330 |  | 3292 | 979 |  | 2093 | 979 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1199 | 0
2025-08-16 | August | 1430 |  | 3292 | 979 |  | 2646 | 979 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 646 | 0
2025-08-16 | August | 1530 |  | 6200 | 964 |  | 5201 | 940 |  |  | 741 | 366 | 741 | Minimum Margin | ID schedules | NA | 1023 | 366 |  |  | AT | 140 | Reduction because NTC over thermal limit on border |  |  |  | FR | 1778 | Bilateral - Process fail during TSO validation phase
2025-08-16 | August | 1630 |  | 6209 | 964 |  | 6123 | 940 |  |  | 738 | 366 | 738 | Minimum Margin | ID schedules | NA | 110 | 366 |  |  | AT | 186 | Reduction because NTC over thermal limit on border |  |  |  | FR | 1778 | Bilateral - Process fail during TSO validation phase
2025-08-16 | August | 1730 |  | 6209 | 964 |  | 6130 | 940 |  |  | 737 | 366 | 737 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 103 | 366 |  |  | AT | 188 | Reduction because NTC over thermal limit on border |  |  |  | FR | 1778 | Bilateral - Process fail during TSO validation phase
2025-08-16 | August | 1830 |  | 5593 | 704 |  | 5566 | 698 |  |  | 169 | 169 | 169 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 33 | 169 | [5 empty] | CH | 5285 | Reduction due to missing redispatch potential
2025-08-16 | August | 1930 |  | 5593 | 704 |  | 5566 | 698 |  |  | 169 | 169 | 169 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 33 | 169 | [5 empty] | CH | 5285 | Reduction due to missing redispatch potential
2025-08-16 | August | 2030 |  | 5593 | 704 |  | 5566 | 698 |  |  | 169 | 169 | 169 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 33 | 169 | [5 empty] | CH | 5285 | Reduction due to missing redispatch potential
2025-08-16 | August | 2130 |  | 6296 | 696 |  | 6283 | 696 |  |  | 371 | 345 | 371 | Minimum Margin | Min import NTC Threshold | NA | 13 | 345
2025-08-16 | August | 2230 |  | 6300 | 696 |  | 6283 | 696 |  |  | 371 | 345 | 371 | Minimum Margin | Min import NTC Threshold | NA | 17 | 345
2025-08-16 | August | 2330 |  | 5745 | 720 |  | 5703 | 720 |  |  | 965 | 345 | 965 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 42 | 345
2025-08-17 | August | 1230 |  | 5980 | 2984 |  | 1519 | 2984 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 4461 | 0 |  |  | AT | 404 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-17 | August | 1330 |  | 5980 | 2984 |  | 1519 | 2984 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 4461 | 0 |  |  | AT | 404 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-17 | August | 1430 |  | 5980 | 2984 |  | 1783 | 2984 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 4197 | 0 |  |  | AT | 404 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-17 | August | 1530 |  | 4827 | 880 |  | 3540 | 879 |  |  | -1915 | -1915 | -1915 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1288 | 0 |  |  | AT | 135 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-17 | August | 1630 |  | 5117 | 1031 |  | 4992 | 1012 |  |  | -1651 | -1651 | -1651 | ID schedules | TTC Validation phase - bilateral reduction | NA | 144 | 0 |  |  | AT | 95 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 1730 |  | 5117 | 998 |  | 5117 | 978 |  |  | -1639 | -1639 | -1639 | ID schedules | ID schedules | NA | 20 | 0 |  |  | AT | 88 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 1830 |  | 5613 | 1036 |  | 5557 | 1004 |  |  | 1363 | 247 | 1363 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 88 | 247 |  |  | AT | 135 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 1930 |  | 5613 | 1038 |  | 5557 | 1005 |  |  | 1363 | 247 | 1363 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 89 | 247 |  |  | AT | 135 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 2030 |  | 5613 | 1036 |  | 5557 | 1004 |  |  | 1363 | 247 | 1363 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 88 | 247 |  |  | AT | 135 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 2130 |  | 6004 | 1051 |  | 5930 | 1016 |  |  | 394 | 394 | 394 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 109 | 394 |  |  | AT | 168 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 2230 |  | 6004 | 1013 |  | 5930 | 985 |  |  | 394 | 394 | 394 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 102 | 394 |  |  | AT | 167 | Reduction because NTC over thermal limit on border
2025-08-17 | August | 2330 |  | 6004 | 1013 |  | 5930 | 985 |  |  | 394 | 394 | 394 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 102 | 394 |  |  | AT | 167 | Reduction because NTC over thermal limit on border
2025-08-18 | August | 1530 |  | 5442 | 133 |  | 5168 | 30 |  |  | 739 | 154 | 739 | Minimum Margin | ID schedules | NA | 377 | 154 |  |  | AT | 215 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-18 | August | 1730 |  | 5413 | 133 |  | 5481 | -53 |  |  | 708 | 154 | 708 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 118 | 154 |  |  | AT | 268 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-18 | August | 2230 |  | 6114 | 796 |  | 5986 | 796 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 128 | 0 | [8 empty] | FR | 2200 | Bilateral - Planned outage of Albertville-Rondissone 1&2 and limitation on PISA 1
2025-08-18 | August | 2330 |  | 5564 | 841 |  | 5542 | 847 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 16 | 0 | [8 empty] | FR | 2200 | Bilateral - Planned outage of Albertville-Rondissone 1&2 and limitation on PISA 1
2025-08-19 | August | 1830 |  | 5298 | 631 |  | 5298 | 629 |  |  | 3506 | -52 | 3506 | ID schedules | TTC Validation phase - bilateral reduction | NA | 2 | -52
2025-08-20 | August | 1830 |  | 6377 | 522 |  | 6377 | 464 |  |  | -5097 | -5097 | -5097 | ID schedules | TTC Validation phase - bilateral reduction | NA | 58 | 0 | [5 empty] | CH | 5512 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | [6 empty] | IT | -10000 | ATC blocked
2025-08-23 | August | 2030 |  | 7050 | 651 |  | 6491 | 651 |  |  | -4409 | -4409 | -4409 | ID schedules | ID schedules | NA | 559 | 0 |  |  | AT | -34 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 1830 |  | 6089 | 722 |  | 5417 | 722 |  |  | -3858 | -3858 | -3858 | Critical Branch | ID schedules | NA | 672 | 0 |  |  | AT | 153 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 1930 |  | 6283 | 724 |  | 5389 | 725 |  |  | -3950 | -3950 | -3950 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 893 | 0 |  |  | AT | -70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 2030 |  | 6283 | 724 |  | 5092 | 725 |  |  | -3950 | -3950 | -3950 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1190 | 0 |  |  | AT | -70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 2130 |  | 6606 | 847 |  | 5125 | 836 |  |  | -5274 | -5274 | -5274 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1492 | 0 |  |  | AT | -70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 2230 |  | 6606 | 847 |  | 5634 | 836 |  |  | -5274 | -5274 | -5274 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 983 | 0 |  |  | AT | -70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-25 | August | 2330 |  | 5822 | 872 |  | 5185 | 861 |  |  | -4564 | -4564 | -4564 | Critical Branch | ID schedules | NA | 648 | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-26 | August | 1830 |  | 5743 | 666 |  | 5743 | 665 |  |  | -3807 | -3807 | -3807 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1 | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-27 | August | 1930 |  | 5927 | 576 |  | 5927 | 575 |  |  | -3789 | -3789 | -3789 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0 |  |  | AT | -53 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5407 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked
2025-08-27 | August | 2030 |  | 5943 | 576 |  | 5943 | 575 |  |  | -3808 | -3808 | -3808 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0 |  |  | AT | -53 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1830 |  | 5761 | 724 |  | 5571 | 726 |  |  | -4702 | -4702 | -4702 | Critical Branch | ID schedules | NA | 188 | 0 |  |  | AT | -17 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 1930 |  | 5779 | 727 |  | 5331 | 727 |  |  | -4713 | -4713 | -4713 | ID schedules | TTC Validation phase - bilateral reduction | NA | 448 | 0 |  |  | AT | -123 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-28 | August | 2030 |  | 5760 | 727 |  | 5381 | 727 |  |  | -4700 | -4700 | -4700 | ID schedules | TTC Validation phase - bilateral reduction | NA | 379 | 0 |  |  | AT | -123 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1830 |  | 6061 | 689 |  | 5328 | 255 |  |  | -5319 | -5319 | -5319 | Critical Branch | ID schedules | NA | 1167 | 0 |  |  | AT | 318 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 1930 |  | 6141 | 713 |  | 5351 | 732 |  |  | -5360 | -5360 | -5360 | Critical Branch | ID schedules | NA | 771 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-29 | August | 2030 |  | 6095 | 689 |  | 5357 | 255 |  |  | -5339 | -5339 | -5339 | Critical Branch | ID schedules | NA | 1172 | 0 |  |  | AT | 318 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 1230 |  | 5932 | 166 |  | 5866 | 166 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 66 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 1330 |  | 5845 | 166 |  | 5578 | 166 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 267 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 1430 |  | 5520 | 157 |  | 5009 | -245 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 913 | 0 |  |  | AT | 271 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 1530 |  | 6568 | 741 |  | 6391 | 512 |  |  | 1091 | 177 | 1091 | Minimum Margin | ID schedules | NA | 406 | 177 |  |  | AT | 103 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2973 | Bilateral - Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-30 | August | 1630 |  | 5973 | 780 |  | 5796 | 787 |  |  | 1766 | 177 | 1766 | Minimum Margin | ID schedules | NA | 170 | 177 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2346 | Bilateral - Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-30 | August | 1730 |  | 6381 | 780 |  | 6204 | 787 |  |  | 1526 | 177 | 1526 | Minimum Margin | ID schedules | NA | 170 | 177 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | FR | 2552 | Bilateral - Process fail during TSO validation phase |  |  |  | IT | -10000 | ATC blocked
2025-08-30 | August | 1830 |  | 6915 | 557 |  | 5644 | 553 |  |  | -5608 | -5608 | -5608 | Critical Branch | ID schedules | NA | 1275 | 0 |  |  | AT | 305 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 6618 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 1930 |  | 6915 | 557 |  | 5616 | 519 |  |  | -5608 | -5608 | -5608 | Critical Branch | ID schedules | NA | 1337 | 0 |  |  | AT | 305 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 6193 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-30 | August | 2030 |  | 6915 | 557 |  | 4871 | 557 |  |  | -5608 | -5608 | -5608 | Critical Branch | ID schedules | NA | 2044 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1230 |  | 5076 | 2993 |  | 1399 | 2993 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 3677 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1330 |  | 5076 | 2993 |  | 1399 | 2993 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 3677 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1430 |  | 5076 | 2993 |  | 1399 | 2993 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 3677 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1530 |  | 4677 | 805 |  | 2359 | 817 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 2306 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1630 |  | 4313 | 865 |  | 4245 | 865 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 68 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1830 |  | 6205 | 811 |  | 5709 | 381 |  |  | -3973 | -3973 | -3973 | Critical Branch | ID schedules | NA | 926 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 1930 |  | 6252 | 822 |  | 5734 | 826 |  |  | -3990 | -3990 | -3990 | Critical Branch | ID schedules | NA | 514 | 0 | [5 empty] | CH | 6016 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-08-31 | August | 2030 |  | 6252 | 822 |  | 5457 | 809 |  |  | -3990 | -3990 | -3990 | Critical Branch | ID schedules | NA | 808 | 0 | [5 empty] | CH | 5845 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | [6 empty] | IT | -10000 | ATC blocked

## ID FLAGS processing
TSO | Long description | Type | # of TS
AT | Because of high redispatch the leftover intraday capacity was set to 0 | Redispatch | 233
AT | Reduction because NTC over thermal limit on border | NTC over thermal limit | 91
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 34
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | Overload | 3
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 6
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE | Missing CNEC in CC | 5
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 1
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | Redispatch | 4
CH | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | Overload | 4
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 1
CH | Reduction due to missing redispatch potential | Overload | 13
CH | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | Overload | 28
CH | Calculation Failed, reduction based on IDCF prognose | Missing CNEC in CC | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-2 Pradella-Robbia + Pradella-Sils | Outage | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 SOAZZA-BULCIAGO | Overload | 1
FR | N-2 Albertville-Grande Ile / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR] | Overload | 3
FR | Bilateral - Test GRANDE ILE PIOSSASCO 1 | Overload | 3
FR | Bilateral - Planned outage G.ILE-PIOSSASCO 1&2 | Outage | 5
FR | Process fail during TSO validation phase | Process Fail | 12
FR | Bilateral - Outage HVDC GRANDE ILE - PIOSSASCO 1 and 2 | Outage | 9
FR | Bilateral - Outage - N-2 Albertville-Rondissone | Outage | 6
FR | Bilateral - Outage - Planned outage G.ILE PIOSSASCO 1 and 2 | Outage | 26
FR | Bilateral - Outage - RDCR FIL 1 & 2 | Outage | 2
FR | Bilateral - Outage - GRANDE ILE - PIOSSASCO 1 and 2 | Outage | 20
FR | Bilateral - Outage - Outage G.ILE PIOSSASCO 1 and 2 | Outage | 3
FR | Bilateral - Outage - HVDC GRANDE ILE - PIOSSASCO 1 and 2 | Outage | 5
FR | Bilateral - N-2 Albertville-Rondissone / [FR-FR] ALBERTVILLE-GRANDE ILE 3 [OPP] [FR] | Overload | 1
FR | Bilateral - Outage - Retrait HVDC | Outage | 7
FR | Bilateral - Outage - Retrait HVDC G.ILE-PIOSSASCO 1&2 | Outage | 3
FR | Bilateral - Outage - Outage - Retrait Barre 2.1 GENISSIAT | Outage | 3
FR | Bilateral - Unplanned outage MERY VIELMOULIN 1 | Outage | 5
FR | Bilateral - Planned Outage CHAFFARD GRANDE ILE 2 | Outage | 3
FR | Bilateral - Outage GRANDE ILE - PIOSSASCO 1&2 | Outage | 3
FR | Bilateral - Outage - HVDC FIL 1 & 2 | Outage | 5
FR | Bilateral - Outage - GENISSIAT S1.2 | Outage | 2
FR | Bilateral - N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | Overload | 3
FR | Bilateral - N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] SOAZZA-BULCIAGO [DIR] [CH] | Overload | 1
FR | Bilateral - N-2 Albertville-Rondissone / [CH-IT] RIDDES-AVISE [DIR][IT] | Overload | 7
FR | Bilateral - N-2 Albertville-Rondissone / [CH-IT] ROBBIA-FIORANO [DIR] [CH] | Overload | 1
FR | Bilateral - Process fail during TSO validation phase | Process Fail | 9
FR | Bilateral - Planned outage of Albertville-Rondissone 1&2 and limitation on PISA 1 | Outage | 2
IT | ATC blocked | ATC Blocked | 369
Smoothing ramp | Smoothing ramp | Smoothing | 4