## DA Results (hidden)
DA results
|  |  | TTC Adjustment |  |  | TTC Validated |  |  | ANTC |  |  | LimitedBy | [8 empty] | AT | AT | AT | AT | AT | AT | CH | CH | CH | CH | CH | CH | FR | FR | FR | FR | FR | FR | IT | IT | IT | IT | IT | IT | SI | SI | SI | SI | SI | SI
Business day | Month | Timestamp | TTC_Full_Import | TTCImport | TTCExport | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | 70% red | TTCRed_Import | TTCRed_Transit_Import | TTCRed_Transit_Export | TTCRed_Transit | TTC and 70% red | FLAG | Bilateral | MNII | Reason | Bilateral - Export | MNIE | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason
20251001 | October | 0030 | 10650 |  |  | 8758 |  |  | -3112 | -3112 | -1243 | Critical Branch | Validation phase | 0 | 1892 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8638; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0130 | 10650 |  |  | 8758 |  |  | -3112 | -3112 | -1243 | Critical Branch | Validation phase | 0 | 1892 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8638; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0230 | 10650 |  |  | 8758 |  |  | -3112 | -3112 | -1243 | Critical Branch | Validation phase | 0 | 1892 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8638; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0330 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 0 | 1460 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8603; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0430 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 0 | 1460 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8603; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0530 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 0 | 1460 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8603; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0630 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 0 | 1460 | NA | NA | NA | 0 | 1 | AT: 375; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 8603; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0730 |  | 9107 | 817 |  | 8201 | 763 | -5953 | -5953 | 0 | Critical Branch | Validation phase | 0 | NA | 906 | 54 | 960 | 5953 | 1 | AT: 248; AT: 130; CH: 9220; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0830 |  | 7907 | 817 |  | 7054 | 762 | -4985 | -4985 | 0 | Critical Branch | Validation phase | 0 | NA | 853 | 55 | 908 | 4985 | 1 | AT: 246; AT: 129; CH: 8020; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0930 |  | 7716 | 701 |  | 7454 | 701 | -4583 | -4583 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 262 | 0 | 262 | 4583 | 1 | AT: 359; AT: 135; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1030 |  | 7716 | 701 |  | 7454 | 701 | -4583 | -4583 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 262 | 0 | 262 | 4583 | 1 | AT: 359; AT: 135; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1130 |  | 7716 | 701 |  | 7454 | 701 | -4583 | -4583 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 262 | 0 | 262 | 4583 | 1 | AT: 359; AT: 135; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1230 |  | 8645 | 779 |  | 7879 | 779 | 550 | 450 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 100 | NA | 766 | 0 | 766 | -450 | 1 | AT: 390; AT: Reduction because NTC over thermal limit on border; AT: 133; AT: Reduction because NTC over thermal limit on border; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1330 |  | 8645 | 779 |  | 7879 | 779 | 550 | 450 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 100 | NA | 766 | 0 | 766 | -450 | 1 | AT: 390; AT: Reduction because NTC over thermal limit on border; AT: 133; AT: Reduction because NTC over thermal limit on border; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1430 |  | 8645 | 779 |  | 7879 | 779 | 550 | 450 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 100 | NA | 766 | 0 | 766 | -450 | 1 | AT: 390; AT: Reduction because NTC over thermal limit on border; AT: 133; AT: Reduction because NTC over thermal limit on border; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1530 |  | 8642 | 740 |  | 7588 | 688 | -3912 | -3912 | 0 | Critical Branch | Validation phase | 0 | NA | 1054 | 52 | 1106 | 3912 | 1 | AT: 390; AT: Reduction because NTC over thermal limit on border; AT: 133; AT: Reduction because NTC over thermal limit on border; CH: 8357; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1630 |  | 8843 | 740 |  | 7782 | 688 | -4153 | -4153 | 0 | Critical Branch | Validation phase | 0 | NA | 1061 | 52 | 1113 | 4153 | 1 | AT: 390; AT: Reduction because NTC over thermal limit on border; AT: 133; AT: Reduction because NTC over thermal limit on border; CH: 8558; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1730 |  | 8843 | 740 |  | 7782 | 688 | -4153 | -4153 | 0 | Critical Branch | Validation phase | 0 | NA | 1061 | 52 | 1113 | 4153 | 1 | AT: 390; AT: Reduction because NTC over thermal limit on border; AT: 133; AT: Reduction because NTC over thermal limit on border; CH: 8558; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1830 |  | 7232 | 732 |  | 7112 | 729 | -2967 | -2967 | 0 | Critical Branch | Validation phase | 0 | NA | 120 | 3 | 123 | 2967 | 1 | AT: 253; AT: 116; CH: 7627; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1930 |  | 7232 | 732 |  | 7112 | 729 | -2967 | -2967 | 0 | Critical Branch | Validation phase | 0 | NA | 120 | 3 | 123 | 2967 | 1 | AT: 253; AT: 116; CH: 7627; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2030 |  | 7232 | 732 |  | 7112 | 729 | -2967 | -2967 | 0 | Critical Branch | Validation phase | 0 | NA | 120 | 3 | 123 | 2967 | 1 | AT: 253; AT: 116; CH: 7627; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2130 |  | 8169 | 700 |  | 7662 | 682 | -3536 | -3536 | 0 | Critical Branch | Validation phase | 0 | NA | 507 | 18 | 525 | 3536 | 1 | AT: 369; AT: 135; CH: 8212; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2230 |  | 8169 | 700 |  | 7662 | 682 | -3536 | -3536 | 0 | Critical Branch | Validation phase | 0 | NA | 507 | 18 | 525 | 3536 | 1 | AT: 369; AT: 135; CH: 8212; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2330 |  | 7615 | 720 |  | 7326 | 707 | -2964 | -2964 | 0 | Critical Branch | Validation phase | 0 | NA | 289 | 13 | 302 | 2964 | 1 | AT: 352; AT: 149; CH: 7607; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3600; FR: Outage - Bus bar 2.1 GENISSIAT
20251002 | October | 0030 | 8392 |  |  | 7382 |  |  | -1595 | -1595 | -585 | Critical Branch | Validation phase | 0 | 1010 | NA | NA | NA | 0 | 1 | CH: 7052; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0130 | 8392 |  |  | 7382 |  |  | -1595 | -1595 | -585 | Critical Branch | Validation phase | 0 | 1010 | NA | NA | NA | 0 | 1 | CH: 7052; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0230 | 8392 |  |  | 7382 |  |  | -1595 | -1595 | -585 | Critical Branch | Validation phase | 0 | 1010 | NA | NA | NA | 0 | 1 | CH: 7052; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0330 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 0 | 1172 | NA | NA | NA | 0 | 1 | CH: 6917; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0430 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 0 | 1172 | NA | NA | NA | 0 | 1 | CH: 6917; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0530 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 0 | 1172 | NA | NA | NA | 0 | 1 | CH: 6917; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0630 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 0 | 1172 | NA | NA | NA | 0 | 1 | CH: 6917; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0730 |  | 7687 | 629 |  | 7631 | 624 | -3645 | -3645 | 0 | Critical Branch | Validation phase | 0 | NA | 56 | 5 | 61 | 3645 | 1 | CH: 7709; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0830 |  | 7687 | 629 |  | 7631 | 624 | -3645 | -3645 | 0 | Critical Branch | Validation phase | 0 | NA | 56 | 5 | 61 | 3645 | 1 | CH: 7709; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0930 | 7719 |  |  | 7719 |  |  | -4548 | -4548 | -4548 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251002 | October | 1030 | 7719 |  |  | 7719 |  |  | -4548 | -4548 | -4548 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251002 | October | 1130 | 7719 |  |  | 7544 |  |  | -4548 | -4548 | -4372 | Critical Branch | Smoothing ramp | 0 | 175 | NA | NA | NA | 0 | 1
20251002 | October | 1230 | 8306 |  |  | 6044 |  |  | -2102 | -2102 | 160 | Critical Branch | Validation phase | 0 | 2262 | NA | NA | NA | 2422 | 1 | CH: 5709; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1330 | 8306 |  |  | 6044 |  |  | -2102 | -2102 | 160 | Critical Branch | Validation phase | 0 | 2262 | NA | NA | NA | 2422 | 1 | CH: 5709; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1430 | 8306 |  |  | 6044 |  |  | -2102 | -2102 | 160 | Critical Branch | Validation phase | 0 | 2262 | NA | NA | NA | 2422 | 1 | CH: 5709; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1530 | 7651 |  |  | 6541 |  |  | -4184 | -4184 | -3074 | Critical Branch | Validation phase | 0 | 1110 | NA | NA | NA | 0 | 1 | CH: 6206; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1630 | 8511 |  |  | 7401 |  |  | -5077 | -5077 | -3967 | Critical Branch | Validation phase | 0 | 1110 | NA | NA | NA | 0 | 1 | CH: 7066; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1730 | 8511 |  |  | 7401 |  |  | -5077 | -5077 | -3967 | Critical Branch | Validation phase | 0 | 1110 | NA | NA | NA | 0 | 1 | CH: 7066; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1830 | 8016 |  |  | 7089 |  |  | 735 | 0 | 1662 | Critical Branch | Validation phase | 735 | 927 | NA | NA | NA | 3324 | 1 | CH: 6754; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 1930 | 8016 |  |  | 7089 |  |  | 735 | 0 | 1662 | Critical Branch | Validation phase | 735 | 927 | NA | NA | NA | 3324 | 1 | CH: 6754; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2030 | 8016 |  |  | 7089 |  |  | 735 | 0 | 1662 | Critical Branch | Validation phase | 735 | 927 | NA | NA | NA | 3324 | 1 | CH: 6754; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2130 | 8985 |  |  | 7791 |  |  | -2573 | -2573 | -1379 | Critical Branch | Validation phase | 0 | 1194 | NA | NA | NA | 0 | 1 | CH: 7456; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2230 | 8985 |  |  | 7791 |  |  | -2573 | -2573 | -1379 | Critical Branch | Validation phase | 0 | 1194 | NA | NA | NA | 0 | 1 | CH: 7456; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2330 | 8375 |  |  | 7181 |  |  | -1949 | -1949 | -755 | Critical Branch | Validation phase | 0 | 1194 | NA | NA | NA | 0 | 1 | CH: 6851; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251003 | October | 0030 | 9044 |  |  | 8293 |  |  | -2397 | -2397 | -1646 | Critical Branch | Validation phase | 0 | 751 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7963; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0130 | 9044 |  |  | 8293 |  |  | -2397 | -2397 | -1646 | Critical Branch | Validation phase | 0 | 751 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7963; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0230 | 9044 |  |  | 8293 |  |  | -2397 | -2397 | -1646 | Critical Branch | Validation phase | 0 | 751 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7963; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0330 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 0 | 701 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 7860; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0430 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 0 | 701 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 7860; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0530 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 0 | 701 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 7860; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0630 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 0 | 701 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 7860; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0730 | 9415 |  |  | 8844 |  |  | -2644 | -2644 | -2073 | Critical Branch | Validation phase | 0 | 571 | NA | NA | NA | 0 | 1 | AT: 444; AT: 155; CH: 8509; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0830 | 9415 |  |  | 8844 |  |  | -2644 | -2644 | -2073 | Critical Branch | Validation phase | 0 | 571 | NA | NA | NA | 0 | 1 | AT: 444; AT: 155; CH: 8509; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0930 | 8600 |  |  | 8599 |  |  | -2137 | -2137 | -2136 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155
20251003 | October | 1030 | 8600 |  |  | 8599 |  |  | -2137 | -2137 | -2136 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155
20251003 | October | 1130 | 8600 |  |  | 8599 |  |  | -2137 | -2137 | -2136 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155
20251003 | October | 1230 |  | 8604 | 835 |  | 8402 | 835 | -1443 | -1443 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 202 | 0 | 202 | 1443 | 1 | AT: 442; AT: 150; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1330 |  | 8604 | 835 |  | 8402 | 835 | -1443 | -1443 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 202 | 0 | 202 | 1443 | 1 | AT: 442; AT: 150; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1430 |  | 8604 | 835 |  | 8402 | 835 | -1443 | -1443 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 202 | 0 | 202 | 1443 | 1 | AT: 442; AT: 150; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1530 | 9182 |  |  | 9077 |  |  | -2694 | -2694 | -2596 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1630 | 9182 |  |  | 9077 |  |  | -2694 | -2694 | -2596 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1730 | 9182 |  |  | 9077 |  |  | -2694 | -2694 | -2596 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1830 |  | 7244 | 574 |  | 7244 | 574 | 2826 | 0 | 0 | Critical Branch | Critical Branch | 2826 | NA | 0 | 0 | 0 | 0 | 1 | AT: 382; AT: 155
20251003 | October | 1930 |  | 7244 | 574 |  | 7244 | 574 | 2826 | 0 | 0 | Critical Branch | Critical Branch | 2826 | NA | 0 | 0 | 0 | 0 | 1 | AT: 382; AT: 155
20251003 | October | 2030 |  | 7244 | 574 |  | 7244 | 574 | 2826 | 0 | 0 | Critical Branch | Critical Branch | 2826 | NA | 0 | 0 | 0 | 0 | 1 | AT: 382; AT: 155
20251003 | October | 2130 | 9726 |  |  | 9080 |  |  | 4926 | 208 | 5475 | Minimum Margin | Validation phase | 4718 | 646 | NA | NA | NA | 10742 | 1 | AT: 445; AT: 155; CH: 8851; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 2230 | 9708 |  |  | 9080 |  |  | 4926 | 190 | 5475 | Minimum Margin | Validation phase | 4736 | 628 | NA | NA | NA | 10760 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 8851; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251003 | October | 2330 | 9064 |  |  | 8576 |  |  | 5068 | 156 | 5400 | Minimum Margin | Validation phase | 4912 | 488 | NA | NA | NA | 10644 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8246; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Retrait Barre Genissiat 400kV
20251004 | October | 0030 | 9051 |  |  | 8673 |  |  | -2440 | -2440 | -2063 | Critical Branch | Validation phase | 0 | 378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8346; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0130 | 9051 |  |  | 8673 |  |  | -2440 | -2440 | -2063 | Critical Branch | Validation phase | 0 | 378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8346; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0230 | 9051 |  |  | 8673 |  |  | -2440 | -2440 | -2063 | Critical Branch | Validation phase | 0 | 378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8346; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0330 | 8896 |  |  | 8731 |  |  | -2356 | -2356 | -2195 | Critical Branch | Validation phase | 0 | 165 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 8459; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0430 | 8896 |  |  | 8731 |  |  | -2356 | -2356 | -2195 | Critical Branch | Validation phase | 0 | 165 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 8459; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0530 | 8896 |  |  | 8731 |  |  | -2356 | -2356 | -2195 | Critical Branch | Validation phase | 0 | 165 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 8459; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0630 | 8696 |  |  | 8533 |  |  | -2133 | -2133 | -1974 | Critical Branch | Validation phase | 0 | 163 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170; CH: 8259; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0730 | 8869 |  |  | 8697 |  |  | -2465 | -2465 | -2293 | Critical Branch | Validation phase | 0 | 172 | NA | NA | NA | 0 | 1 | AT: 429; AT: 155; CH: 8362; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0830 | 8869 |  |  | 8697 |  |  | -2465 | -2465 | -2293 | Critical Branch | Validation phase | 0 | 172 | NA | NA | NA | 0 | 1 | AT: 429; AT: 155; CH: 8362; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0930 | 8886 |  |  | 8686 |  |  | -1548 | -1548 | -1348 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 430; AT: 155; CH: 8351; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1030 | 8886 |  |  | 8686 |  |  | -1548 | -1548 | -1348 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 430; AT: 155; CH: 8351; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1130 | 8886 |  |  | 8686 |  |  | -1548 | -1548 | -1348 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 430; AT: 155; CH: 8351; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1230 | 8193 |  |  | 8163 |  |  | -2313 | -2313 | -2283 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 401; AT: 155; CH: 7828; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 1330 | 8193 |  |  | 8163 |  |  | -2313 | -2313 | -2283 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 401; AT: 155; CH: 7828; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 1430 | 8193 |  |  | 8163 |  |  | -2313 | -2313 | -2283 | Critical Branch | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 401; AT: 155; CH: 7828; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 1530 |  | 8156 | 978 |  | 7836 | 961 | -958 | -958 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 320 | 17 | 337 | 958 | 1 | AT: 241; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1630 |  | 8156 | 978 |  | 7836 | 961 | -958 | -958 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 320 | 17 | 337 | 958 | 1 | AT: 241; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1730 |  | 8156 | 978 |  | 7836 | 961 | -958 | -958 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 320 | 17 | 337 | 958 | 1 | AT: 241; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1830 |  | 7923 | 654 |  | 7922 | 654 | -5636 | -5636 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5636 | 1 | AT: 412; AT: 155
20251004 | October | 1930 |  | 7923 | 654 |  | 7922 | 654 | -5636 | -5636 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5636 | 1 | AT: 412; AT: 155
20251004 | October | 2030 |  | 7923 | 654 |  | 7922 | 654 | -5636 | -5636 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5636 | 1 | AT: 412; AT: 155
20251004 | October | 2130 | 8829 |  |  | 8737 |  |  | -2409 | -2409 | -2317 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 420; AT: 155; CH: 8402; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 2230 | 8829 |  |  | 8737 |  |  | -2409 | -2409 | -2317 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 420; AT: 155; CH: 8402; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 2330 | 8219 |  |  | 8127 |  |  | -1790 | -1790 | -1698 | Critical Branch | Validation phase | 0 | 92 | NA | NA | NA | 0 | 1 | AT: 403; AT: 170; CH: 7797; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251005 | October | 0030 | 8418 |  |  | 8063 |  |  | -557 | -557 | -202 | Critical Branch | Validation phase | 0 | 355 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251005 | October | 0130 | 8418 |  |  | 8063 |  |  | -557 | -557 | -202 | Critical Branch | Validation phase | 0 | 355 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251005 | October | 0230 | 8418 |  |  | 8063 |  |  | -557 | -557 | -202 | Critical Branch | Validation phase | 0 | 355 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7733; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251005 | October | 0330 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 22 | 0 | 22 | 1086 | 1 | AT: 425; AT: 167; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0430 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 22 | 0 | 22 | 1086 | 1 | AT: 425; AT: 167; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0530 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 22 | 0 | 22 | 1086 | 1 | AT: 425; AT: 167; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0630 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 22 | 0 | 22 | 1086 | 1 | AT: 425; AT: 167; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0730 |  | 8110 | 751 |  | 7935 | 736 | -1097 | -1097 | 0 | Critical Branch | Validation phase | 0 | NA | 175 | 15 | 190 | 1097 | 1 | AT: 427; AT: 169; CH: 8120; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0830 |  | 7810 | 751 |  | 7633 | 735 | -710 | -710 | 0 | Critical Branch | Validation phase | 0 | NA | 177 | 16 | 193 | 710 | 1 | AT: 424; AT: 169; CH: 7820; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0930 |  | 5972 | 519 |  | 5971 | 519 | -3294 | -3294 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 1 | 0 | 1 | 3294 | 1 | AT: 339; AT: 170
20251005 | October | 1030 |  | 5972 | 519 |  | 5971 | 519 | -3294 | -3294 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 1 | 0 | 1 | 3294 | 1 | AT: 339; AT: 170
20251005 | October | 1130 |  | 5972 | 519 |  | 5971 | 519 | -3294 | -3294 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 1 | 0 | 1 | 3294 | 1 | AT: 339; AT: 170
20251005 | October | 1230 |  | 5972 | 417 |  | 5971 | 417 | -3016 | -3016 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | 0 | NA | 1 | 0 | 1 | 3016 | 1 | AT: 339; AT: 170
20251005 | October | 1330 |  | 5972 | 417 |  | 5971 | 417 | -3016 | -3016 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | 0 | NA | 1 | 0 | 1 | 3016 | 1 | AT: 339; AT: 170
20251005 | October | 1430 |  | 5972 | 417 |  | 5971 | 417 | -3016 | -3016 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | 0 | NA | 1 | 0 | 1 | 3016 | 1 | AT: 339; AT: 170
20251005 | October | 1530 |  | 8406 | 782 |  | 7453 | 698 | 171 | 171 | 0 | Adjustment reached | Validation phase | 0 | NA | 953 | 84 | 1037 | -171 | 1 | AT: 417; AT: 168; CH: 7719; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1630 |  | 8536 | 767 |  | 7755 | 698 | -212 | -212 | 0 | Critical Branch | Validation phase | 0 | NA | 781 | 69 | 850 | 212 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8019; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1730 |  | 8536 | 767 |  | 7755 | 698 | -212 | -212 | 0 | Critical Branch | Validation phase | 0 | NA | 781 | 69 | 850 | 212 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8019; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1830 |  | 8461 | 795 |  | 7755 | 733 | -3076 | -3076 | 0 | Critical Branch | Validation phase | 0 | NA | 706 | 62 | 768 | 3076 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; CH: 8485; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1930 |  | 8461 | 795 |  | 7755 | 733 | -3076 | -3076 | 0 | Critical Branch | Validation phase | 0 | NA | 706 | 62 | 768 | 3076 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; CH: 8485; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2030 |  | 8461 | 795 |  | 7755 | 733 | -3076 | -3076 | 0 | Critical Branch | Validation phase | 0 | NA | 706 | 62 | 768 | 3076 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; CH: 8485; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2130 |  | 8389 | 806 |  | 8137 | 797 | -1227 | -1227 | 0 | Critical Branch | Validation phase | 0 | NA | 252 | 9 | 261 | 1227 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; CH: 8410; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2230 |  | 8389 | 806 |  | 8137 | 797 | -1227 | -1227 | 0 | Critical Branch | Validation phase | 0 | NA | 252 | 9 | 261 | 1227 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; CH: 8410; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2330 |  | 8389 | 806 |  | 8137 | 797 | -1227 | -1227 | 0 | Critical Branch | Validation phase | 0 | NA | 252 | 9 | 261 | 1227 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; CH: 8410; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 4000; FR: Overload - Planned Outage Busbar 1.2 Genissiat
20251006 | October | 0030 | 8421 |  |  | 8063 |  |  | -2116 | -2116 | -1758 | Critical Branch | Validation phase | 0 | 358 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7733; CH: Values from previous day, cause of missing data
20251006 | October | 0130 | 8421 |  |  | 8063 |  |  | -2116 | -2116 | -1758 | Critical Branch | Validation phase | 0 | 358 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7733; CH: Values from previous day, cause of missing data
20251006 | October | 0230 | 8421 |  |  | 8063 |  |  | -2116 | -2116 | -1758 | Critical Branch | Validation phase | 0 | 358 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7733; CH: Values from previous day, cause of missing data
20251006 | October | 0330 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251006 | October | 0430 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251006 | October | 0530 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251006 | October | 0630 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251006 | October | 0730 | 8802 |  |  | 7693 |  |  | -2114 | -2114 | -1047 | Critical Branch | Validation phase | 0 | 1109 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 7638; CH: Values from previous day, cause of missing data; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 0830 | 8562 |  |  | 7430 |  |  | -1893 | -1893 | -798 | Critical Branch | Validation phase | 0 | 1132 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7338; CH: Values from previous day, cause of missing data; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 0930 | 6250 |  |  | 6250 |  |  | 3946 | 0 | 3946 | TTC Selection - LTTC | TTC Selection - LTTC | 3946 | 0 | NA | NA | NA | 3946 | 1 | AT: 210; AT: 70
20251006 | October | 1030 | 6472 |  |  | 6472 |  |  | 3946 | 222 | 3724 | Minimum Margin | Minimum Margin | 3724 | 0 | NA | NA | NA | 7226 | 1 | AT: 210; AT: 70
20251006 | October | 1130 | 6461 |  |  | 6461 |  |  | 3946 | 211 | 3735 | Minimum Margin | Minimum Margin | 3735 | 0 | NA | NA | NA | 7259 | 1 | AT: 210; AT: 70
20251006 | October | 1230 | 6439 |  |  | 6439 |  |  | 4444 | 189 | 4255 | Minimum Margin | Minimum Margin | 4255 | 0 | NA | NA | NA | 8321 | 1 | AT: 210; AT: 70
20251006 | October | 1330 | 6439 |  |  | 6439 |  |  | 4444 | 189 | 4255 | Minimum Margin | Minimum Margin | 4255 | 0 | NA | NA | NA | 8321 | 1 | AT: 210; AT: 70
20251006 | October | 1430 | 6439 |  |  | 6439 |  |  | 4444 | 189 | 4255 | Minimum Margin | Minimum Margin | 4255 | 0 | NA | NA | NA | 8321 | 1 | AT: 210; AT: 70
20251006 | October | 1530 | 7389 |  |  | 7276 |  |  | 2679 | 211 | 2706 | Minimum Margin | TTC Validation phase - bilateral reduction | 2468 | 113 | NA | NA | NA | 5201 | 1 | AT: 210; AT: 70; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 1630 | 7178 |  |  | 7178 |  |  | 2679 | 0 | 2679 | Critical Branch | Critical Branch | 2679 | 0 | NA | NA | NA | 2679 | 1 | AT: 210; AT: 70
20251006 | October | 1730 | 7178 |  |  | 7178 |  |  | 2679 | 0 | 2679 | Critical Branch | Critical Branch | 2679 | 0 | NA | NA | NA | 2679 | 1 | AT: 210; AT: 70
20251006 | October | 1830 | 8767 |  |  | 7495 |  |  | -2804 | -2804 | -1581 | Critical Branch | Validation phase | 0 | 1272 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7458; CH: Values from previous day, cause of missing data; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 1930 | 8767 |  |  | 7495 |  |  | -2804 | -2804 | -1581 | Critical Branch | Validation phase | 0 | 1272 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7458; CH: Values from previous day, cause of missing data; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2030 | 8767 |  |  | 7495 |  |  | -2804 | -2804 | -1581 | Critical Branch | Validation phase | 0 | 1272 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 7458; CH: Values from previous day, cause of missing data; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2130 | 8218 |  |  | 7725 |  |  | -1914 | -1914 | -1494 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 493 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2230 | 8218 |  |  | 7725 |  |  | -1914 | -1914 | -1494 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 493 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2330 | 7623 |  |  | 7281 |  |  | -1302 | -1302 | -1009 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 342 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; FR: 3000; FR: Outage - CHAFFARD - GRANDE ILE 1
20251007 | October | 0030 | 7776 |  |  | 7361 |  |  | -4682 | -4682 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 415 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0130 | 7776 |  |  | 7361 |  |  | -4682 | -4682 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 415 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0230 | 7776 |  |  | 7361 |  |  | -4682 | -4682 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 415 | NA | NA | NA | 0 | 1 | AT: 209; AT: 70; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0330 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0430 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0530 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0630 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0730 | 7790 |  |  | 7393 |  |  | 6687 | 0 | 7318 | Critical Branch | Validation phase | 6687 | 397 | NA | NA | NA | 14636 | 1 | AT: 199; AT: 70; CH: 7270; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0830 | 7790 |  |  | 7393 |  |  | 6687 | 0 | 7318 | Critical Branch | Validation phase | 6687 | 397 | NA | NA | NA | 14636 | 1 | AT: 199; AT: 70; CH: 7270; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0930 | 7664 |  |  | 7424 |  |  | 3667 | 0 | 4172 | Critical Branch | TTC Validation phase - bilateral reduction | 3667 | 240 | NA | NA | NA | 8344 | 1 | AT: 197; AT: 70; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1030 | 7664 |  |  | 7424 |  |  | 3667 | 0 | 4172 | Critical Branch | TTC Validation phase - bilateral reduction | 3667 | 240 | NA | NA | NA | 8344 | 1 | AT: 197; AT: 70; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1130 | 7790 |  |  | 7492 |  |  | 3667 | 126 | 4167 | Minimum Margin | TTC Validation phase - bilateral reduction | 3541 | 298 | NA | NA | NA | 8208 | 1 | AT: 199; AT: 70; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1230 | 8420 |  |  | 7218 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1202 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7329; CH: Calculation not possible, values manuell adapted; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1; SI: 6947; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251007 | October | 1330 | 8420 |  |  | 7218 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1202 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7329; CH: Calculation not possible, values manuell adapted; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1; SI: 6947; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251007 | October | 1430 | 8420 |  |  | 7218 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1202 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7329; CH: Calculation not possible, values manuell adapted; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1; SI: 6947; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251007 | October | 1530 | 8420 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 995 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7329; CH: Calculation not possible, values manuell adapted; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1630 | 8420 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 995 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7329; CH: Calculation not possible, values manuell adapted; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1730 | 8420 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 995 | NA | NA | NA | 0 | 1 | AT: 210; AT: 70; CH: 7329; CH: Calculation not possible, values manuell adapted; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1830 | 7226 |  |  | 7225 |  |  | -1953 | -1953 | -1953 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 190; AT: 70
20251007 | October | 1930 | 7226 |  |  | 7225 |  |  | -1953 | -1953 | -1953 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 190; AT: 70
20251007 | October | 2030 | 7226 |  |  | 7225 |  |  | -1953 | -1953 | -1953 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 190; AT: 70
20251007 | October | 2130 | 8572 |  |  | 7915 |  |  | -2739 | -2739 | -2183 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 657 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 2230 | 8572 |  |  | 7915 |  |  | -2739 | -2739 | -2183 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 657 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 2330 | 7977 |  |  | 7464 |  |  | -2128 | -2128 | -1692 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 513 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Planed outage on CHAFFARD - GDE ILE 1
20251008 | October | 0030 | 8488 |  |  | 7387 |  |  | 2581 | 196 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2385 | 1101 | NA | NA | NA | -196 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0130 | 8488 |  |  | 7387 |  |  | 2581 | 196 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2385 | 1101 | NA | NA | NA | -196 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0230 | 8488 |  |  | 7387 |  |  | 2581 | 196 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2385 | 1101 | NA | NA | NA | -196 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0330 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2901 | 1183 | NA | NA | NA | -200 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0430 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2901 | 1183 | NA | NA | NA | -200 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0530 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2901 | 1183 | NA | NA | NA | -200 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0630 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2901 | 1183 | NA | NA | NA | -200 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0730 | 7983 |  |  | 7235 |  |  | -5170 | -5170 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 748 | NA | NA | NA | 5170 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 0830 | 7983 |  |  | 7151 |  |  | -5170 | -5170 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 832 | NA | NA | NA | 5170 | 1 | AT: 190; AT: 70; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 0930 |  | 5071 | 377 | 5651 |  |  | 5465 | 2 | 6208 | Minimum Margin | Minimum Margin | 5463 | NA | NA | NA | NA | 12414 | 1 | AT: 147; AT: 70
20251008 | October | 1030 |  | 5142 | 384 | 5727 |  |  | 5465 | 73 | 6133 | Minimum Margin | Minimum Margin | 5392 | NA | NA | NA | NA | 12193 | 1 | AT: 150; AT: 70
20251008 | October | 1130 |  | 5301 | 400 | 5898 |  |  | 5465 | 233 | 5962 | Minimum Margin | Minimum Margin | 5232 | NA | NA | NA | NA | 11691 | 1 | AT: 155; AT: 70
20251008 | October | 1230 |  | 5265 | 529 | 5868 |  |  | 5185 | 196 | 5578 | Minimum Margin | Minimum Margin | 4989 | NA | NA | NA | NA | 10960 | 1 | AT: 154; AT: 70
20251008 | October | 1330 |  | 5265 | 529 | 5868 |  |  | 5185 | 196 | 5578 | Minimum Margin | Minimum Margin | 4989 | NA | NA | NA | NA | 10960 | 1 | AT: 154; AT: 70
20251008 | October | 1430 |  | 5265 | 529 | 5868 |  |  | 5185 | 196 | 5578 | Minimum Margin | Minimum Margin | 4989 | NA | NA | NA | NA | 10960 | 1 | AT: 154; AT: 70
20251008 | October | 1530 |  | 7231 | 830 | 7144 |  |  | 2750 | 187 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2563 | NA | NA | NA | NA | -187 | 1 | AT: 119; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1630 |  | 7141 | 819 | 7100 |  |  | 2750 | 97 | 4796 | Minimum Margin | TTC Validation phase - bilateral reduction | 2653 | NA | NA | NA | NA | 9495 | 1 | AT: 128; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1730 |  | 7244 | 831 | 7153 |  |  | 2750 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2550 | NA | NA | NA | NA | -200 | 1 | AT: 128; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1830 |  | 6965 | 852 | 6940 |  |  | -5142 | -5142 | -4628 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 0 | 1 | AT: 100; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1; IT: 490; IT: Forecasted security violation
20251008 | October | 1930 |  | 6965 | 852 | 6940 |  |  | -5142 | -5142 | -4628 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 0 | 1 | AT: 100; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1; IT: 490; IT: Forecasted security violation
20251008 | October | 2030 |  | 6965 | 852 | 6940 |  |  | -5142 | -5142 | -4628 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 0 | 1 | AT: 100; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1; IT: 490; IT: Forecasted security violation
20251008 | October | 2130 |  | 8091 | 917 | 7235 |  |  | -2595 | -2595 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2595 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 65; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 2230 |  | 8091 | 917 | 7235 |  |  | -2595 | -2595 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2595 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 65; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 2330 |  | 7559 | 937 | 6787 |  |  | -1945 | -1945 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 1945 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 65; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251009 | October | 0030 | 8374 |  |  | 7423 |  |  | 1927 | 220 | 3803 | Minimum Margin | TTC Validation phase - bilateral reduction | 1707 | 951 | NA | NA | NA | 7386 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0130 | 8374 |  |  | 7423 |  |  | 1927 | 220 | 3803 | Minimum Margin | TTC Validation phase - bilateral reduction | 1707 | 951 | NA | NA | NA | 7386 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0230 | 8374 |  |  | 7423 |  |  | 1927 | 220 | 3803 | Minimum Margin | TTC Validation phase - bilateral reduction | 1707 | 951 | NA | NA | NA | 7386 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0330 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 3069 | 131 | NA | NA | NA | 6490 | 1 | AT: 195; AT: 70; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0430 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 3069 | 131 | NA | NA | NA | 6490 | 1 | AT: 195; AT: 70; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0530 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 3069 | 131 | NA | NA | NA | 6490 | 1 | AT: 195; AT: 70; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0630 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 3069 | 131 | NA | NA | NA | 6490 | 1 | AT: 195; AT: 70; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0730 | 7401 |  |  | 6988 |  |  | -2202 | -2202 | -1791 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 413 | NA | NA | NA | 0 | 1 | AT: 202; AT: 70; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0830 | 7401 |  |  | 6984 |  |  | -2202 | -2202 | -1789 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 417 | NA | NA | NA | 0 | 1 | AT: 198; AT: 70; FR: 2400; FR: Outage - RDCR FIL Link 1
20251009 | October | 0930 | 5766 |  |  | 5765 |  |  | 5231 | 116 | 5115 | Minimum Margin | Minimum Margin | 5115 | 1 | NA | NA | NA | 10114 | 1 | AT: 174; AT: 70
20251009 | October | 1030 | 5887 |  |  | 5886 |  |  | 5231 | 237 | 4994 | Minimum Margin | Minimum Margin | 4994 | 1 | NA | NA | NA | 9751 | 1 | AT: 176; AT: 70
20251009 | October | 1130 | 5883 |  |  | 5882 |  |  | 5231 | 233 | 4998 | Minimum Margin | Minimum Margin | 4998 | 1 | NA | NA | NA | 9763 | 1 | AT: 176; AT: 70
20251009 | October | 1230 | 5890 |  |  | 5501 |  |  | 2935 | 240 | 3598 | Minimum Margin | TTC Validation phase - bilateral reduction | 2695 | 389 | NA | NA | NA | 6956 | 1 | AT: 176; AT: 70; FR: 1800; FR: Outage - RDCR FIL Link 1 & 2
20251009 | October | 1330 | 5322 |  |  | 5322 |  |  | 4623 | 272 | 4351 | Minimum Margin | Minimum Margin | 4351 | 0 | NA | NA | NA | 8430 | 1 | AT: 174; AT: 70
20251009 | October | 1430 | 5322 |  |  | 5322 |  |  | 4623 | 272 | 4351 | Minimum Margin | Minimum Margin | 4351 | 0 | NA | NA | NA | 8430 | 1 | AT: 174; AT: 70
20251009 | October | 1530 |  | 6408 | 710 |  | 5819 | 710 | 3713 | 254 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3459 | NA | 589 | 0 | 589 | -254 | 1 | AT: 205; AT: 70; FR: 1800; FR: Outage - RDCR FIL Link 1 & 2
20251009 | October | 1630 |  | 6408 | 710 |  | 5823 | 710 | 3713 | 254 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3459 | NA | 585 | 0 | 585 | -254 | 1 | AT: 209; AT: 70; FR: 1800; FR: Outage - RDCR FIL Link 1 & 2
20251009 | October | 1730 |  | 6648 | 710 |  | 6055 | 710 | 3613 | 254 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3359 | NA | 593 | 0 | 593 | -254 | 1 | AT: 440; AT: 155; FR: 1800; FR: Outage - RDCR FIL Link 1 & 2
20251009 | October | 1830 |  | 8561 | 795 |  | 7598 | 795 | -4451 | -4451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 963 | 0 | 963 | 4451 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - RO CHAFFARD G.ILE 1
20251009 | October | 1930 |  | 8561 | 795 |  | 7598 | 795 | -4451 | -4451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 963 | 0 | 963 | 4451 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2030 |  | 8561 | 795 |  | 7598 | 795 | -4451 | -4451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 963 | 0 | 963 | 4451 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2130 | 9155 |  |  | 8324 |  |  | -2823 | -2823 | -2066 | Critical Branch | Validation phase | 0 | 831 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 8813; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2230 | 9155 |  |  | 8324 |  |  | -2823 | -2823 | -2066 | Critical Branch | Validation phase | 0 | 831 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 8813; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2330 | 8545 |  |  | 7852 |  |  | -2208 | -2208 | -1575 | Critical Branch | Validation phase | 0 | 693 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8208; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - RO CHAFFARD G.ILE 1
20251010 | October | 0030 | 7158 |  |  | 7158 |  |  | -28 | -28 | -28 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0130 | 7158 |  |  | 7158 |  |  | -28 | -28 | -28 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0230 | 7158 |  |  | 7158 |  |  | -28 | -28 | -28 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0330 | 6609 |  |  | 6609 |  |  | -2766 | -2766 | -2766 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0430 | 6609 |  |  | 6609 |  |  | -2766 | -2766 | -2766 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0530 | 6609 |  |  | 6609 |  |  | -2766 | -2766 | -2766 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0630 | 6609 |  |  | 6609 |  |  | -2766 | -2766 | -2766 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0730 | 7419 |  |  | 7419 |  |  | -2388 | -2388 | -2388 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0830 | 7419 |  |  | 7419 |  |  | -2388 | -2388 | -2388 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251010 | October | 0930 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2325 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1030 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2325 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1130 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2325 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1230 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2325 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1330 | 8260 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1925 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1430 | 8260 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1925 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1530 | 8660 |  |  | 7385 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1275 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1630 | 8660 |  |  | 7385 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1275 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1730 | 8660 |  |  | 7385 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1275 | NA | NA | NA | 0 | 1 | CH: 7084; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1830 | 7707 |  |  | 7545 |  |  | -2971 | -2971 | -2810 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 162 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1930 | 7707 |  |  | 7545 |  |  | -2971 | -2971 | -2810 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 162 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2030 | 7707 |  |  | 7545 |  |  | -2971 | -2971 | -2810 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 162 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2130 | 8660 |  |  | 7736 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 924 | NA | NA | NA | 0 | 1 | CH: 7715; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2230 | 8660 |  |  | 7736 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 924 | NA | NA | NA | 0 | 1 | CH: 7715; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2330 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0030 | 6490 |  |  | 6490 |  |  | -28 | -28 | -28 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 0130 | 6490 |  |  | 6490 |  |  | -28 | -28 | -28 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 0230 | 6490 |  |  | 6490 |  |  | -28 | -28 | -28 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 0330 | 6973 |  |  | 6874 |  |  | 4022 | 215 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 3807 | 99 | NA | NA | NA | 7809 | 1 | FR: 2843; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0430 | 6973 |  |  | 6874 |  |  | 4022 | 215 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 3807 | 99 | NA | NA | NA | 7809 | 1 | FR: 2843; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0530 | 6973 |  |  | 6874 |  |  | 4022 | 215 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 3807 | 99 | NA | NA | NA | 7809 | 1 | FR: 2843; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0630 | 6979 |  |  | 6877 |  |  | 4022 | 221 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 3801 | 102 | NA | NA | NA | 7803 | 1 | FR: 2843; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0730 | 6490 |  |  | 6490 |  |  | -476 | -476 | -476 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 0830 | 6490 |  |  | 6490 |  |  | -476 | -476 | -476 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 0930 | 6950 |  |  | 6750 |  |  | 1879 | 447 | 1701 | Minimum Margin | TTC Validation phase - bilateral reduction | 1432 | 200 | NA | NA | NA | 2955 | 1 | FR: 2626; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 1030 | 6778 |  |  | 6655 |  |  | 1879 | 275 | 1770 | Minimum Margin | TTC Validation phase - bilateral reduction | 1604 | 123 | NA | NA | NA | 3265 | 1 | FR: 2626; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 1130 | 6950 |  |  | 6750 |  |  | 1879 | 447 | 1701 | Minimum Margin | TTC Validation phase - bilateral reduction | 1432 | 200 | NA | NA | NA | 2955 | 1 | FR: 2626; FR: Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 1230 | 6723 |  |  | 6723 |  |  | -631 | -631 | -631 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 1330 | 6723 |  |  | 6723 |  |  | -631 | -631 | -631 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 1430 | 6723 |  |  | 6723 |  |  | -631 | -631 | -631 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 1530 |  | 6032 | 536 |  | 6032 | 536 | -47 | -47 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 47 | 0
20251011 | October | 1630 |  | 6032 | 536 |  | 6032 | 536 | -47 | -47 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 47 | 0
20251011 | October | 1730 |  | 6032 | 536 |  | 6032 | 536 | -47 | -47 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 47 | 0
20251011 | October | 1830 | 6490 |  |  | 6202 |  |  | -1151 | -1151 | -863 | TTC Selection - LTTC | Validation phase | 0 | 288 | NA | NA | NA | 0 | 1 | CH: 5867; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251011 | October | 1930 | 6490 |  |  | 6202 |  |  | -1151 | -1151 | -863 | TTC Selection - LTTC | Validation phase | 0 | 288 | NA | NA | NA | 0 | 1 | CH: 5867; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251011 | October | 2030 | 6490 |  |  | 6202 |  |  | -1151 | -1151 | -863 | TTC Selection - LTTC | Validation phase | 0 | 288 | NA | NA | NA | 0 | 1 | CH: 5867; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251011 | October | 2130 | 6490 |  |  | 6490 |  |  | -6 | -6 | -6 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 2230 | 6490 |  |  | 6490 |  |  | -6 | -6 | -6 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251011 | October | 2330 | 6419 |  |  | 6170 |  |  | 591 | 539 | 310 | Minimum Margin | TTC Validation phase - bilateral reduction | 52 | 249 | NA | NA | NA | 81 | 1 | FR: 2438; FR: Outage - Outage Chaffard - Gd ILE 1
20251012 | October | 0030 | 8550 |  |  | 7858 |  |  | -1648 | -1648 | -1073 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 692 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0130 | 8550 |  |  | 7858 |  |  | -1648 | -1648 | -1073 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 692 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0230 | 8550 |  |  | 7858 |  |  | -1648 | -1648 | -1073 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 692 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0330 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 754 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0430 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 754 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0530 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 754 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0630 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 754 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0730 | 8543 |  |  | 7855 |  |  | -1910 | -1910 | -1337 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0830 | 8543 |  |  | 7855 |  |  | -1910 | -1910 | -1337 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0930 | 7690 |  |  | 7417 |  |  | 1235 | 218 | 1579 | Minimum Margin | TTC Validation phase - bilateral reduction | 1017 | 273 | NA | NA | NA | 2940 | 1 | AT: 417; AT: 170; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1030 | 7688 |  |  | 7416 |  |  | 1235 | 216 | 1579 | Minimum Margin | TTC Validation phase - bilateral reduction | 1019 | 272 | NA | NA | NA | 2942 | 1 | AT: 417; AT: 170; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1130 | 7689 |  |  | 7416 |  |  | 1235 | 217 | 1579 | Minimum Margin | TTC Validation phase - bilateral reduction | 1018 | 273 | NA | NA | NA | 2941 | 1 | AT: 417; AT: 170; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1230 | 8075 |  |  | 7624 |  |  | 1461 | 202 | 2190 | Minimum Margin | TTC Validation phase - bilateral reduction | 1259 | 451 | NA | NA | NA | 4178 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1330 | 8079 |  |  | 7626 |  |  | 1461 | 206 | 2190 | Minimum Margin | TTC Validation phase - bilateral reduction | 1255 | 453 | NA | NA | NA | 4174 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1430 | 8075 |  |  | 7624 |  |  | 1461 | 202 | 2190 | Minimum Margin | TTC Validation phase - bilateral reduction | 1259 | 451 | NA | NA | NA | 4178 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1530 | 6859 |  |  | 6859 |  |  | 2236 | 218 | 2018 | Minimum Margin | Minimum Margin | 2018 | 0 | NA | NA | NA | 3818 | 1 | AT: 378; AT: 170
20251012 | October | 1630 | 6859 |  |  | 6859 |  |  | 2236 | 218 | 2018 | Minimum Margin | Minimum Margin | 2018 | 0 | NA | NA | NA | 3818 | 1 | AT: 378; AT: 170
20251012 | October | 1730 | 6859 |  |  | 6859 |  |  | 2236 | 218 | 2018 | Minimum Margin | Minimum Margin | 2018 | 0 | NA | NA | NA | 3818 | 1 | AT: 378; AT: 170
20251012 | October | 1830 | 8681 |  |  | 7923 |  |  | -3132 | -3132 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 758 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1930 | 8681 |  |  | 7923 |  |  | -3132 | -3132 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 758 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2030 | 8681 |  |  | 7923 |  |  | -3132 | -3132 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 758 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2130 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2230 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2330 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - Outage CHAFFARD - GD ILE 1
20251013 | October | 0030 | 8343 |  |  | 7756 |  |  | -4851 | -4851 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 587 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0130 | 8343 |  |  | 7756 |  |  | -4851 | -4851 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 587 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0230 | 8343 |  |  | 7756 |  |  | -4851 | -4851 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 587 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0330 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 449 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0430 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 449 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0530 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 449 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0630 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 449 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0730 | 9001 |  |  | 8249 |  |  | -3247 | -3247 | -2598 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 752 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0830 | 9001 |  |  | 8249 |  |  | -3247 | -3247 | -2598 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 752 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0930 | 8306 |  |  | 7877 |  |  | -4187 | -4187 | -3771 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 429 | NA | NA | NA | 0 | 1 | AT: 433; AT: 155; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1030 | 8306 |  |  | 7877 |  |  | -4187 | -4187 | -3771 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 429 | NA | NA | NA | 0 | 1 | AT: 433; AT: 155; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1130 | 8306 |  |  | 7870 |  |  | -4187 | -4187 | -3764 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 436 | NA | NA | NA | 0 | 1 | AT: 426; AT: 155; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1230 |  | 6077 | 519 |  | 6077 | 519 | 3218 | 184 | 0 | Minimum Margin | Minimum Margin | 3034 | NA | 0 | 0 | 0 | -184 | 1 | AT: 361; AT: 155
20251013 | October | 1330 |  | 6077 | 519 |  | 6077 | 519 | 3218 | 184 | 0 | Minimum Margin | Minimum Margin | 3034 | NA | 0 | 0 | 0 | -184 | 1 | AT: 361; AT: 155
20251013 | October | 1430 |  | 6077 | 519 |  | 6077 | 519 | 3218 | 184 | 0 | Minimum Margin | Minimum Margin | 3034 | NA | 0 | 0 | 0 | -184 | 1 | AT: 361; AT: 155
20251013 | October | 1530 |  | 6400 | 568 |  | 6400 | 568 | 3150 | 181 | 0 | Minimum Margin | Minimum Margin | 2969 | NA | 0 | 0 | 0 | -181 | 1 | AT: 377; AT: 155
20251013 | October | 1630 |  | 6400 | 568 |  | 6400 | 396 | 3150 | 181 | 0 | Minimum Margin | Minimum Margin | 2969 | NA | 0 | 172 | 172 | -181 | 1 | AT: 377; AT: 155
20251013 | October | 1730 |  | 6400 | 568 |  | 6400 | 221 | 3150 | 181 | 0 | Minimum Margin | Minimum Margin | 2969 | NA | 0 | 347 | 347 | -181 | 1 | AT: 377; AT: 155
20251013 | October | 1830 |  | 7882 | 721 |  | 7285 | 47 | -5008 | -5008 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 597 | 674 | 1271 | 5008 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT; IT: 0; IT: Forecasted security violation
20251013 | October | 1930 |  | 7882 | 721 |  | 7285 | 47 | -5008 | -5008 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 597 | 674 | 1271 | 5008 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT; IT: 0; IT: Forecasted security violation
20251013 | October | 2030 |  | 7882 | 721 |  | 7285 | 47 | -5008 | -5008 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 597 | 674 | 1271 | 5008 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT; IT: 0; IT: Forecasted security violation
20251013 | October | 2130 | 9128 |  |  | 7888 |  |  | -3380 | -3380 | -2197 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1240 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 7989; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 2230 | 9128 |  |  | 7888 |  |  | -3380 | -3380 | -2197 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1240 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 7989; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 2330 | 8518 |  |  | 7431 |  |  | -2758 | -2758 | -1707 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1087 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7384; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA; FR: 3000; FR: Outage - maintenance work on bus bar 2.1 GENISSIAT
20251014 | October | 0030 | 8323 |  |  | 7745 |  |  | -4524 | -4524 | -3961 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 578 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0130 | 8323 |  |  | 7745 |  |  | -4524 | -4524 | -3961 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 578 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0230 | 8323 |  |  | 7745 |  |  | -4524 | -4524 | -3961 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 578 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0330 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 706 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0430 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 706 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0530 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 706 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0630 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 706 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0730 |  | 7604 | 693 |  | 7143 | 693 | -2676 | -2676 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 461 | 0 | 461 | 2676 | 1 | AT: 434; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0830 |  | 7604 | 693 |  | 7143 | 693 | -2676 | -2676 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 461 | 0 | 461 | 2676 | 1 | AT: 434; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0930 | 8437 |  |  | 7949 |  |  | -3188 | -3188 | -2753 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 488 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1030 | 8437 |  |  | 7949 |  |  | -3188 | -3188 | -2753 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 488 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1130 | 8437 |  |  | 7949 |  |  | -3188 | -3188 | -2753 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 488 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1230 | 7575 |  |  | 7467 |  |  | 4695 | 216 | 4713 | Minimum Margin | TTC Validation phase - bilateral reduction | 4479 | 108 | NA | NA | NA | 9210 | 1 | AT: 390; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1330 | 7575 |  |  | 7467 |  |  | 4695 | 216 | 4713 | Minimum Margin | TTC Validation phase - bilateral reduction | 4479 | 108 | NA | NA | NA | 9210 | 1 | AT: 390; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1430 | 7575 |  |  | 7467 |  |  | 4695 | 216 | 4713 | Minimum Margin | TTC Validation phase - bilateral reduction | 4479 | 108 | NA | NA | NA | 9210 | 1 | AT: 390; AT: 155; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1530 |  | 7744 | 710 |  | 7215 | 693 | -4139 | -4139 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 529 | 17 | 546 | 4139 | 1 | AT: 442; AT: 154; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1630 |  | 7744 | 710 |  | 7215 | 477 | -4139 | -4139 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 529 | 233 | 762 | 4139 | 1 | AT: 442; AT: 154; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1730 |  | 7744 | 710 |  | 7215 | 262 | -4139 | -4139 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 529 | 448 | 977 | 4139 | 1 | AT: 442; AT: 154; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1830 |  | 7264 | 888 |  | 6740 | 74 | -2593 | -2593 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 524 | 814 | 1338 | 2593 | 1 | AT: 203; AT: 154; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT; IT: 0; IT: Forecasted security violation
20251014 | October | 1930 |  | 7264 | 888 |  | 6740 | 74 | -2593 | -2593 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 524 | 814 | 1338 | 2593 | 1 | AT: 203; AT: 154; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT; IT: 0; IT: Forecasted security violation
20251014 | October | 2030 |  | 7264 | 888 |  | 6740 | 74 | -2593 | -2593 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 524 | 814 | 1338 | 2593 | 1 | AT: 203; AT: 154; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT; IT: 0; IT: Forecasted security violation
20251014 | October | 2130 |  | 8120 | 765 |  | 7394 | 280 | -3838 | -3838 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 726 | 485 | 1211 | 3838 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 2230 |  | 8120 | 765 |  | 7394 | 513 | -3838 | -3838 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 726 | 252 | 978 | 3838 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 2330 |  | 7569 | 785 |  | 7018 | 722 | -3200 | -3200 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 551 | 63 | 614 | 3200 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - Bus bar 2.1 GENISSIAT
20251015 | October | 0030 | 8743 |  |  | 7953 |  |  | -3072 | -3072 | -2365 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 790 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0130 | 8743 |  |  | 7953 |  |  | -3072 | -3072 | -2365 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 790 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0230 | 8743 |  |  | 7953 |  |  | -3072 | -3072 | -2365 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 790 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0330 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 737 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0430 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 737 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0530 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 737 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0630 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 737 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0730 |  | 7169 | 791 |  | 6701 | 790 | -4931 | -4931 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 468 | 1 | 469 | 4931 | 1 | AT: 139; AT: 100; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0830 |  | 7169 | 791 |  | 6701 | 790 | -4931 | -4931 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 468 | 1 | 469 | 4931 | 1 | AT: 139; AT: 100; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0930 | 8209 |  |  | 7759 |  |  | -3643 | -3643 | -3219 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 450 | NA | NA | NA | 0 | 1 | AT: 291; AT: 105; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1030 | 8209 |  |  | 7759 |  |  | -3643 | -3643 | -3219 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 450 | NA | NA | NA | 0 | 1 | AT: 291; AT: 105; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1130 | 8209 |  |  | 7753 |  |  | -3643 | -3643 | -3216 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 456 | NA | NA | NA | 0 | 1 | AT: 285; AT: 105; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1230 |  | 5937 | 411 |  | 5936 | 411 | 2566 | 191 | 0 | Minimum Margin | Validation phase | 2375 | NA | 1 | 0 | 1 | -191 | 1 | AT: 246; AT: 105; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251015 | October | 1330 |  | 5937 | 411 |  | 5936 | 411 | 2566 | 191 | 0 | Minimum Margin | Validation phase | 2375 | NA | 1 | 0 | 1 | -191 | 1 | AT: 246; AT: 105; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251015 | October | 1430 |  | 5943 | 411 |  | 5943 | 411 | 2566 | 197 | 0 | Minimum Margin | Validation phase | 2369 | NA | 0 | 0 | 0 | -197 | 1 | AT: 247; AT: 105; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251015 | October | 1530 |  | 7205 | 654 |  | 6871 | 652 | 3389 | 198 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3191 | NA | 334 | 2 | 336 | -198 | 1 | AT: 284; AT: 105; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1630 |  | 7200 | 654 |  | 6869 | 450 | 3389 | 193 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3196 | NA | 331 | 204 | 535 | -193 | 1 | AT: 284; AT: 105; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1730 |  | 7209 | 655 |  | 6873 | 249 | 3389 | 202 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3187 | NA | 336 | 406 | 742 | -202 | 1 | AT: 284; AT: 105; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1830 |  | 7460 | 675 |  | 7071 | 47 | 258 | 236 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 22 | NA | 389 | 628 | 1017 | -236 | 1 | AT: 430; AT: 155; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1; IT: 0; IT: Forecasted Security Violation
20251015 | October | 1930 |  | 7328 | 663 |  | 7003 | 47 | 258 | 103 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 155 | NA | 325 | 616 | 941 | -103 | 1 | AT: 423; AT: 155; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1; IT: 0; IT: Forecasted Security Violation
20251015 | October | 2030 |  | 7453 | 675 |  | 7067 | 47 | 258 | 229 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 29 | NA | 386 | 628 | 1014 | -229 | 1 | AT: 429; AT: 155; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1; IT: 0; IT: Forecasted Security Violation
20251015 | October | 2130 |  | 8776 | 817 |  | 7697 | 297 | -3641 | -3641 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1079 | 520 | 1599 | 3641 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 2230 |  | 8776 | 817 |  | 7697 | 547 | -3641 | -3641 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1079 | 270 | 1349 | 3641 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 2330 |  | 8228 | 837 |  | 7311 | 769 | -2975 | -2975 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 917 | 68 | 985 | 2975 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 166; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251016 | October | 0030 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0130 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0230 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0330 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0430 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0530 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0630 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0730 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0830 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0930 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1030 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1130 | 8510 |  |  | 7835 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 675 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1230 | 8510 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2175 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251016 | October | 1330 | 8510 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2175 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251016 | October | 1430 | 8510 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2175 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251016 | October | 1530 | 8510 |  |  | 7835 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 675 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1630 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1730 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1830 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1; IT: 0; IT: Forecasted Security Violation
20251016 | October | 1930 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1; IT: 0; IT: Forecasted Security Violation
20251016 | October | 2030 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1; IT: 0; IT: Forecasted Security Violation
20251016 | October | 2130 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 2230 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 585 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 2330 | 8200 |  |  | 7762 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0030 | 7348 |  |  | 7233 |  |  | -3434 | -3434 | -3322 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 115 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0130 | 7348 |  |  | 7233 |  |  | -3434 | -3434 | -3322 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 115 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0230 | 7348 |  |  | 7233 |  |  | -3434 | -3434 | -3322 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 115 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0330 | 6901 |  |  | 6901 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 0430 | 6901 |  |  | 6901 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 0530 | 6901 |  |  | 6901 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 0630 | 6901 |  |  | 6901 |  |  | -3233 | -3233 | -3233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 0730 | 8350 |  |  | 7903 |  |  | -3035 | -3035 | -2636 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 447 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0830 | 8350 |  |  | 7903 |  |  | -3035 | -3035 | -2636 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 447 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0930 | 8107 |  |  | 7768 |  |  | -4555 | -4555 | -4221 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 339 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 1030 | 8107 |  |  | 7768 |  |  | -4555 | -4555 | -4221 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 339 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 1130 | 8107 |  |  | 7768 |  |  | -4555 | -4555 | -4221 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 339 | NA | NA | NA | 0 | 1 | FR: 3000; FR: Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 1230 | 6720 |  |  | 6720 |  |  | 5289 | 230 | 5059 | Minimum Margin | Minimum Margin | 5059 | 0 | NA | NA | NA | 9888 | 0
20251017 | October | 1330 | 6720 |  |  | 6720 |  |  | 5289 | 230 | 5059 | Minimum Margin | Minimum Margin | 5059 | 0 | NA | NA | NA | 9888 | 0
20251017 | October | 1430 | 6720 |  |  | 6720 |  |  | 5289 | 230 | 5059 | Minimum Margin | Minimum Margin | 5059 | 0 | NA | NA | NA | 9888 | 0
20251017 | October | 1530 | 7108 |  |  | 7108 |  |  | 4673 | 204 | 4469 | Minimum Margin | Minimum Margin | 4469 | 0 | NA | NA | NA | 8734 | 0
20251017 | October | 1630 | 7110 |  |  | 7110 |  |  | 4673 | 206 | 4467 | Minimum Margin | Minimum Margin | 4467 | 0 | NA | NA | NA | 8728 | 0
20251017 | October | 1730 | 8006 |  |  | 8006 |  |  | 3085 | 202 | 2883 | Minimum Margin | Minimum Margin | 2883 | 0 | NA | NA | NA | 5564 | 0
20251017 | October | 1830 | 8881 |  |  | 8881 |  |  | -2596 | -2596 | -2596 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 1930 | 8881 |  |  | 8881 |  |  | -2596 | -2596 | -2596 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 2030 | 8881 |  |  | 8881 |  |  | -2596 | -2596 | -2596 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251017 | October | 2130 | 9511 |  |  | 9125 |  |  | -3256 | -3256 | -2870 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | CH: 8790; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251017 | October | 2230 | 9511 |  |  | 9125 |  |  | -3256 | -3256 | -2870 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | CH: 8790; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251017 | October | 2330 | 8901 |  |  | 8515 |  |  | -2633 | -2633 | -2247 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | CH: 8185; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251018 | October | 0030 | 9458 |  |  | 8912 |  |  | -2774 | -2774 | -2233 | Critical Branch | Validation phase | 0 | 546 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 0130 | 9458 |  |  | 8912 |  |  | -2774 | -2774 | -2233 | Critical Branch | Validation phase | 0 | 546 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 0230 | 9458 |  |  | 8912 |  |  | -2774 | -2774 | -2233 | Critical Branch | Validation phase | 0 | 546 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 0330 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0430 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0530 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0630 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0730 | 8637 |  |  | 8637 |  |  | -4884 | -4884 | -4883 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 412; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0830 | 8637 |  |  | 8637 |  |  | -4884 | -4884 | -4883 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 412; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0930 | 8197 |  |  | 8196 |  |  | -4400 | -4400 | -4399 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 394; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1030 | 8197 |  |  | 8196 |  |  | -4400 | -4400 | -4399 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 394; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1130 | 8197 |  |  | 8196 |  |  | -4400 | -4400 | -4399 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 394; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1230 | 8577 |  |  | 8577 |  |  | 3055 | 153 | 2902 | Minimum Margin | TTC Validation phase - bilateral reduction | 2902 | 0 | NA | NA | NA | 5651 | 1 | AT: 410; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1330 | 8577 |  |  | 8577 |  |  | 3055 | 153 | 2902 | Minimum Margin | TTC Validation phase - bilateral reduction | 2902 | 0 | NA | NA | NA | 5651 | 1 | AT: 410; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1430 | 8577 |  |  | 8577 |  |  | 3055 | 153 | 2902 | Minimum Margin | TTC Validation phase - bilateral reduction | 2902 | 0 | NA | NA | NA | 5651 | 1 | AT: 410; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1530 |  | 8845 | 780 |  | 8580 | 774 | -2449 | -2449 | 0 | Critical Branch | Validation phase | 0 | NA | 265 | 6 | 271 | 2449 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1630 |  | 8845 | 780 |  | 8580 | 774 | -2449 | -2449 | 0 | Critical Branch | Validation phase | 0 | NA | 265 | 6 | 271 | 2449 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1730 |  | 8845 | 780 |  | 8580 | 774 | -2449 | -2449 | 0 | Critical Branch | Validation phase | 0 | NA | 265 | 6 | 271 | 2449 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1830 |  | 8497 | 720 |  | 8452 | 720 | -3209 | -3209 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 45 | 0 | 45 | 3209 | 1 | AT: 438; AT: 154; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1930 |  | 8497 | 720 |  | 8452 | 720 | -3209 | -3209 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 45 | 0 | 45 | 3209 | 1 | AT: 438; AT: 154; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 2030 |  | 8497 | 720 |  | 8452 | 720 | -3209 | -3209 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 45 | 0 | 45 | 3209 | 1 | AT: 438; AT: 154; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251018 | October | 2130 | 8403 |  |  | 8402 |  |  | -4539 | -4539 | -4538 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 402; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 2230 | 8403 |  |  | 8402 |  |  | -4539 | -4539 | -4538 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 402; AT: 155; CH: 9225; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 2330 | 7793 |  |  | 7792 |  |  | -3929 | -3929 | -3928 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 385; AT: 170; CH: 8620; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251019 | October | 0030 | 9011 |  |  | 8225 |  |  | -5652 | -5652 | -4866 | Critical Branch | Validation phase | 0 | 786 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7895; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0130 | 9011 |  |  | 8225 |  |  | -5652 | -5652 | -4866 | Critical Branch | Validation phase | 0 | 786 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7895; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0230 | 9011 |  |  | 8225 |  |  | -5652 | -5652 | -4866 | Critical Branch | Validation phase | 0 | 786 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7895; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0330 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 408; AT: 170
20251019 | October | 0430 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 408; AT: 170
20251019 | October | 0530 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 408; AT: 170
20251019 | October | 0630 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 408; AT: 170
20251019 | October | 0730 | 8664 |  |  | 8387 |  |  | -4959 | -4959 | -4682 | Critical Branch | Validation phase | 0 | 277 | NA | NA | NA | 0 | 1 | AT: 422; AT: 170; CH: 8057; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0830 | 8664 |  |  | 8387 |  |  | -4959 | -4959 | -4682 | Critical Branch | Validation phase | 0 | 277 | NA | NA | NA | 0 | 1 | AT: 422; AT: 170; CH: 8057; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0930 | 8285 |  |  | 7266 |  |  | -1769 | -1769 | -750 | Critical Branch | Validation phase | 0 | 1019 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170; CH: 6936; CH: Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251019 | October | 1030 | 8285 |  |  | 7266 |  |  | -1769 | -1769 | -750 | Critical Branch | Validation phase | 0 | 1019 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170; CH: 6936; CH: Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251019 | October | 1130 | 8285 |  |  | 7266 |  |  | -1769 | -1769 | -750 | Critical Branch | Validation phase | 0 | 1019 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170; CH: 6936; CH: Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251019 | October | 1230 | 6936 |  |  | 6935 |  |  | -2858 | -2858 | -2858 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 349; AT: 170
20251019 | October | 1330 | 6936 |  |  | 6935 |  |  | -2858 | -2858 | -2858 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 349; AT: 170
20251019 | October | 1430 | 6936 |  |  | 6935 |  |  | -2858 | -2858 | -2858 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 349; AT: 170
20251019 | October | 1530 |  | 8298 | 778 |  | 8003 | 752 | -1788 | -1788 | 0 | Critical Branch | Validation phase | 0 | NA | 295 | 26 | 321 | 1788 | 1 | AT: 425; AT: 168; CH: 8249; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 1630 |  | 8298 | 778 |  | 8003 | 752 | -1788 | -1788 | 0 | Critical Branch | Validation phase | 0 | NA | 295 | 26 | 321 | 1788 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8249; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 1730 |  | 8298 | 778 |  | 8003 | 752 | -1788 | -1788 | 0 | Critical Branch | Validation phase | 0 | NA | 295 | 26 | 321 | 1788 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8249; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 1830 |  | 8445 | 767 |  | 8246 | 755 | -3088 | -3088 | 0 | Critical Branch | Validation phase | 0 | NA | 199 | 12 | 211 | 3088 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8468; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251019 | October | 1930 |  | 8445 | 767 |  | 8246 | 755 | -3088 | -3088 | 0 | Critical Branch | Validation phase | 0 | NA | 199 | 12 | 211 | 3088 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8468; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251019 | October | 2030 |  | 8445 | 767 |  | 8246 | 755 | -3088 | -3088 | 0 | Critical Branch | Validation phase | 0 | NA | 199 | 12 | 211 | 3088 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 168; AT: Reduction because NTC over thermal limit on border; CH: 8468; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 4100; FR: Outage - Busbar 2.1 GENISSIAT
20251019 | October | 2130 | 8023 |  |  | 8022 |  |  | -4491 | -4491 | -4490 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 395; AT: 170
20251019 | October | 2230 | 8023 |  |  | 8022 |  |  | -4491 | -4491 | -4490 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 395; AT: 170
20251019 | October | 2330 | 8023 |  |  | 8022 |  |  | -4491 | -4491 | -4490 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 395; AT: 170
20251020 | October | 0030 | 8222 |  |  | 8222 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0130 | 8222 |  |  | 8222 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0230 | 8222 |  |  | 8222 |  |  | -4493 | -4493 | -4493 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0330 | 7624 |  |  | 7624 |  |  | -3842 | -3842 | -3842 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0430 | 7624 |  |  | 7624 |  |  | -3842 | -3842 | -3842 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0530 | 7624 |  |  | 7624 |  |  | -3842 | -3842 | -3842 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0630 | 7624 |  |  | 7624 |  |  | -3842 | -3842 | -3842 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 0730 |  | 8034 | 685 |  | 7613 | 651 | -2778 | -2778 | 0 | Critical Branch | Validation phase | 0 | NA | 421 | 34 | 455 | 2778 | 1 | CH: 7891; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251020 | October | 0830 |  | 8034 | 685 |  | 7613 | 651 | -2778 | -2778 | 0 | Critical Branch | Validation phase | 0 | NA | 421 | 34 | 455 | 2778 | 1 | CH: 7891; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251020 | October | 0930 | 7698 |  |  | 7698 |  |  | -3552 | -3552 | -3552 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 1030 | 7698 |  |  | 7698 |  |  | -3552 | -3552 | -3552 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251020 | October | 1130 | 7698 |  |  | 7698 |  |  | -3552 | -3552 | -3552 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 7363; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1230 | 8250 |  |  | 7801 |  |  | -4127 | -4127 | -3678 | Critical Branch | Validation phase | 0 | 449 | NA | NA | NA | 0 | 1 | CH: 7466; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1330 | 8250 |  |  | 7801 |  |  | -4127 | -4127 | -3678 | Critical Branch | Validation phase | 0 | 449 | NA | NA | NA | 0 | 1 | CH: 7466; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1430 | 8250 |  |  | 7801 |  |  | -4127 | -4127 | -3678 | Critical Branch | Validation phase | 0 | 449 | NA | NA | NA | 0 | 1 | CH: 7466; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1530 |  | 8157 | 690 |  | 7759 | 658 | -2479 | -2479 | 0 | Critical Branch | Validation phase | 0 | NA | 398 | 32 | 430 | 2479 | 1 | CH: 8197; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1630 |  | 8157 | 690 |  | 7759 | 658 | -2479 | -2479 | 0 | Critical Branch | Validation phase | 0 | NA | 398 | 32 | 430 | 2479 | 1 | CH: 8197; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1730 |  | 8157 | 690 |  | 7759 | 658 | -2479 | -2479 | 0 | Critical Branch | Validation phase | 0 | NA | 398 | 32 | 430 | 2479 | 1 | CH: 8197; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1830 |  | 7632 | 619 |  | 7632 | 619 | -2450 | -2450 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2450 | 0
20251020 | October | 1930 |  | 7632 | 619 |  | 7632 | 619 | -2450 | -2450 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2450 | 0
20251020 | October | 2030 |  | 7632 | 619 |  | 7632 | 619 | -2450 | -2450 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2450 | 0
20251020 | October | 2130 | 8514 |  |  | 7801 |  |  | -2429 | -2429 | -1716 | Critical Branch | Validation phase | 0 | 713 | NA | NA | NA | 0 | 1 | CH: 7466; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 2230 | 8514 |  |  | 7801 |  |  | -2429 | -2429 | -1716 | Critical Branch | Validation phase | 0 | 713 | NA | NA | NA | 0 | 1 | CH: 7466; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 2330 | 7904 |  |  | 7801 |  |  | -1806 | -1806 | -1703 | Critical Branch | Validation phase | 0 | 103 | NA | NA | NA | 0 | 1 | CH: 7471; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251021 | October | 0030 | 7643 |  |  | 6760 |  |  | -3823 | -3823 | -2940 | Critical Branch | Validation phase | 0 | 883 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0130 | 7643 |  |  | 6760 |  |  | -3823 | -3823 | -2940 | Critical Branch | Validation phase | 0 | 883 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0230 | 7643 |  |  | 6760 |  |  | -3823 | -3823 | -2940 | Critical Branch | Validation phase | 0 | 883 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0330 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 0 | 462 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0430 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 0 | 462 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0530 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 0 | 462 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0630 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 0 | 462 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0730 |  | 7734 | 675 |  | 6891 | 675 | -2534 | -2534 | 0 | Critical Branch | Validation phase | 0 | NA | 843 | 0 | 843 | 2534 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0830 |  | 7734 | 675 |  | 6891 | 675 | -2534 | -2534 | 0 | Critical Branch | Validation phase | 0 | NA | 843 | 0 | 843 | 2534 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0930 | 8357 |  |  | 7248 |  |  | -2167 | -2167 | -1058 | Critical Branch | Validation phase | 0 | 1109 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1030 | 8357 |  |  | 7248 |  |  | -2167 | -2167 | -1058 | Critical Branch | Validation phase | 0 | 1109 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1130 | 8357 |  |  | 7248 |  |  | -2167 | -2167 | -1058 | Critical Branch | Validation phase | 0 | 1109 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1230 | 8550 |  |  | 7248 |  |  | -2173 | -2173 | -871 | Critical Branch | Validation phase | 0 | 1302 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1330 | 8550 |  |  | 7248 |  |  | -2173 | -2173 | -871 | Critical Branch | Validation phase | 0 | 1302 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1430 | 8550 |  |  | 7248 |  |  | -2173 | -2173 | -871 | Critical Branch | Validation phase | 0 | 1302 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1530 | 8512 |  |  | 7248 |  |  | -2428 | -2428 | -1164 | Critical Branch | Validation phase | 0 | 1264 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1630 | 8512 |  |  | 7248 |  |  | -2428 | -2428 | -1164 | Critical Branch | Validation phase | 0 | 1264 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1730 | 8512 |  |  | 7248 |  |  | -2428 | -2428 | -1164 | Critical Branch | Validation phase | 0 | 1264 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1830 |  | 7896 | 649 |  | 6884 | 649 | -2730 | -2730 | 0 | Critical Branch | Validation phase | 0 | NA | 1012 | 0 | 1012 | 2730 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1930 |  | 7896 | 649 |  | 6884 | 649 | -2730 | -2730 | 0 | Critical Branch | Validation phase | 0 | NA | 1012 | 0 | 1012 | 2730 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2030 |  | 7896 | 649 |  | 6884 | 649 | -2730 | -2730 | 0 | Critical Branch | Validation phase | 0 | NA | 1012 | 0 | 1012 | 2730 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2130 | 8388 |  |  | 7248 |  |  | -2345 | -2345 | -1205 | Critical Branch | Validation phase | 0 | 1140 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2230 | 8388 |  |  | 7248 |  |  | -2345 | -2345 | -1205 | Critical Branch | Validation phase | 0 | 1140 | NA | NA | NA | 0 | 1 | CH: 6913; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2330 | 7778 |  |  | 6760 |  |  | -1719 | -1719 | -701 | Critical Branch | Validation phase | 0 | 1018 | NA | NA | NA | 0 | 1 | CH: 6430; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251022 | October | 0030 | 9347 |  |  | 6730 |  |  | -5159 | -5159 | -2542 | Critical Branch | Validation phase | 0 | 2617 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0130 | 9347 |  |  | 6730 |  |  | -5159 | -5159 | -2542 | Critical Branch | Validation phase | 0 | 2617 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0230 | 9347 |  |  | 6730 |  |  | -5159 | -5159 | -2542 | Critical Branch | Validation phase | 0 | 2617 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0330 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 0 | 2240 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0430 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 0 | 2240 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0530 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 0 | 2240 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0630 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 0 | 2240 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0730 |  | 9437 | 800 | 7100 |  |  | -3724 | -3724 | -809 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0830 |  | 9437 | 800 | 7100 |  |  | -3724 | -3724 | -809 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0930 | 9561 |  |  | 7100 |  |  | -3407 | -3407 | -946 | Critical Branch | Validation phase | 0 | 2461 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1030 | 9561 |  |  | 7100 |  |  | -3407 | -3407 | -946 | Critical Branch | Validation phase | 0 | 2461 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1130 | 9561 |  |  | 7100 |  |  | -3407 | -3407 | -946 | Critical Branch | Validation phase | 0 | 2461 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1230 | 8099 |  |  | 7100 |  |  | -3737 | -3737 | -2738 | Critical Branch | Validation phase | 0 | 999 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1330 | 8099 |  |  | 7100 |  |  | -3737 | -3737 | -2738 | Critical Branch | Validation phase | 0 | 999 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1430 | 8099 |  |  | 7100 |  |  | -3737 | -3737 | -2738 | Critical Branch | Validation phase | 0 | 999 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1530 |  | 8950 | 760 | 7100 |  |  | -3725 | -3725 | -1209 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1630 |  | 8950 | 760 | 7100 |  |  | -3725 | -3725 | -1209 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1730 |  | 8950 | 760 | 7100 |  |  | -3725 | -3725 | -1209 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1830 |  | 9374 | 775 | 7100 |  |  | -2662 | -2662 | 365 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 3392 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1930 |  | 9374 | 775 | 7100 |  |  | -2662 | -2662 | 365 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 3392 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2030 |  | 9374 | 775 | 7100 |  |  | -2662 | -2662 | 365 | Critical Branch | Validation phase | 0 | NA | NA | NA | NA | 3392 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2130 | 9453 |  |  | 7100 |  |  | -5128 | -5128 | -2775 | Critical Branch | Validation phase | 0 | 2353 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2230 | 9453 |  |  | 7100 |  |  | -5128 | -5128 | -2775 | Critical Branch | Validation phase | 0 | 2353 | NA | NA | NA | 0 | 1 | CH: 6765; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2330 | 8843 |  |  | 6730 |  |  | -4520 | -4520 | -2407 | Critical Branch | Validation phase | 0 | 2113 | NA | NA | NA | 0 | 1 | CH: 6400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4100; FR: Outage - RO S2.1 GENISSIAT 400
20251023 | October | 0030 | 8400 |  |  | 8400 |  |  | -4263 | -4263 | -4263 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251023 | October | 0130 | 8400 |  |  | 8400 |  |  | -4263 | -4263 | -4263 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251023 | October | 0230 | 8400 |  |  | 8400 |  |  | -4263 | -4263 | -4263 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251023 | October | 0330 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 0 | 951 | NA | NA | NA | 0 | 1 | CH: 7691; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0430 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 0 | 951 | NA | NA | NA | 0 | 1 | CH: 7691; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0530 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 0 | 951 | NA | NA | NA | 0 | 1 | CH: 7691; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0630 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 0 | 951 | NA | NA | NA | 0 | 1 | CH: 7691; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0730 |  | 9189 | 655 |  | 8478 | 605 | -4041 | -4041 | 0 | Critical Branch | Validation phase | 0 | NA | 711 | 50 | 761 | 4041 | 1 | CH: 8944; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0830 |  | 9189 | 655 |  | 8478 | 605 | -4041 | -4041 | 0 | Critical Branch | Validation phase | 0 | NA | 711 | 50 | 761 | 4041 | 1 | CH: 8944; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0930 | 9200 |  |  | 8535 |  |  | -3221 | -3221 | -2556 | Critical Branch | Validation phase | 0 | 665 | NA | NA | NA | 0 | 1 | CH: 8285; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1030 | 9200 |  |  | 8535 |  |  | -3221 | -3221 | -2556 | Critical Branch | Validation phase | 0 | 665 | NA | NA | NA | 0 | 1 | CH: 8285; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1130 | 9200 |  |  | 8535 |  |  | -3221 | -3221 | -2556 | Critical Branch | Validation phase | 0 | 665 | NA | NA | NA | 0 | 1 | CH: 8285; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1230 | 8809 |  |  | 8102 |  |  | -4564 | -4564 | -3857 | Critical Branch | Validation phase | 0 | 707 | NA | NA | NA | 0 | 1 | CH: 7852; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1330 | 8809 |  |  | 8102 |  |  | -4564 | -4564 | -3857 | Critical Branch | Validation phase | 0 | 707 | NA | NA | NA | 0 | 1 | CH: 7852; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1430 | 8809 |  |  | 8102 |  |  | -4564 | -4564 | -3857 | Critical Branch | Validation phase | 0 | 707 | NA | NA | NA | 0 | 1 | CH: 7852; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1530 |  | 9196 | 708 |  | 8290 | 644 | -3468 | -3468 | 0 | Critical Branch | Validation phase | 0 | NA | 906 | 64 | 970 | 3468 | 1 | CH: 9323; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1630 |  | 9196 | 708 |  | 8290 | 644 | -3468 | -3468 | 0 | Critical Branch | Validation phase | 0 | NA | 906 | 64 | 970 | 3468 | 1 | CH: 9323; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1730 |  | 9196 | 708 |  | 8290 | 644 | -3468 | -3468 | 0 | Critical Branch | Validation phase | 0 | NA | 906 | 64 | 970 | 3468 | 1 | CH: 9323; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1830 |  | 9019 | 682 |  | 8290 | 630 | -3613 | -3613 | 0 | Critical Branch | Validation phase | 0 | NA | 729 | 52 | 781 | 3613 | 1 | CH: 9139; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1930 |  | 9019 | 682 |  | 8290 | 630 | -3613 | -3613 | 0 | Critical Branch | Validation phase | 0 | NA | 729 | 52 | 781 | 3613 | 1 | CH: 9139; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2030 |  | 9019 | 682 |  | 8290 | 630 | -3613 | -3613 | 0 | Critical Branch | Validation phase | 0 | NA | 729 | 52 | 781 | 3613 | 1 | CH: 9139; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2130 | 9261 |  |  | 8327 |  |  | -2808 | -2808 | -1874 | Critical Branch | Validation phase | 0 | 934 | NA | NA | NA | 0 | 1 | CH: 8077; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2230 | 9261 |  |  | 8327 |  |  | -2808 | -2808 | -1874 | Critical Branch | Validation phase | 0 | 934 | NA | NA | NA | 0 | 1 | CH: 8077; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2330 | 8451 |  |  | 7517 |  |  | -1986 | -1986 | -1052 | Critical Branch | Validation phase | 0 | 934 | NA | NA | NA | 0 | 1 | CH: 7267; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251024 | October | 0030 | 8329 |  |  | 8329 |  |  | -4348 | -4348 | -4348 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0130 | 8329 |  |  | 8329 |  |  | -4348 | -4348 | -4348 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0230 | 8329 |  |  | 8329 |  |  | -4348 | -4348 | -4348 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0330 | 8155 |  |  | 8155 |  |  | -3165 | -3165 | -3165 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0430 | 8155 |  |  | 8155 |  |  | -3165 | -3165 | -3165 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0530 | 8155 |  |  | 8155 |  |  | -3165 | -3165 | -3165 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0630 | 8155 |  |  | 8155 |  |  | -3165 | -3165 | -3165 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0730 | 8367 |  |  | 8367 |  |  | -4446 | -4446 | -4446 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0830 | 8307 |  |  | 8307 |  |  | -4382 | -4382 | -4382 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251024 | October | 0930 | 8430 |  |  | 8143 |  |  | -2516 | -2516 | -2229 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | CH: 7893; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1030 | 8430 |  |  | 8143 |  |  | -2516 | -2516 | -2229 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | CH: 7893; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1130 | 8430 |  |  | 8143 |  |  | -2516 | -2516 | -2229 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | CH: 7893; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1230 | 8726 |  |  | 8143 |  |  | -2524 | -2524 | -1941 | Critical Branch | Validation phase | 0 | 583 | NA | NA | NA | 0 | 1 | CH: 7893; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1330 | 8726 |  |  | 8143 |  |  | -2524 | -2524 | -1941 | Critical Branch | Validation phase | 0 | 583 | NA | NA | NA | 0 | 1 | CH: 7893; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1430 | 8726 |  |  | 8143 |  |  | -2524 | -2524 | -1941 | Critical Branch | Validation phase | 0 | 583 | NA | NA | NA | 0 | 1 | CH: 7893; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1530 |  | 8384 | 740 |  | 8316 | 740 | 2598 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2469 | NA | 68 | 0 | 68 | -129 | 1 | FR: 4050; FR: Process fail during TSO validation phase
20251024 | October | 1630 |  | 8384 | 740 |  | 8316 | 740 | 2598 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2469 | NA | 68 | 0 | 68 | -129 | 1 | FR: 4050; FR: Process fail during TSO validation phase
20251024 | October | 1730 |  | 8384 | 740 |  | 8316 | 740 | 2598 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2469 | NA | 68 | 0 | 68 | -129 | 1 | FR: 4050; FR: Process fail during TSO validation phase
20251024 | October | 1830 |  | 8253 | 724 |  | 8253 | 724 | -3201 | -3201 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3201 | 0
20251024 | October | 1930 |  | 8253 | 724 |  | 8253 | 724 | -3201 | -3201 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3201 | 0
20251024 | October | 2030 |  | 8253 | 724 |  | 8253 | 724 | -3201 | -3201 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3201 | 0
20251024 | October | 2130 | 8995 |  |  | 8546 |  |  | -2349 | -2349 | -1900 | Critical Branch | Validation phase | 0 | 449 | NA | NA | NA | 0 | 1 | CH: 8296; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 2230 | 8995 |  |  | 8546 |  |  | -2349 | -2349 | -1900 | Critical Branch | Validation phase | 0 | 449 | NA | NA | NA | 0 | 1 | CH: 8296; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 2330 | 8385 |  |  | 7936 |  |  | -1739 | -1739 | -1290 | Critical Branch | Validation phase | 0 | 449 | NA | NA | NA | 0 | 1 | CH: 7686; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251025 | October | 0030 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0130 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0230 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0330 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0430 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0530 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0630 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0730 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0830 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 0930 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1030 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1130 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1230 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1330 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1430 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1530 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1630 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1730 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1830 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 1930 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 2030 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 2130 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 2230 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1860 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251025 | October | 2330 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1250 | NA | NA | NA | 0 | 1 | CH: 7450; CH: manual values cause of to high BackUP values
20251026 | October | 0030 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 170
20251026 | October | 0130 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 170
20251026 | October | 0230 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 170
20251026 | October | 0230 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 170
20251026 | October | 0330 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251026 | October | 0430 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251026 | October | 0530 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251026 | October | 0630 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251026 | October | 0730 | 8090 |  |  | 8089 |  |  | -4004 | -4004 | -4003 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 390; AT: 170
20251026 | October | 0830 | 8090 |  |  | 8089 |  |  | -4004 | -4004 | -4003 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 390; AT: 170
20251026 | October | 0930 | 8098 |  |  | 8098 |  |  | -4413 | -4413 | -4413 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 170
20251026 | October | 1030 | 8098 |  |  | 8098 |  |  | -4413 | -4413 | -4413 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 170
20251026 | October | 1130 | 8098 |  |  | 8098 |  |  | -4413 | -4413 | -4413 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 170
20251026 | October | 1230 | 8423 |  |  | 8422 |  |  | -1603 | -1603 | -1602 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 407; AT: 170
20251026 | October | 1330 | 8423 |  |  | 8422 |  |  | -1603 | -1603 | -1602 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 407; AT: 170
20251026 | October | 1430 | 8423 |  |  | 8422 |  |  | -1603 | -1603 | -1602 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 407; AT: 170
20251026 | October | 1530 |  | 8311 | 958 |  | 8311 | 949 | -2825 | -2825 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 2825 | 1 | AT: 271; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251026 | October | 1630 |  | 8311 | 958 |  | 8311 | 949 | -2825 | -2825 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 2825 | 1 | AT: 271; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251026 | October | 1730 |  | 8311 | 958 |  | 8311 | 949 | -2825 | -2825 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 2825 | 1 | AT: 271; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251026 | October | 1830 | 9076 |  |  | 9070 |  |  | -2420 | -2420 | -2414 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251026 | October | 1930 | 9076 |  |  | 9070 |  |  | -2420 | -2420 | -2414 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251026 | October | 2030 | 9076 |  |  | 9070 |  |  | -2420 | -2420 | -2414 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251026 | October | 2130 | 8678 |  |  | 8677 |  |  | -1655 | -1655 | -1654 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 420; AT: 170
20251026 | October | 2230 | 8678 |  |  | 8677 |  |  | -1655 | -1655 | -1654 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 420; AT: 170
20251026 | October | 2330 | 8678 |  |  | 8677 |  |  | -1655 | -1655 | -1654 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 420; AT: 170
20251027 | October | 0030 | 7900 |  |  | 7899 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251027 | October | 0130 | 7900 |  |  | 7899 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251027 | October | 0230 | 7900 |  |  | 7899 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251027 | October | 0330 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 170
20251027 | October | 0430 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 170
20251027 | October | 0530 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 170
20251027 | October | 0630 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 377; AT: 170
20251027 | October | 0730 | 9047 |  |  | 9047 |  |  | -3235 | -3235 | -3235 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155
20251027 | October | 0830 | 9047 |  |  | 9047 |  |  | -3235 | -3235 | -3235 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155
20251027 | October | 0930 | 8990 |  |  | 8990 |  |  | -2287 | -2287 | -2287 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 155
20251027 | October | 1030 | 8990 |  |  | 8990 |  |  | -2287 | -2287 | -2287 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 155
20251027 | October | 1130 | 8990 |  |  | 8990 |  |  | -2287 | -2287 | -2287 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 155
20251027 | October | 1230 | 8435 |  |  | 8435 |  |  | -5107 | -5107 | -5107 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 403; AT: 155
20251027 | October | 1330 | 8435 |  |  | 8435 |  |  | -5107 | -5107 | -5107 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 403; AT: 155
20251027 | October | 1430 | 8435 |  |  | 8435 |  |  | -5107 | -5107 | -5107 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 403; AT: 155
20251027 | October | 1530 |  | 8005 | 741 |  | 8004 | 741 | -1947 | -1947 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1947 | 1 | AT: 418; AT: 153
20251027 | October | 1630 |  | 8005 | 741 |  | 8004 | 741 | -1947 | -1947 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1947 | 1 | AT: 418; AT: 153
20251027 | October | 1730 |  | 8005 | 741 |  | 8004 | 741 | -1947 | -1947 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 1947 | 1 | AT: 418; AT: 153
20251027 | October | 1830 |  | 8918 | 832 |  | 8898 | 832 | -3308 | -3308 | 0 | Critical Branch | Critical Branch | 0 | NA | 20 | 0 | 20 | 3308 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border
20251027 | October | 1930 |  | 8918 | 832 |  | 8898 | 832 | -3308 | -3308 | 0 | Critical Branch | Critical Branch | 0 | NA | 20 | 0 | 20 | 3308 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border
20251027 | October | 2030 |  | 8918 | 832 |  | 8584 | 832 | -3308 | -3308 | 0 | Critical Branch | Critical Branch | 0 | NA | 334 | 0 | 334 | 3308 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border
20251027 | October | 2130 | 7489 |  |  | 7488 |  |  | -3692 | -3692 | -3691 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 354; AT: 155
20251027 | October | 2230 | 7489 |  |  | 7488 |  |  | -3692 | -3692 | -3691 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 354; AT: 155
20251027 | October | 2330 | 6879 |  |  | 6879 |  |  | -3085 | -3085 | -3085 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 336; AT: 170
20251028 | October | 0030 | 7970 |  |  | 7970 |  |  | -1066 | -1066 | -1066 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0130 | 7970 |  |  | 7970 |  |  | -1066 | -1066 | -1066 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0230 | 7970 |  |  | 7970 |  |  | -1066 | -1066 | -1066 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0330 | 8220 |  |  | 8220 |  |  | -1479 | -1479 | -1479 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0430 | 8220 |  |  | 8220 |  |  | -1479 | -1479 | -1479 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0530 | 8220 |  |  | 8220 |  |  | -1479 | -1479 | -1479 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0630 | 8220 |  |  | 8220 |  |  | -1479 | -1479 | -1479 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0730 | 7253 |  |  | 7253 |  |  | -637 | -637 | -637 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0830 | 7253 |  |  | 7253 |  |  | -637 | -637 | -637 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 0930 | 8220 |  |  | 8220 |  |  | -4411 | -4411 | -4411 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1030 | 8220 |  |  | 8220 |  |  | -4411 | -4411 | -4411 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1130 | 8220 |  |  | 8220 |  |  | -4411 | -4411 | -4411 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1230 | 8471 |  |  | 8471 |  |  | -2578 | -2578 | -2578 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1330 | 8471 |  |  | 8471 |  |  | -2578 | -2578 | -2578 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1430 | 8471 |  |  | 8471 |  |  | -2578 | -2578 | -2578 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1530 |  | 7999 | 741 |  | 7996 | 741 | 53 | 53 | 0 | Adjustment reached | Adjustment reached | 0 | NA | 3 | 0 | 3 | -53 | 0
20251028 | October | 1630 |  | 8946 | 737 |  | 8946 | 737 | -1179 | -1179 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 1179 | 0
20251028 | October | 1730 |  | 8946 | 737 |  | 8946 | 737 | -1179 | -1179 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 1179 | 0
20251028 | October | 1830 | 9530 |  |  | 9530 |  |  | -5786 | -5786 | -5786 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 1930 | 9530 |  |  | 9530 |  |  | -5786 | -5786 | -5786 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 2030 | 9530 |  |  | 9530 |  |  | -5786 | -5786 | -5786 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 2130 | 8867 |  |  | 8867 |  |  | -5143 | -5143 | -5143 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 2230 | 8867 |  |  | 8867 |  |  | -5143 | -5143 | -5143 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251028 | October | 2330 | 8057 |  |  | 8057 |  |  | -4334 | -4334 | -4334 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0030 | 7491 |  |  | 7491 |  |  | -3420 | -3420 | -3420 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0130 | 7491 |  |  | 7491 |  |  | -3420 | -3420 | -3420 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0230 | 7491 |  |  | 7491 |  |  | -3420 | -3420 | -3420 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0330 | 7683 |  |  | 7683 |  |  | -3614 | -3614 | -3614 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0430 | 7683 |  |  | 7683 |  |  | -3614 | -3614 | -3614 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0530 | 7683 |  |  | 7683 |  |  | -3614 | -3614 | -3614 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0630 | 7683 |  |  | 7683 |  |  | -3614 | -3614 | -3614 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0730 | 8914 |  |  | 8914 |  |  | -2402 | -2402 | -2402 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0830 | 8914 |  |  | 8914 |  |  | -2402 | -2402 | -2402 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 0930 | 9257 |  |  | 9257 |  |  | -1780 | -1780 | -1780 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 1030 | 9257 |  |  | 9257 |  |  | -1780 | -1780 | -1780 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 1130 | 9257 |  |  | 8886 |  |  | -1780 | -1780 | -1409 | Critical Branch | Smoothing ramp | 0 | 371 | NA | NA | NA | 0 | 1
20251029 | October | 1230 | 7386 |  |  | 7386 |  |  | -2880 | -2880 | -2880 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 1330 | 7386 |  |  | 7386 |  |  | -2880 | -2880 | -2880 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 1430 | 7386 |  |  | 7386 |  |  | -2880 | -2880 | -2880 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 1530 |  | 7847 | 690 |  | 7832 | 690 | 1258 | 235 | 0 | Minimum Margin | Min import NTC Threshold | 1023 | NA | 15 | 0 | 15 | -235 | 0
20251029 | October | 1630 |  | 8706 | 680 |  | 8706 | 680 | 181 | 96 | 0 | Minimum Margin | Minimum Margin | 85 | NA | 0 | 0 | 0 | -96 | 0
20251029 | October | 1730 |  | 8810 | 673 |  | 8810 | 673 | -35 | -35 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 35 | 0
20251029 | October | 1830 |  | 9081 | 726 |  | 9081 | 726 | -2206 | -2206 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2206 | 0
20251029 | October | 1930 |  | 9081 | 726 |  | 9081 | 726 | -2206 | -2206 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2206 | 0
20251029 | October | 2030 |  | 9081 | 726 |  | 9081 | 726 | -2206 | -2206 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2206 | 0
20251029 | October | 2130 | 8426 |  |  | 8426 |  |  | -4353 | -4353 | -4353 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 2230 | 8426 |  |  | 8426 |  |  | -4353 | -4353 | -4353 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251029 | October | 2330 | 7616 |  |  | 7616 |  |  | -3543 | -3543 | -3543 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251030 | October | 0030 | 9842 |  |  | 9838 |  |  | -3172 | -3172 | -3169 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251030 | October | 0130 | 9842 |  |  | 9838 |  |  | -3172 | -3172 | -3169 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251030 | October | 0230 | 9842 |  |  | 9838 |  |  | -3172 | -3172 | -3169 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251030 | October | 0330 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170
20251030 | October | 0430 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170
20251030 | October | 0530 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170
20251030 | October | 0630 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170
20251030 | October | 0730 | 9681 |  |  | 9680 |  |  | -2572 | -2572 | -2571 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155
20251030 | October | 0830 | 8281 |  |  | 8281 |  |  | -1038 | -1038 | -1037 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 404; AT: 155
20251030 | October | 0930 | 7958 |  |  | 7957 |  |  | -4064 | -4064 | -4064 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 155
20251030 | October | 1030 | 7958 |  |  | 7957 |  |  | -4064 | -4064 | -4064 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 155
20251030 | October | 1130 | 7958 |  |  | 7957 |  |  | -4064 | -4064 | -4064 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 155
20251030 | October | 1230 | 7108 |  |  | 7108 |  |  | 4033 | 118 | 3915 | Minimum Margin | Minimum Margin | 3915 | 0 | NA | NA | NA | 7712 | 1 | AT: 343; AT: 155
20251030 | October | 1330 | 7108 |  |  | 7108 |  |  | 4033 | 118 | 3915 | Minimum Margin | Minimum Margin | 3915 | 0 | NA | NA | NA | 7712 | 1 | AT: 343; AT: 155
20251030 | October | 1430 | 7108 |  |  | 7108 |  |  | 4033 | 118 | 3915 | Minimum Margin | Minimum Margin | 3915 | 0 | NA | NA | NA | 7712 | 1 | AT: 343; AT: 155
20251030 | October | 1530 | 8512 |  |  | 8512 |  |  | -414 | -414 | -414 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 416; AT: 155
20251030 | October | 1630 | 8512 |  |  | 8512 |  |  | -414 | -414 | -414 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 416; AT: 155
20251030 | October | 1730 | 8512 |  |  | 8512 |  |  | -414 | -414 | -414 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 416; AT: 155
20251030 | October | 1830 | 8302 |  |  | 8302 |  |  | -2771 | -2771 | -2770 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 155
20251030 | October | 1930 | 8302 |  |  | 8302 |  |  | -2771 | -2771 | -2770 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 155
20251030 | October | 2030 | 8302 |  |  | 8302 |  |  | -2771 | -2771 | -2770 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 155
20251030 | October | 2130 | 8339 |  |  | 8339 |  |  | -1950 | -1950 | -1950 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 407; AT: 155
20251030 | October | 2230 | 8339 |  |  | 8339 |  |  | -1950 | -1950 | -1950 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 407; AT: 155
20251030 | October | 2330 | 7729 |  |  | 7728 |  |  | -1313 | -1313 | -1313 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 390; AT: 170
20251031 | October | 0030 | 7894 |  |  | 7893 |  |  | -4095 | -4095 | -4094 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 399; AT: 170
20251031 | October | 0130 | 7894 |  |  | 7893 |  |  | -4095 | -4095 | -4094 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 399; AT: 170
20251031 | October | 0230 | 7894 |  |  | 7893 |  |  | -4095 | -4095 | -4094 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 399; AT: 170
20251031 | October | 0330 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 0 | 120 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8551; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0430 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 0 | 120 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8551; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0530 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 0 | 120 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8551; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0630 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 0 | 120 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8551; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0730 | 9175 |  |  | 8982 |  |  | -2490 | -2490 | -2297 | Critical Branch | Critical Branch | 0 | 193 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20251031 | October | 0830 | 9175 |  |  | 7482 |  |  | -2490 | -2490 | -949 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1693 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 0930 | 8463 |  |  | 7122 |  |  | -1323 | -1323 | -172 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1341 | NA | NA | NA | 0 | 1 | AT: 413; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 1030 | 8463 |  |  | 7122 |  |  | -1323 | -1323 | -172 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1341 | NA | NA | NA | 0 | 1 | AT: 413; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 1130 | 8463 |  |  | 7122 |  |  | -1323 | -1323 | -172 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1341 | NA | NA | NA | 0 | 1 | AT: 413; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 1230 | 8839 |  |  | 7313 |  |  | -1950 | -1950 | -605 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 433; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 1330 | 8839 |  |  | 7313 |  |  | -1950 | -1950 | -605 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 433; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 1430 | 8839 |  |  | 7313 |  |  | -1950 | -1950 | -605 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 433; AT: 155; IT: 3600; IT: forecasted security violation
20251031 | October | 1530 | 9227 |  |  | 7305 |  |  | -2438 | -2438 | -820 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1922 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 3300; IT: forecasted security violation
20251031 | October | 1630 | 9227 |  |  | 7305 |  |  | -2438 | -2438 | -820 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1922 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 3300; IT: forecasted security violation
20251031 | October | 1730 | 9227 |  |  | 6909 |  |  | -2438 | -2438 | -396 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2318 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 3000; IT: forecasted security violation
20251031 | October | 1830 | 8406 |  |  | 6297 |  |  | -1198 | -1198 | 642 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2109 | NA | NA | NA | 2482 | 1 | AT: 410; AT: 155; IT: 2700; IT: forecasted security violation
20251031 | October | 1930 | 8406 |  |  | 6297 |  |  | -1198 | -1198 | 642 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2109 | NA | NA | NA | 2482 | 1 | AT: 410; AT: 155; IT: 2700; IT: forecasted security violation
20251031 | October | 2030 | 8406 |  |  | 6297 |  |  | -1198 | -1198 | 642 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2109 | NA | NA | NA | 2482 | 1 | AT: 410; AT: 155; IT: 2700; IT: forecasted security violation
20251031 | October | 2130 | 9117 |  |  | 6396 |  |  | -2062 | -2062 | 467 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2721 | NA | NA | NA | 2996 | 1 | AT: 447; AT: 155; IT: 2700; IT: forecasted security violation
20251031 | October | 2230 | 9117 |  |  | 6896 |  |  | -2062 | -2062 | -84 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2221 | NA | NA | NA | 0 | 1 | AT: 447; AT: 155; IT: 3000; IT: forecasted security violation
20251031 | October | 2330 | 8507 |  |  | 6790 |  |  | -1423 | -1423 | 64 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1717 | NA | NA | NA | 1551 | 1 | AT: 432; AT: 170; IT: 3500; IT: forecasted security violation
20251101 | November | 0030 | 7679 |  |  | 7678 |  |  | -4645 | -4645 | -4644 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 170
20251101 | November | 0130 | 7679 |  |  | 7678 |  |  | -4645 | -4645 | -4644 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 170
20251101 | November | 0230 | 7679 |  |  | 7678 |  |  | -4645 | -4645 | -4644 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 387; AT: 170
20251101 | November | 0330 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251101 | November | 0430 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251101 | November | 0530 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251101 | November | 0630 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251101 | November | 0730 | 8025 |  |  | 8024 |  |  | -4699 | -4699 | -4698 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170
20251101 | November | 0830 | 8025 |  |  | 8024 |  |  | -4699 | -4699 | -4698 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 406; AT: 170
20251101 | November | 0930 | 7951 |  |  | 7950 |  |  | -633 | -633 | -632 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251101 | November | 1030 | 7951 |  |  | 7950 |  |  | -633 | -633 | -632 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251101 | November | 1130 | 7951 |  |  | 7950 |  |  | -633 | -633 | -632 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20251101 | November | 1230 | 8272 |  |  | 8271 |  |  | -1580 | -1580 | -1579 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170
20251101 | November | 1330 | 8272 |  |  | 8271 |  |  | -1580 | -1580 | -1579 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170
20251101 | November | 1430 | 8272 |  |  | 8271 |  |  | -1580 | -1580 | -1579 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170
20251101 | November | 1530 | 7446 |  |  | 7446 |  |  | -4287 | -4287 | -4287 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 375; AT: 170
20251101 | November | 1630 | 7446 |  |  | 7446 |  |  | -4287 | -4287 | -4287 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 375; AT: 170
20251101 | November | 1730 | 7446 |  |  | 7446 |  |  | -4287 | -4287 | -4287 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 375; AT: 170
20251101 | November | 1830 | 8865 |  |  | 7501 |  |  | -1830 | -1830 | -425 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1364 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2400; IT: forecasted security violation
20251101 | November | 1930 | 8865 |  |  | 7501 |  |  | -1830 | -1830 | -425 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1364 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2400; IT: forecasted security violation
20251101 | November | 2030 | 8865 |  |  | 7501 |  |  | -1830 | -1830 | -425 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1364 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2400; IT: forecasted security violation
20251101 | November | 2130 | 9115 |  |  | 7521 |  |  | -1907 | -1907 | -274 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1594 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2400; IT: forecasted security violation
20251101 | November | 2230 | 9115 |  |  | 7521 |  |  | -1907 | -1907 | -274 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1594 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2400; IT: forecasted security violation
20251101 | November | 2330 | 9115 |  |  | 8021 |  |  | -1907 | -1907 | -786 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1094 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2600; IT: forecasted security violation
20251102 | November | 0030 | 9073 |  |  | 7179 |  |  | -2119 | -2119 | -225 | Critical Branch | Validation phase | 0 | 1894 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6929; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0130 | 9073 |  |  | 7179 |  |  | -2119 | -2119 | -225 | Critical Branch | Validation phase | 0 | 1894 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6929; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0230 | 9073 |  |  | 7179 |  |  | -2119 | -2119 | -225 | Critical Branch | Validation phase | 0 | 1894 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6929; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0330 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 0 | 1065 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0430 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 0 | 1065 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0530 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 0 | 1065 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0630 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 0 | 1065 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0730 | 7669 |  |  | 7525 |  |  | -4190 | -4190 | -4046 | Critical Branch | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 397; AT: 170; CH: 7275; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0830 | 7669 |  |  | 7525 |  |  | -4190 | -4190 | -4046 | Critical Branch | Validation phase | 0 | 144 | NA | NA | NA | 0 | 1 | AT: 397; AT: 170; CH: 7275; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0930 | 9063 |  |  | 7451 |  |  | -1765 | -1765 | -153 | Critical Branch | Validation phase | 0 | 1612 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7201; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1030 | 9063 |  |  | 7451 |  |  | -1765 | -1765 | -153 | Critical Branch | Validation phase | 0 | 1612 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7201; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1130 | 9063 |  |  | 7451 |  |  | -1765 | -1765 | -153 | Critical Branch | Validation phase | 0 | 1612 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7201; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1230 | 8920 |  |  | 7772 |  |  | -2033 | -2033 | -885 | Critical Branch | Validation phase | 0 | 1148 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7522; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1330 | 8920 |  |  | 7772 |  |  | -2033 | -2033 | -885 | Critical Branch | Validation phase | 0 | 1148 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7522; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1430 | 8920 |  |  | 7772 |  |  | -2033 | -2033 | -885 | Critical Branch | Validation phase | 0 | 1148 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7522; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1530 | 7969 |  |  | 6946 |  |  | -4507 | -4507 | -3484 | Critical Branch | Validation phase | 0 | 1023 | NA | NA | NA | 0 | 1 | AT: 413; AT: 170; CH: 6696; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1630 | 7969 |  |  | 6946 |  |  | -4507 | -4507 | -3484 | Critical Branch | Validation phase | 0 | 1023 | NA | NA | NA | 0 | 1 | AT: 413; AT: 170; CH: 6696; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2500; IT: forecasted security violation
20251102 | November | 1730 | 7969 |  |  | 6946 |  |  | -4507 | -4507 | -3484 | Critical Branch | Validation phase | 0 | 1023 | NA | NA | NA | 0 | 1 | AT: 413; AT: 170; CH: 6696; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251102 | November | 1830 | 8211 |  |  | 7307 |  |  | -4647 | -4647 | -3745 | Critical Branch | Validation phase | 0 | 904 | NA | NA | NA | 0 | 1 | AT: 427; AT: 170; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251102 | November | 1930 | 8211 |  |  | 7307 |  |  | -4647 | -4647 | -3745 | Critical Branch | Validation phase | 0 | 904 | NA | NA | NA | 0 | 1 | AT: 427; AT: 170; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251102 | November | 2030 | 8211 |  |  | 7307 |  |  | -4647 | -4647 | -3745 | Critical Branch | Validation phase | 0 | 904 | NA | NA | NA | 0 | 1 | AT: 427; AT: 170; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251102 | November | 2130 | 8525 |  |  | 7307 |  |  | -5497 | -5497 | -4281 | Critical Branch | Validation phase | 0 | 1218 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251102 | November | 2230 | 8525 |  |  | 7307 |  |  | -5497 | -5497 | -4281 | Critical Branch | Validation phase | 0 | 1218 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251102 | November | 2330 | 8725 |  |  | 7809 |  |  | -5703 | -5703 | -4776 | Critical Branch | Validation phase | 0 | 916 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 7800; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2500; IT: forecasted security violation
20251103 | November | 0030 | 7844 |  |  | 7115 |  |  | -3118 | -3118 | -2376 | Critical Branch | Validation phase | 0 | 729 | NA | NA | NA | 0 | 1 | AT: 396; AT: 170; CH: 7094; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0130 | 7844 |  |  | 7115 |  |  | -3118 | -3118 | -2376 | Critical Branch | Validation phase | 0 | 729 | NA | NA | NA | 0 | 1 | AT: 396; AT: 170; CH: 7094; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0230 | 7844 |  |  | 7115 |  |  | -3118 | -3118 | -2376 | Critical Branch | Validation phase | 0 | 729 | NA | NA | NA | 0 | 1 | AT: 396; AT: 170; CH: 7094; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0330 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 374; AT: 170; CH: 6682; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0430 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 374; AT: 170; CH: 6682; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0530 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 374; AT: 170; CH: 6682; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0630 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 374; AT: 170; CH: 6682; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251103 | November | 0730 | 8523 |  |  | 7176 |  |  | -3779 | -3779 | -2405 | Critical Branch | Validation phase | 0 | 1347 | NA | NA | NA | 0 | 1 | AT: 416; AT: 155; CH: 7275; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2400; IT: forecasted security violation
20251103 | November | 0830 | 8523 |  |  | 7525 |  |  | -3779 | -3779 | -2781 | Critical Branch | Validation phase | 0 | 998 | NA | NA | NA | 0 | 1 | AT: 416; AT: 155; CH: 7275; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 0930 | 8222 |  |  | 7451 |  |  | -3618 | -3618 | -2847 | Critical Branch | Validation phase | 0 | 771 | NA | NA | NA | 0 | 1 | AT: 401; AT: 155; CH: 7201; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 1030 | 8222 |  |  | 7451 |  |  | -3618 | -3618 | -2847 | Critical Branch | Validation phase | 0 | 771 | NA | NA | NA | 0 | 1 | AT: 401; AT: 155; CH: 7201; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 1130 | 8222 |  |  | 7451 |  |  | -3618 | -3618 | -2847 | Critical Branch | Validation phase | 0 | 771 | NA | NA | NA | 0 | 1 | AT: 401; AT: 155; CH: 7201; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 1230 | 8884 |  |  | 7610 |  |  | -2192 | -2192 | -916 | Critical Branch | Validation phase | 0 | 1274 | NA | NA | NA | 0 | 1 | AT: 435; AT: 155; CH: 7522; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 1330 | 8884 |  |  | 7610 |  |  | -2192 | -2192 | -916 | Critical Branch | Validation phase | 0 | 1274 | NA | NA | NA | 0 | 1 | AT: 435; AT: 155; CH: 7522; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 1430 | 8884 |  |  | 7610 |  |  | -2192 | -2192 | -916 | Critical Branch | Validation phase | 0 | 1274 | NA | NA | NA | 0 | 1 | AT: 435; AT: 155; CH: 7522; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2600; IT: forecasted security violation
20251103 | November | 1530 |  | 8676 | 832 |  | 6402 | 832 | -2878 | -2878 | 0 | Critical Branch | Validation phase | 0 | NA | 2274 | 0 | 2274 | 2878 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border; CH: 6696; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2400; IT: forecasted security violation
20251103 | November | 1630 |  | 8676 | 832 |  | 6402 | 832 | -2878 | -2878 | 0 | Critical Branch | Validation phase | 0 | NA | 2274 | 0 | 2274 | 2878 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border; CH: 6696; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2400; IT: forecasted security violation
20251103 | November | 1730 |  | 8676 | 832 |  | 6002 | 832 | -2878 | -2878 | 0 | Critical Branch | Validation phase | 0 | NA | 2674 | 0 | 2674 | 2878 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border; CH: 6696; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2200; IT: forecasted security violation
20251103 | November | 1830 | 8771 |  |  | 6221 |  |  | -1945 | -1945 | 643 | Critical Branch | Validation phase | 0 | 2550 | NA | NA | NA | 3231 | 1 | AT: 429; AT: 155; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2000; IT: forecasted security violation
20251103 | November | 1930 | 8771 |  |  | 6221 |  |  | -1945 | -1945 | 643 | Critical Branch | Validation phase | 0 | 2550 | NA | NA | NA | 3231 | 1 | AT: 429; AT: 155; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2000; IT: forecasted security violation
20251103 | November | 2030 | 8771 |  |  | 6221 |  |  | -1945 | -1945 | 643 | Critical Branch | Validation phase | 0 | 2550 | NA | NA | NA | 3231 | 1 | AT: 429; AT: 155; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2000; IT: forecasted security violation
20251103 | November | 2130 | 8745 |  |  | 6221 |  |  | -2089 | -2089 | 477 | Critical Branch | Validation phase | 0 | 2524 | NA | NA | NA | 3043 | 1 | AT: 428; AT: 155; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2000; IT: forecasted security violation
20251103 | November | 2230 | 8745 |  |  | 6621 |  |  | -2089 | -2089 | 54 | Critical Branch | Validation phase | 0 | 2124 | NA | NA | NA | 2197 | 1 | AT: 428; AT: 155; CH: 7600; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2200; IT: forecasted security violation
20251103 | November | 2330 | 8135 |  |  | 7154 |  |  | -1450 | -1450 | -450 | Critical Branch | Validation phase | 0 | 981 | NA | NA | NA | 0 | 1 | AT: 412; AT: 170; CH: 7385; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; IT: 2300; IT: forecasted security violation
20251104 | November | 0030 | 9311 |  |  | 7332 |  |  | -2343 | -2343 | -305 | Critical Branch | Validation phase | 0 | 1979 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 9007; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2300; IT: forecasted security violation
20251104 | November | 0130 | 9311 |  |  | 7332 |  |  | -2343 | -2343 | -305 | Critical Branch | Validation phase | 0 | 1979 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 9007; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2300; IT: forecasted security violation
20251104 | November | 0230 | 9311 |  |  | 7332 |  |  | -2343 | -2343 | -305 | Critical Branch | Validation phase | 0 | 1979 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 9007; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2300; IT: forecasted security violation
20251104 | November | 0330 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1714 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2300; IT: forecasted security violation
20251104 | November | 0430 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1714 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2300; IT: forecasted security violation
20251104 | November | 0530 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1714 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2300; IT: forecasted security violation
20251104 | November | 0630 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1714 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2300; IT: forecasted security violation
20251104 | November | 0730 | 9323 |  |  | 7417 |  |  | -4846 | -4846 | -2825 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1906 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2400; IT: forecasted security violation
20251104 | November | 0830 | 9323 |  |  | 7817 |  |  | -4846 | -4846 | -3235 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1506 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2600; IT: forecasted security violation
20251104 | November | 0930 | 9131 |  |  | 7793 |  |  | -2287 | -2287 | -919 | Critical Branch | Validation phase | 0 | 1338 | NA | NA | NA | 0 | 1 | AT: 448; AT: 155; CH: 8840; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; IT: 2600; IT: forecasted security violation
20251104 | November | 1030 | 9131 |  |  | 7793 |  |  | -2287 | -2287 | -919 | Critical Branch | Validation phase | 0 | 1338 | NA | NA | NA | 0 | 1 | AT: 448; AT: 155; CH: 8840; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; IT: 2600; IT: forecasted security violation
20251104 | November | 1130 | 9131 |  |  | 7793 |  |  | -2287 | -2287 | -919 | Critical Branch | Validation phase | 0 | 1338 | NA | NA | NA | 0 | 1 | AT: 448; AT: 155; CH: 8840; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; IT: 2600; IT: forecasted security violation
20251104 | November | 1230 | 9381 |  |  | 7774 |  |  | -2626 | -2626 | -988 | Critical Branch | Validation phase | 0 | 1607 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 8702; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA; IT: 2600; IT: forecasted security violation
20251104 | November | 1330 | 9381 |  |  | 7774 |  |  | -2626 | -2626 | -988 | Critical Branch | Validation phase | 0 | 1607 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 8702; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA; IT: 2600; IT: forecasted security violation
20251104 | November | 1430 | 9381 |  |  | 7774 |  |  | -2626 | -2626 | -988 | Critical Branch | Validation phase | 0 | 1607 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 8702; CH: Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA; IT: 2600; IT: forecasted security violation
20251104 | November | 1530 | 9171 |  |  | 7255 |  |  | -4314 | -4314 | -2279 | Critical Branch | Validation phase | 0 | 1916 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 8563; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2400; IT: forecasted security violation
20251104 | November | 1630 | 9171 |  |  | 7255 |  |  | -4314 | -4314 | -2279 | Critical Branch | Validation phase | 0 | 1916 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 8563; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2400; IT: forecasted security violation
20251104 | November | 1730 | 9171 |  |  | 6855 |  |  | -4314 | -4314 | -1868 | Critical Branch | Validation phase | 0 | 2316 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 8563; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2200; IT: forecasted security violation
20251104 | November | 1830 | 9376 |  |  | 6422 |  |  | -2992 | -2992 | 31 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2954 | NA | NA | NA | 3054 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2000; IT: forecasted security violation
20251104 | November | 1930 | 9376 |  |  | 6422 |  |  | -2992 | -2992 | 31 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2954 | NA | NA | NA | 3054 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2000; IT: forecasted security violation
20251104 | November | 2030 | 9376 |  |  | 6422 |  |  | -2992 | -2992 | 31 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2954 | NA | NA | NA | 3054 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2000; IT: forecasted security violation
20251104 | November | 2130 | 9366 |  |  | 6421 |  |  | -2224 | -2224 | 801 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2945 | NA | NA | NA | 3826 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2000; IT: forecasted security violation
20251104 | November | 2230 | 9366 |  |  | 6821 |  |  | -2224 | -2224 | 375 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2545 | NA | NA | NA | 2974 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2200; IT: forecasted security violation
20251104 | November | 2330 | 8756 |  |  | 7292 |  |  | -1574 | -1574 | -66 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1464 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; IT: 2300; IT: forecasted security violation
20251105 | November | 0030 | 8922 |  |  | 7502 |  |  | -2082 | -2082 | -620 | Critical Branch | Validation phase | 0 | 1420 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8624; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; IT: 2400; IT: forecasted security violation
20251105 | November | 0130 | 8922 |  |  | 7502 |  |  | -2082 | -2082 | -620 | Critical Branch | Validation phase | 0 | 1420 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8624; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; IT: 2400; IT: forecasted security violation
20251105 | November | 0230 | 8922 |  |  | 7502 |  |  | -2082 | -2082 | -620 | Critical Branch | Validation phase | 0 | 1420 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8624; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; IT: 2400; IT: forecasted security violation
20251105 | November | 0330 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 0 | 1290 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8024; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2400; IT: forecasted security violation
20251105 | November | 0430 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 0 | 1290 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8024; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2400; IT: forecasted security violation
20251105 | November | 0530 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 0 | 1290 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8024; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2400; IT: forecasted security violation
20251105 | November | 0630 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 0 | 1290 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8024; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2400; IT: forecasted security violation
20251105 | November | 0730 | 8105 |  |  | 7456 |  |  | -1415 | -1415 | -788 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 649 | NA | NA | NA | 0 | 1 | AT: 395; AT: 155; IT: 2400; IT: forecasted security violation
20251105 | November | 0830 | 8105 |  |  | 7756 |  |  | -1415 | -1415 | -1065 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 395; AT: 155; IT: 2600; IT: forecasted security violation
20251105 | November | 0930 | 8666 |  |  | 7827 |  |  | -3689 | -3689 | -2798 | Critical Branch | Validation phase | 0 | 839 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155; CH: 8364; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2600; IT: forecasted security violation
20251105 | November | 1030 | 8666 |  |  | 7827 |  |  | -3689 | -3689 | -2798 | Critical Branch | Validation phase | 0 | 839 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155; CH: 8364; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2600; IT: forecasted security violation
20251105 | November | 1130 | 8666 |  |  | 7827 |  |  | -3689 | -3689 | -2798 | Critical Branch | Validation phase | 0 | 839 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155; CH: 8364; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2600; IT: forecasted security violation
20251105 | November | 1230 | 8858 |  |  | 7810 |  |  | -2533 | -2533 | -1447 | Critical Branch | Validation phase | 0 | 1048 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155; CH: 8243; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2600; IT: forecasted security violation
20251105 | November | 1330 | 8858 |  |  | 7810 |  |  | -2533 | -2533 | -1447 | Critical Branch | Validation phase | 0 | 1048 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155; CH: 8243; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2600; IT: forecasted security violation
20251105 | November | 1430 | 8858 |  |  | 7810 |  |  | -2533 | -2533 | -1447 | Critical Branch | Validation phase | 0 | 1048 | NA | NA | NA | 0 | 1 | AT: 434; AT: 155; CH: 8243; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2600; IT: forecasted security violation
20251105 | November | 1530 | 8435 |  |  | 7602 |  |  | -3551 | -3551 | -2748 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 833 | NA | NA | NA | 0 | 1 | AT: 412; AT: 155; IT: 2400; IT: forecasted security violation
20251105 | November | 1630 | 8435 |  |  | 7302 |  |  | -3551 | -3551 | -2355 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1133 | NA | NA | NA | 0 | 1 | AT: 412; AT: 155; IT: 2400; IT: forecasted security violation
20251105 | November | 1730 | 9835 |  |  | 6657 |  |  | -4787 | -4787 | -1618 | Critical Branch | Validation phase | 0 | 3178 | NA | NA | NA | 0 | 1 | AT: 417; AT: 155; CH: 8250; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano; IT: 2500; IT: forecasted security violation
20251105 | November | 1830 | 10465 |  |  | 6721 |  |  | -2887 | -2887 | 904 | Critical Branch | Validation phase | 0 | 3744 | NA | NA | NA | 4695 | 1 | AT: 445; AT: 155; CH: 8786; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2700; IT: forecasted security violation
20251105 | November | 1930 | 10465 |  |  | 6721 |  |  | -2887 | -2887 | 904 | Critical Branch | Validation phase | 0 | 3744 | NA | NA | NA | 4695 | 1 | AT: 445; AT: 155; CH: 8786; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2700; IT: forecasted security violation
20251105 | November | 2030 | 10465 |  |  | 6721 |  |  | -2887 | -2887 | 904 | Critical Branch | Validation phase | 0 | 3744 | NA | NA | NA | 4695 | 1 | AT: 441; AT: 155; CH: 8786; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 2700; IT: forecasted security violation
20251105 | November | 2130 | 8864 |  |  | 6700 |  |  | -3958 | -3958 | -1685 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2164 | NA | NA | NA | 0 | 1 | AT: 374; AT: 155; IT: 2700; IT: forecasted security violation
20251105 | November | 2230 | 8864 |  |  | 7300 |  |  | -3958 | -3958 | -2303 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1564 | NA | NA | NA | 0 | 1 | AT: 374; AT: 155; IT: 2900; IT: forecasted security violation
20251105 | November | 2330 | 8054 |  |  | 7178 |  |  | -3149 | -3149 | -2212 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 876 | NA | NA | NA | 0 | 1 | AT: 355; AT: 170; IT: 2700; IT: forecasted security violation
20251106 | November | 0030 | 9379 |  |  | 7432 |  |  | -4635 | -4635 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1947 | NA | NA | NA | 0 | 1 | AT: 417; AT: 170; IT: 2900; IT: forecasted security violation
20251106 | November | 0130 | 9379 |  |  | 7432 |  |  | -4635 | -4635 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1947 | NA | NA | NA | 0 | 1 | AT: 417; AT: 170; IT: 2900; IT: forecasted security violation
20251106 | November | 0230 | 9379 |  |  | 7432 |  |  | -4635 | -4635 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1947 | NA | NA | NA | 0 | 1 | AT: 417; AT: 170; IT: 2900; IT: forecasted security violation
20251106 | November | 0330 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1643 | NA | NA | NA | 0 | 1 | AT: 401; AT: 170; IT: 2900; IT: forecasted security violation
20251106 | November | 0430 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1643 | NA | NA | NA | 0 | 1 | AT: 401; AT: 170; IT: 2900; IT: forecasted security violation
20251106 | November | 0530 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1643 | NA | NA | NA | 0 | 1 | AT: 401; AT: 170; IT: 2900; IT: forecasted security violation
20251106 | November | 0630 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1643 | NA | NA | NA | 0 | 1 | AT: 401; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; IT: 2900; IT: forecasted security violation
20251106 | November | 0730 | 9620 |  |  | 7490 |  |  | -1636 | -1636 | 620 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2130 | NA | NA | NA | 2876 | 1 | AT: 407; AT: 155; IT: 2900; IT: forecasted security violation
20251106 | November | 0830 | 9620 |  |  | 7790 |  |  | -1636 | -1636 | 252 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1830 | NA | NA | NA | 2140 | 1 | AT: 407; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 0930 | 9301 |  |  | 7752 |  |  | -4813 | -4813 | -3185 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1549 | NA | NA | NA | 0 | 1 | AT: 393; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 1030 | 9301 |  |  | 7752 |  |  | -4813 | -4813 | -3185 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1549 | NA | NA | NA | 0 | 1 | AT: 393; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 1130 | 9301 |  |  | 7752 |  |  | -4813 | -4813 | -3185 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1549 | NA | NA | NA | 0 | 1 | AT: 393; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 1230 | 10282 |  |  | 7869 |  |  | -5061 | -5061 | -2533 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2413 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 1330 | 10282 |  |  | 7869 |  |  | -5061 | -5061 | -2533 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2413 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 1430 | 10282 |  |  | 7869 |  |  | -5061 | -5061 | -2533 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2413 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; IT: 3200; IT: forecasted security violation
20251106 | November | 1530 | 9837 |  |  | 7792 |  |  | -2915 | -2915 | -806 | Critical Branch | Validation phase | 0 | 2045 | NA | NA | NA | 0 | 1 | AT: 417; AT: 155; CH: 9378; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 3200; IT: forecasted security violation
20251106 | November | 1630 | 9837 |  |  | 7392 |  |  | -2915 | -2915 | -394 | Critical Branch | Validation phase | 0 | 2445 | NA | NA | NA | 0 | 1 | AT: 417; AT: 155; CH: 9378; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano; IT: 3000; IT: forecasted security violation
20251106 | November | 1730 | 9837 |  |  | 8892 |  |  | -2915 | -2915 | -1970 | Critical Branch | Smoothing ramp | 0 | 945 | NA | NA | NA | 0 | 1 | AT: 417; AT: 155; CH: 9378; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano
20251106 | November | 1830 | 10049 |  |  | 9762 |  |  | -3084 | -3084 | -2797 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 427; AT: 155; CH: 9512; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251106 | November | 1930 | 10049 |  |  | 9762 |  |  | -3084 | -3084 | -2797 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 427; AT: 155; CH: 9512; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2030 | 10049 |  |  | 9762 |  |  | -3084 | -3084 | -2797 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 427; AT: 155; CH: 9512; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2130 | 9940 |  |  | 9562 |  |  | -4009 | -4009 | -3631 | Critical Branch | Validation phase | 0 | 378 | NA | NA | NA | 0 | 1 | AT: 422; AT: 155; CH: 9312; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2230 | 9940 |  |  | 9562 |  |  | -4009 | -4009 | -3631 | Critical Branch | Validation phase | 0 | 378 | NA | NA | NA | 0 | 1 | AT: 422; AT: 155; CH: 9312; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2330 | 9130 |  |  | 8752 |  |  | -3195 | -3195 | -2817 | Critical Branch | Validation phase | 0 | 378 | NA | NA | NA | 0 | 1 | AT: 405; AT: 170; CH: 8502; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0030 | 9681 |  |  | 8904 |  |  | -4320 | -4320 | -3543 | Critical Branch | Validation phase | 0 | 777 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170; CH: 8654; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0130 | 9681 |  |  | 8904 |  |  | -4320 | -4320 | -3543 | Critical Branch | Validation phase | 0 | 777 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170; CH: 8654; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0230 | 9681 |  |  | 8904 |  |  | -4320 | -4320 | -3543 | Critical Branch | Validation phase | 0 | 777 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170; CH: 8654; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0330 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 0 | 844 | NA | NA | NA | 0 | 1 | AT: 433; AT: 170; CH: 8623; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0430 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 0 | 844 | NA | NA | NA | 0 | 1 | AT: 433; AT: 170; CH: 8623; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0530 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 0 | 844 | NA | NA | NA | 0 | 1 | AT: 433; AT: 170; CH: 8623; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0630 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 0 | 844 | NA | NA | NA | 0 | 1 | AT: 433; AT: 170; CH: 8623; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0730 | 9949 |  |  | 8400 |  |  | -2896 | -2896 | -1347 | Critical Branch | Validation phase | 0 | 1549 | NA | NA | NA | 0 | 1 | AT: 422; AT: 155; CH: 8150; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0830 | 9949 |  |  | 8400 |  |  | -2896 | -2896 | -1347 | Critical Branch | Validation phase | 0 | 1549 | NA | NA | NA | 0 | 1 | AT: 422; AT: 155; CH: 8150; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0930 | 9670 |  |  | 8269 |  |  | -2567 | -2567 | -1166 | Critical Branch | Validation phase | 0 | 1401 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155; CH: 8019; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1030 | 9670 |  |  | 8269 |  |  | -2567 | -2567 | -1166 | Critical Branch | Validation phase | 0 | 1401 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155; CH: 8019; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1130 | 9670 |  |  | 8269 |  |  | -2567 | -2567 | -1166 | Critical Branch | Validation phase | 0 | 1401 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155; CH: 8019; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1230 | 8814 |  |  | 7941 |  |  | -2686 | -2686 | -1813 | Critical Branch | Validation phase | 0 | 873 | NA | NA | NA | 0 | 1 | AT: 371; AT: 155; CH: 7691; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1330 | 8814 |  |  | 7941 |  |  | -2686 | -2686 | -1813 | Critical Branch | Validation phase | 0 | 873 | NA | NA | NA | 0 | 1 | AT: 371; AT: 155; CH: 7691; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1430 | 8814 |  |  | 7941 |  |  | -2686 | -2686 | -1813 | Critical Branch | Validation phase | 0 | 873 | NA | NA | NA | 0 | 1 | AT: 371; AT: 155; CH: 7691; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1530 |  | 9970 | 766 |  | 9049 | 727 | -2911 | -2911 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 921 | 39 | 960 | 2911 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; CH: 9949; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251107 | November | 1630 |  | 9970 | 766 |  | 9423 | 727 | -2911 | -2911 | 0 | Critical Branch | Validation phase | 0 | NA | 547 | 39 | 586 | 2911 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; CH: 9949; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251107 | November | 1730 |  | 9970 | 766 |  | 9423 | 727 | -2911 | -2911 | 0 | Critical Branch | Validation phase | 0 | NA | 547 | 39 | 586 | 2911 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border; CH: 9949; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251107 | November | 1830 |  | 10205 | 801 |  | 9943 | 783 | -5645 | -5645 | 0 | Critical Branch | Validation phase | 0 | NA | 262 | 18 | 280 | 5645 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 10371; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251107 | November | 1930 |  | 10205 | 801 |  | 9943 | 783 | -5645 | -5645 | 0 | Critical Branch | Validation phase | 0 | NA | 262 | 18 | 280 | 5645 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 10371; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251107 | November | 2030 |  | 10205 | 801 |  | 9321 | 783 | -5645 | -5645 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 884 | 18 | 902 | 5645 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border; CH: 10371; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251107 | November | 2130 | 10336 |  |  | 8212 |  |  | -2945 | -2945 | -821 | Critical Branch | Validation phase | 0 | 2124 | NA | NA | NA | 0 | 1 | AT: 439; AT: 155; CH: 7962; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 2230 | 10336 |  |  | 8212 |  |  | -2945 | -2945 | -821 | Critical Branch | Validation phase | 0 | 2124 | NA | NA | NA | 0 | 1 | AT: 439; AT: 155; CH: 7962; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 2330 | 9526 |  |  | 7402 |  |  | -2120 | -2120 | 4 | Critical Branch | Validation phase | 0 | 2124 | NA | NA | NA | 2128 | 1 | AT: 424; AT: 170; CH: 7152; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0030 | 10754 |  |  | 8914 |  |  | -5430 | -5430 | -3590 | Critical Branch | Validation phase | 0 | 1840 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8664; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0130 | 10754 |  |  | 8914 |  |  | -5430 | -5430 | -3590 | Critical Branch | Validation phase | 0 | 1840 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8664; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0230 | 10754 |  |  | 8669 |  |  | -5430 | -5430 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2085 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 8664; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0330 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 0 | 3378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6919; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0430 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 0 | 3378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6919; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0530 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 0 | 3378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6919; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0630 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 0 | 3378 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; CH: 6919; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0730 | 10563 |  |  | 8669 |  |  | -2881 | -2881 | -987 | Critical Branch | Smoothing ramp | 0 | 1894 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 9737; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0830 | 10563 |  |  | 9987 |  |  | -2881 | -2881 | -2305 | Critical Branch | Validation phase | 0 | 576 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 9737; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0930 | 9265 |  |  | 9104 |  |  | -3944 | -3944 | -3783 | Critical Branch | Validation phase | 0 | 161 | NA | NA | NA | 0 | 1 | AT: 392; AT: 155; CH: 8854; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1030 | 9265 |  |  | 9104 |  |  | -3944 | -3944 | -3783 | Critical Branch | Validation phase | 0 | 161 | NA | NA | NA | 0 | 1 | AT: 392; AT: 155; CH: 8854; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1130 | 9265 |  |  | 9104 |  |  | -3944 | -3944 | -3783 | Critical Branch | Validation phase | 0 | 161 | NA | NA | NA | 0 | 1 | AT: 392; AT: 155; CH: 8854; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1230 | 9532 |  |  | 8899 |  |  | -3952 | -3952 | -3319 | Critical Branch | Validation phase | 0 | 633 | NA | NA | NA | 0 | 1 | AT: 404; AT: 155; CH: 8649; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1330 | 9532 |  |  | 8899 |  |  | -3952 | -3952 | -3319 | Critical Branch | Validation phase | 0 | 633 | NA | NA | NA | 0 | 1 | AT: 404; AT: 155; CH: 8649; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1430 | 9532 |  |  | 8899 |  |  | -3952 | -3952 | -3319 | Critical Branch | Validation phase | 0 | 633 | NA | NA | NA | 0 | 1 | AT: 404; AT: 155; CH: 8649; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1530 |  | 10286 | 815 |  | 9990 | 815 | -5861 | -5861 | 0 | Critical Branch | Critical Branch | 0 | NA | 296 | 0 | 296 | 5861 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border
20251108 | November | 1630 |  | 10286 | 815 |  | 10261 | 815 | -5861 | -5861 | 0 | Critical Branch | Critical Branch | 0 | NA | 25 | 0 | 25 | 5861 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border
20251108 | November | 1730 |  | 10286 | 815 |  | 10261 | 815 | -5861 | -5861 | 0 | Critical Branch | Critical Branch | 0 | NA | 25 | 0 | 25 | 5861 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 150; AT: Reduction because NTC over thermal limit on border
20251108 | November | 1830 | 10279 |  |  | 9756 |  |  | -2820 | -2820 | -2297 | Critical Branch | Validation phase | 0 | 523 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; CH: 9506; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251108 | November | 1930 | 10279 |  |  | 9756 |  |  | -2820 | -2820 | -2297 | Critical Branch | Validation phase | 0 | 523 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; CH: 9506; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251108 | November | 2030 | 10279 |  |  | 9756 |  |  | -2820 | -2820 | -2297 | Critical Branch | Validation phase | 0 | 523 | NA | NA | NA | 0 | 1 | AT: 437; AT: 155; CH: 9506; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251108 | November | 2130 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251108 | November | 2230 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251108 | November | 2330 | 9750 |  |  | 7738 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; CH: 7488; CH: D2CC failed. Correction of BackUp-values.
20251109 | November | 0030 | 10534 |  |  | 10497 |  |  | -5174 | -5174 | -5142 | Critical Branch | Critical Branch | 0 | 37 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0130 | 10534 |  |  | 10497 |  |  | -5174 | -5174 | -5142 | Critical Branch | Critical Branch | 0 | 37 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0230 | 10534 |  |  | 10497 |  |  | -5174 | -5174 | -5142 | Critical Branch | Critical Branch | 0 | 37 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0330 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | 0 | NA | 7 | 0 | 7 | 1190 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 162; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0430 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | 0 | NA | 7 | 0 | 7 | 1190 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 162; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0530 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | 0 | NA | 7 | 0 | 7 | 1190 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 162; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0630 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | 0 | NA | 7 | 0 | 7 | 1190 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 162; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0730 | 10325 |  |  | 10298 |  |  | -5501 | -5501 | -5481 | Critical Branch | Critical Branch | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0830 | 10325 |  |  | 10298 |  |  | -5501 | -5501 | -5481 | Critical Branch | Critical Branch | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 0930 |  | 9395 | 783 |  | 9379 | 783 | -4175 | -4175 | 0 | Critical Branch | Critical Branch | 0 | NA | 16 | 0 | 16 | 4175 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border
20251109 | November | 1030 |  | 9395 | 783 |  | 9379 | 783 | -4175 | -4175 | 0 | Critical Branch | Critical Branch | 0 | NA | 16 | 0 | 16 | 4175 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 167; AT: Reduction because NTC over thermal limit on border
20251109 | November | 1130 |  | 9395 | 783 |  | 8758 | 783 | -4175 | -4175 | 0 | Critical Branch | Critical Branch | 0 | NA | 637 | 0 | 637 | 4175 | 1 | AT: 419; AT: 167
20251109 | November | 1230 |  | 7080 | 489 |  | 7066 | 489 | 4168 | 25 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4143 | NA | 14 | 0 | 14 | -25 | 1 | AT: 334; AT: 170; FR: 3166; FR: Process fail during TSO validation phase
20251109 | November | 1330 |  | 7204 | 499 |  | 7131 | 499 | 4168 | 149 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4019 | NA | 73 | 0 | 73 | -149 | 1 | AT: 340; AT: 170; FR: 3166; FR: Process fail during TSO validation phase
20251109 | November | 1430 |  | 7264 | 504 |  | 7163 | 504 | 4168 | 210 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3958 | NA | 101 | 0 | 101 | -210 | 1 | AT: 343; AT: 170; FR: 3167; FR: Process fail during TSO validation phase
20251109 | November | 1530 |  | 9918 | 1083 |  | 8649 | 1048 | -5551 | -5551 | 0 | Critical Branch | Critical Branch | 0 | NA | 1269 | 35 | 1304 | 5551 | 1 | AT: 206; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 1630 |  | 9918 | 1083 |  | 9918 | 1048 | -5551 | -5551 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 5551 | 1 | AT: 236; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 1730 |  | 9918 | 1083 |  | 9918 | 1048 | -5551 | -5551 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 5551 | 1 | AT: 236; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 1830 |  | 10046 | 793 |  | 9997 | 793 | -2747 | -2747 | 0 | Critical Branch | Critical Branch | 0 | NA | 49 | 0 | 49 | 2747 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 166; AT: Reduction because NTC over thermal limit on border
20251109 | November | 1930 |  | 10046 | 793 |  | 9997 | 793 | -2747 | -2747 | 0 | Critical Branch | Critical Branch | 0 | NA | 49 | 0 | 49 | 2747 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 166; AT: Reduction because NTC over thermal limit on border
20251109 | November | 2030 |  | 10046 | 793 |  | 9997 | 793 | -2747 | -2747 | 0 | Critical Branch | Critical Branch | 0 | NA | 49 | 0 | 49 | 2747 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 166; AT: Reduction because NTC over thermal limit on border
20251109 | November | 2130 | 10796 |  |  | 10747 |  |  | -5842 | -5842 | -5797 | Critical Branch | Critical Branch | 0 | 49 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 2230 | 10796 |  |  | 10747 |  |  | -5842 | -5842 | -5797 | Critical Branch | Critical Branch | 0 | 49 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251109 | November | 2330 | 10796 |  |  | 10747 |  |  | -5842 | -5842 | -5797 | Critical Branch | Critical Branch | 0 | 49 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251110 | November | 0030 | 10099 |  |  | 10083 |  |  | -3038 | -3038 | -3027 | Critical Branch | Critical Branch | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251110 | November | 0130 | 10099 |  |  | 10083 |  |  | -3038 | -3038 | -3027 | Critical Branch | Critical Branch | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251110 | November | 0230 | 10099 |  |  | 10083 |  |  | -3038 | -3038 | -3027 | Critical Branch | Critical Branch | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251110 | November | 0330 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170
20251110 | November | 0430 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170
20251110 | November | 0530 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170
20251110 | November | 0630 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170
20251110 | November | 0730 |  | 9798 | 1009 |  | 9798 | 984 | -3269 | -3269 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 25 | 25 | 3269 | 1 | AT: 227; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251110 | November | 0830 |  | 9798 | 1009 |  | 9798 | 984 | -3269 | -3269 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 25 | 25 | 3269 | 1 | AT: 227; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251110 | November | 0930 |  | 10212 | 782 |  | 10180 | 782 | -3373 | -3373 | 0 | Critical Branch | Critical Branch | 0 | NA | 32 | 0 | 32 | 3373 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1030 |  | 10212 | 782 |  | 10180 | 782 | -3373 | -3373 | 0 | Critical Branch | Critical Branch | 0 | NA | 32 | 0 | 32 | 3373 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1130 |  | 10212 | 782 |  | 10180 | 782 | -3373 | -3373 | 0 | Critical Branch | Critical Branch | 0 | NA | 32 | 0 | 32 | 3373 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1230 |  | 10107 | 732 |  | 10080 | 732 | -3927 | -3927 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 3927 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1330 |  | 10107 | 732 |  | 10080 | 732 | -3927 | -3927 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 3927 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1430 |  | 10107 | 732 |  | 10080 | 732 | -3927 | -3927 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 3927 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1530 | 10441 |  |  | 10437 |  |  | -3096 | -3096 | -3092 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1630 | 10441 |  |  | 10437 |  |  | -3096 | -3096 | -3092 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1730 | 10641 |  |  | 10637 |  |  | -3327 | -3327 | -3324 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251110 | November | 1830 |  | 9783 | 704 |  | 9782 | 704 | -3447 | -3447 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3447 | 1 | AT: 450; AT: 154
20251110 | November | 1930 |  | 9783 | 704 |  | 9782 | 704 | -3447 | -3447 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3447 | 1 | AT: 450; AT: 154
20251110 | November | 2030 |  | 9783 | 704 |  | 9782 | 704 | -3447 | -3447 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3447 | 1 | AT: 450; AT: 154
20251110 | November | 2130 | 9684 |  |  | 9683 |  |  | -2410 | -2410 | -2409 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155
20251110 | November | 2230 | 9684 |  |  | 9683 |  |  | -2410 | -2410 | -2409 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 410; AT: 155
20251110 | November | 2330 | 8874 |  |  | 8873 |  |  | -1715 | -1715 | -1715 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 393; AT: 170
20251111 | November | 0030 | 10160 |  |  | 10141 |  |  | -3505 | -3505 | -3485 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251111 | November | 0130 | 10160 |  |  | 10141 |  |  | -3505 | -3505 | -3485 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251111 | November | 0230 | 10160 |  |  | 10141 |  |  | -3505 | -3505 | -3485 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251111 | November | 0330 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 434; AT: 170
20251111 | November | 0430 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 434; AT: 170
20251111 | November | 0530 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 434; AT: 170
20251111 | November | 0630 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 434; AT: 170
20251111 | November | 0730 |  | 9278 | 678 |  | 9277 | 678 | -2624 | -2624 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2624 | 1 | AT: 435; AT: 155
20251111 | November | 0830 |  | 9278 | 678 |  | 9277 | 678 | -2624 | -2624 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2624 | 1 | AT: 435; AT: 155
20251111 | November | 0930 | 9710 |  |  | 9710 |  |  | -2844 | -2844 | -2844 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 155
20251111 | November | 1030 | 9710 |  |  | 9710 |  |  | -2844 | -2844 | -2844 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 155
20251111 | November | 1130 | 9710 |  |  | 9710 |  |  | -2844 | -2844 | -2844 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 155
20251111 | November | 1230 |  | 9948 | 727 |  | 9929 | 727 | -3802 | -3802 | 0 | Critical Branch | Critical Branch | 0 | NA | 19 | 0 | 19 | 3802 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20251111 | November | 1330 |  | 9948 | 727 |  | 9929 | 727 | -3802 | -3802 | 0 | Critical Branch | Critical Branch | 0 | NA | 19 | 0 | 19 | 3802 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20251111 | November | 1430 |  | 9948 | 727 |  | 9929 | 727 | -3802 | -3802 | 0 | Critical Branch | Critical Branch | 0 | NA | 19 | 0 | 19 | 3802 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20251111 | November | 1530 | 9836 |  |  | 9836 |  |  | -3696 | -3696 | -3695 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 426; AT: 155
20251111 | November | 1630 | 9836 |  |  | 9836 |  |  | -3696 | -3696 | -3695 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 426; AT: 155
20251111 | November | 1730 | 10036 |  |  | 10035 |  |  | -3911 | -3911 | -3911 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 426; AT: 155
20251111 | November | 1830 |  | 9307 | 660 |  | 9306 | 660 | -2990 | -2990 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2990 | 1 | AT: 427; AT: 155
20251111 | November | 1930 |  | 9307 | 660 |  | 9306 | 660 | -2990 | -2990 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2990 | 1 | AT: 427; AT: 155
20251111 | November | 2030 |  | 9307 | 660 |  | 9306 | 660 | -2990 | -2990 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2990 | 1 | AT: 427; AT: 155
20251111 | November | 2130 | 9627 |  |  | 9627 |  |  | -3000 | -3000 | -2999 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 155
20251111 | November | 2230 | 9627 |  |  | 9627 |  |  | -3000 | -3000 | -2999 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 408; AT: 155
20251111 | November | 2330 | 8817 |  |  | 8817 |  |  | -2160 | -2160 | -2160 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 170
20251112 | November | 0030 | 9873 |  |  | 9867 |  |  | -2427 | -2427 | -2423 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251112 | November | 0130 | 9873 |  |  | 9867 |  |  | -2427 | -2427 | -2423 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251112 | November | 0230 | 9873 |  |  | 9867 |  |  | -2427 | -2427 | -2423 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251112 | November | 0330 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251112 | November | 0430 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251112 | November | 0530 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251112 | November | 0630 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251112 | November | 0730 |  | 8609 | 632 |  | 8608 | 632 | -2139 | -2139 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2139 | 1 | AT: 402; AT: 155
20251112 | November | 0830 |  | 8010 | 632 |  | 8010 | 632 | -1299 | -1299 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1299 | 1 | AT: 399; AT: 155
20251112 | November | 0930 | 8389 |  |  | 8389 |  |  | -55 | -55 | -55 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 334; AT: 135
20251112 | November | 1030 | 8389 |  |  | 8389 |  |  | -55 | -55 | -55 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 334; AT: 135
20251112 | November | 1130 | 8389 |  |  | 8389 |  |  | -55 | -55 | -55 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 334; AT: 135
20251112 | November | 1230 | 9119 |  |  | 9118 |  |  | -2447 | -2447 | -2446 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 418; AT: 155
20251112 | November | 1330 | 9119 |  |  | 9118 |  |  | -2447 | -2447 | -2446 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 418; AT: 155
20251112 | November | 1430 | 9119 |  |  | 9118 |  |  | -2447 | -2447 | -2446 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 418; AT: 155
20251112 | November | 1530 |  | 8694 | 673 |  | 8693 | 673 | -3884 | -3884 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 3884 | 1 | AT: 435; AT: 155
20251112 | November | 1630 |  | 9294 | 673 |  | 9294 | 673 | -4454 | -4454 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4454 | 1 | AT: 436; AT: 155
20251112 | November | 1730 |  | 9494 | 673 |  | 9493 | 673 | -4675 | -4675 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4675 | 1 | AT: 436; AT: 155
20251112 | November | 1830 |  | 8739 | 637 |  | 8739 | 637 | -1851 | -1851 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1851 | 1 | AT: 400; AT: 155
20251112 | November | 1930 |  | 8739 | 637 |  | 8739 | 637 | -1851 | -1851 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1851 | 1 | AT: 400; AT: 155
20251112 | November | 2030 |  | 8739 | 637 |  | 8739 | 637 | -1851 | -1851 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1851 | 1 | AT: 400; AT: 155
20251112 | November | 2130 | 10243 |  |  | 10242 |  |  | -3553 | -3553 | -3552 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 435; AT: 155
20251112 | November | 2230 | 10243 |  |  | 10242 |  |  | -3553 | -3553 | -3552 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 435; AT: 155
20251112 | November | 2330 | 9433 |  |  | 9433 |  |  | -2755 | -2755 | -2755 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 420; AT: 170
20251113 | November | 0030 | 9404 |  |  | 9404 |  |  | -3824 | -3824 | -3824 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0130 | 9404 |  |  | 9404 |  |  | -3824 | -3824 | -3824 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0230 | 9404 |  |  | 9404 |  |  | -3824 | -3824 | -3824 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0330 | 9330 |  |  | 9330 |  |  | -3570 | -3570 | -3570 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0430 | 9330 |  |  | 9330 |  |  | -3570 | -3570 | -3570 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0530 | 9330 |  |  | 9330 |  |  | -3570 | -3570 | -3570 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0630 | 9330 |  |  | 9330 |  |  | -3570 | -3570 | -3570 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0730 | 9504 |  |  | 9504 |  |  | -2375 | -2375 | -2375 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0830 | 8904 |  |  | 8904 |  |  | -1604 | -1604 | -1604 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 0930 | 8171 |  |  | 8171 |  |  | -1872 | -1872 | -1872 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1030 | 8171 |  |  | 8171 |  |  | -1872 | -1872 | -1872 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1130 | 8171 |  |  | 8171 |  |  | -1872 | -1872 | -1872 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1230 | 8812 |  |  | 8812 |  |  | -2770 | -2770 | -2770 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1330 | 8812 |  |  | 8812 |  |  | -2770 | -2770 | -2770 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1430 | 8812 |  |  | 8812 |  |  | -2770 | -2770 | -2770 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1530 | 9246 |  |  | 9246 |  |  | -3976 | -3976 | -3976 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1630 | 9246 |  |  | 9246 |  |  | -3976 | -3976 | -3976 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1730 | 9446 |  |  | 9446 |  |  | -4188 | -4188 | -4188 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1830 | 9283 |  |  | 9283 |  |  | -1482 | -1482 | -1482 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 1930 | 9283 |  |  | 9283 |  |  | -1482 | -1482 | -1482 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 2030 | 9283 |  |  | 9283 |  |  | -1482 | -1482 | -1482 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 2130 | 9641 |  |  | 9641 |  |  | -4538 | -4538 | -4538 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 2230 | 9641 |  |  | 9641 |  |  | -4538 | -4538 | -4538 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251113 | November | 2330 | 8831 |  |  | 8831 |  |  | -3729 | -3729 | -3729 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251114 | November | 0030 | 9311 |  |  | 9303 |  |  | -4264 | -4264 | -4255 | Critical Branch | Critical Branch | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251114 | November | 0130 | 9311 |  |  | 9303 |  |  | -4264 | -4264 | -4255 | Critical Branch | Critical Branch | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251114 | November | 0230 | 9311 |  |  | 9303 |  |  | -4264 | -4264 | -4255 | Critical Branch | Critical Branch | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251114 | November | 0330 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251114 | November | 0430 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251114 | November | 0530 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251114 | November | 0630 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 431; AT: 170
20251114 | November | 0730 |  | 9536 | 771 |  | 9259 | 771 | -4225 | -4225 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 277 | 0 | 277 | 4225 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 0830 |  | 9536 | 771 |  | 9259 | 771 | -4225 | -4225 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 277 | 0 | 277 | 4225 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 0930 | 10011 |  |  | 9899 |  |  | -3255 | -3255 | -3147 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 112 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1030 | 10011 |  |  | 9899 |  |  | -3255 | -3255 | -3147 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 112 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1130 | 10011 |  |  | 9899 |  |  | -3255 | -3255 | -3147 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 112 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1230 | 10277 |  |  | 10046 |  |  | -2670 | -2670 | -2475 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 231 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1330 | 10277 |  |  | 10046 |  |  | -2670 | -2670 | -2475 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 231 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1430 | 10277 |  |  | 10046 |  |  | -2670 | -2670 | -2475 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 231 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1530 | 10004 |  |  | 9895 |  |  | -2850 | -2850 | -2757 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 109 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3685; FR: Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1630 | 10604 |  |  | 10593 |  |  | -3387 | -3387 | -3377 | Critical Branch | Critical Branch | 0 | 11 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251114 | November | 1730 | 10804 |  |  | 10793 |  |  | -3615 | -3615 | -3605 | Critical Branch | Critical Branch | 0 | 11 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20251114 | November | 1830 |  | 10392 | 766 |  | 10362 | 766 | -3693 | -3693 | 0 | Critical Branch | Critical Branch | 0 | NA | 30 | 0 | 30 | 3693 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20251114 | November | 1930 |  | 10392 | 766 |  | 10362 | 766 | -3693 | -3693 | 0 | Critical Branch | Critical Branch | 0 | NA | 30 | 0 | 30 | 3693 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20251114 | November | 2030 |  | 10392 | 766 |  | 10362 | 766 | -3693 | -3693 | 0 | Critical Branch | Critical Branch | 0 | NA | 30 | 0 | 30 | 3693 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20251114 | November | 2130 | 9409 |  |  | 9408 |  |  | -4039 | -4039 | -4039 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 398; AT: 155
20251114 | November | 2230 | 9409 |  |  | 9408 |  |  | -4039 | -4039 | -4039 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 398; AT: 155
20251114 | November | 2330 | 8599 |  |  | 8598 |  |  | -3230 | -3230 | -3229 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251115 | November | 0030 | 9474 |  |  | 9474 |  |  | -4855 | -4855 | -4855 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0130 | 9474 |  |  | 9474 |  |  | -4855 | -4855 | -4855 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0230 | 9474 |  |  | 9474 |  |  | -4855 | -4855 | -4855 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0330 | 9004 |  |  | 9004 |  |  | -4193 | -4193 | -4193 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0430 | 9004 |  |  | 9004 |  |  | -4193 | -4193 | -4193 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0530 | 9004 |  |  | 9004 |  |  | -4193 | -4193 | -4193 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0630 | 9004 |  |  | 9004 |  |  | -4193 | -4193 | -4193 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0730 | 9808 |  |  | 9808 |  |  | -5158 | -5158 | -5158 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0830 | 9808 |  |  | 9808 |  |  | -5158 | -5158 | -5158 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 0930 | 9015 |  |  | 9015 |  |  | -3909 | -3909 | -3909 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1030 | 9015 |  |  | 9015 |  |  | -3909 | -3909 | -3909 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1130 | 9015 |  |  | 9015 |  |  | -3909 | -3909 | -3909 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1230 |  | 8380 | 677 |  | 8380 | 677 | -3674 | -3674 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3674 | 0
20251115 | November | 1330 |  | 8380 | 677 |  | 8380 | 677 | -3674 | -3674 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3674 | 0
20251115 | November | 1430 |  | 8380 | 677 |  | 8380 | 677 | -3674 | -3674 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3674 | 0
20251115 | November | 1530 | 9844 |  |  | 9844 |  |  | -5506 | -5506 | -5506 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1630 | 9844 |  |  | 9844 |  |  | -5506 | -5506 | -5506 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1730 | 9844 |  |  | 9844 |  |  | -5506 | -5506 | -5506 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1830 | 8893 |  |  | 8893 |  |  | -1092 | -1092 | -1092 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 1930 | 8893 |  |  | 8893 |  |  | -1092 | -1092 | -1092 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 2030 | 8893 |  |  | 8893 |  |  | -1092 | -1092 | -1092 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 2130 | 9404 |  |  | 9404 |  |  | -4832 | -4832 | -4832 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 2230 | 9404 |  |  | 9404 |  |  | -4832 | -4832 | -4832 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251115 | November | 2330 | 8594 |  |  | 8594 |  |  | -4026 | -4026 | -4026 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0030 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0130 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0230 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0330 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0430 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0530 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0630 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0730 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0830 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 0930 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 1030 | 9750 |  |  | 9750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 1130 | 9750 |  |  | 9646 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 104 | NA | NA | NA | 0 | 1
20251116 | November | 1230 | 9750 |  |  | 8146 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1604 | NA | NA | NA | 0 | 1 | SI: 7896; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251116 | November | 1330 | 9525 |  |  | 8034 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1491 | NA | NA | NA | 0 | 1 | SI: 7784; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251116 | November | 1430 | 9525 |  |  | 8034 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1491 | NA | NA | NA | 0 | 1 | SI: 7784; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251116 | November | 1530 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 1630 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 1730 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 1830 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 1930 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 2030 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 2130 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 2230 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251116 | November | 2330 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0030 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0130 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0230 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0330 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0430 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0530 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0630 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0730 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0830 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 0930 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1030 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1130 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1230 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1330 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1430 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1530 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1630 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1730 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1830 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 1930 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 2030 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 2130 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 2230 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251117 | November | 2330 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0030 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0130 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0230 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0330 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0430 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0530 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0630 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0730 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0830 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 0930 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1030 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1130 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1230 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1330 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1430 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1530 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1630 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1730 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1830 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 1930 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 2030 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 2130 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 2230 | 10320 |  |  | 10320 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251118 | November | 2330 | 9525 |  |  | 9525 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0030 | 7898 |  |  | 7898 |  |  | -2800 | -2800 | -2800 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0130 | 7898 |  |  | 7898 |  |  | -2800 | -2800 | -2800 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0230 | 7898 |  |  | 7898 |  |  | -2800 | -2800 | -2800 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0330 | 7798 |  |  | 7798 |  |  | -2811 | -2811 | -2811 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0430 | 7798 |  |  | 7798 |  |  | -2811 | -2811 | -2811 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0530 | 7798 |  |  | 7798 |  |  | -2811 | -2811 | -2811 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0630 | 7798 |  |  | 7798 |  |  | -2811 | -2811 | -2811 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 0730 | 9507 |  |  | 8789 |  |  | -1703 | -1703 | -985 | Critical Branch | Validation phase | 0 | 718 | NA | NA | NA | 0 | 1 | CH: 8539; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251119 | November | 0830 | 9507 |  |  | 8789 |  |  | -1703 | -1703 | -985 | Critical Branch | Validation phase | 0 | 718 | NA | NA | NA | 0 | 1 | CH: 8539; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251119 | November | 0930 | 8150 |  |  | 8150 |  |  | -2968 | -2968 | -2968 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 1030 | 8150 |  |  | 8150 |  |  | -2968 | -2968 | -2968 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 1130 | 8150 |  |  | 8150 |  |  | -2968 | -2968 | -2968 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 1230 | 8396 |  |  | 8396 |  |  | -3150 | -3150 | -3150 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 1330 | 8396 |  |  | 8396 |  |  | -3150 | -3150 | -3150 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 1430 | 8396 |  |  | 8396 |  |  | -3150 | -3150 | -3150 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 1530 | 9587 |  |  | 8247 |  |  | -4421 | -4421 | -3081 | Critical Branch | Validation phase | 0 | 1340 | NA | NA | NA | 0 | 1 | CH: 7997; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1630 | 9587 |  |  | 8247 |  |  | -4421 | -4421 | -3081 | Critical Branch | Validation phase | 0 | 1340 | NA | NA | NA | 0 | 1 | CH: 7997; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1730 | 9587 |  |  | 8247 |  |  | -4421 | -4421 | -3081 | Critical Branch | Validation phase | 0 | 1340 | NA | NA | NA | 0 | 1 | CH: 7997; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1830 | 10120 |  |  | 9445 |  |  | -2559 | -2559 | -1884 | Critical Branch | Validation phase | 0 | 675 | NA | NA | NA | 0 | 1 | CH: 9195; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1930 | 10120 |  |  | 9445 |  |  | -2559 | -2559 | -1884 | Critical Branch | Validation phase | 0 | 675 | NA | NA | NA | 0 | 1 | CH: 9195; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 2030 | 10120 |  |  | 9445 |  |  | -2559 | -2559 | -1884 | Critical Branch | Validation phase | 0 | 675 | NA | NA | NA | 0 | 1 | CH: 9195; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 2130 | 9080 |  |  | 9080 |  |  | -4057 | -4057 | -4057 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 2230 | 9080 |  |  | 9080 |  |  | -4057 | -4057 | -4057 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251119 | November | 2330 | 8285 |  |  | 8285 |  |  | -3263 | -3263 | -3263 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251120 | November | 0030 | 9375 |  |  | 9374 |  |  | -4843 | -4843 | -4843 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 206; AT: 70
20251120 | November | 0130 | 9375 |  |  | 9374 |  |  | -4843 | -4843 | -4843 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 206; AT: 70
20251120 | November | 0230 | 9375 |  |  | 9374 |  |  | -4843 | -4843 | -4843 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 206; AT: 70
20251120 | November | 0330 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 0 | 604 | NA | NA | NA | 0 | 1 | AT: 205; AT: 70; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0430 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 0 | 604 | NA | NA | NA | 0 | 1 | AT: 205; AT: 70; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0530 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 0 | 604 | NA | NA | NA | 0 | 1 | AT: 205; AT: 70; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0630 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 0 | 604 | NA | NA | NA | 0 | 1 | AT: 205; AT: 70; CH: 8476; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0730 |  | 8676 | 825 |  | 8676 | 821 | -4148 | -4148 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 4 | 4 | 4148 | 1 | AT: 92; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 0830 |  | 8676 | 825 |  | 8676 | 821 | -4148 | -4148 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 4 | 4 | 4148 | 1 | AT: 92; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 0930 |  | 8054 | 143 |  | 8017 | 81 | 5318 | 79 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 5239 | NA | 37 | 62 | 99 | -79 | 1 | AT: 163; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3337; FR: Process fail during TSO validation phase
20251120 | November | 1030 |  | 8173 | 146 |  | 8082 | 81 | 5318 | 198 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 5120 | NA | 91 | 65 | 156 | -198 | 1 | AT: 163; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3337; FR: Process fail during TSO validation phase
20251120 | November | 1130 |  | 8108 | 145 |  | 8046 | 81 | 5318 | 133 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 5185 | NA | 62 | 64 | 126 | -133 | 1 | AT: 163; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3337; FR: Process fail during TSO validation phase
20251120 | November | 1230 |  | 7437 | 488 |  | 6401 | 487 | 3523 | 86 | 0 | Minimum Margin | Validation phase | 3437 | NA | 1036 | 1 | 1037 | -86 | 1 | AT: 163; AT: 43; FR: 3337; FR: Process fail during TSO validation phase; SI: 6489; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251120 | November | 1330 |  | 7433 | 488 |  | 6395 | 487 | 3523 | 82 | 0 | Minimum Margin | Validation phase | 3441 | NA | 1038 | 1 | 1039 | -82 | 1 | AT: 163; AT: 43; FR: 3337; FR: Process fail during TSO validation phase; SI: 6487; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251120 | November | 1430 |  | 7515 | 495 |  | 6584 | 493 | 3523 | 165 | 0 | Minimum Margin | Validation phase | 3358 | NA | 931 | 2 | 933 | -165 | 1 | AT: 163; AT: 44; FR: 3337; FR: Process fail during TSO validation phase; SI: 6593; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251120 | November | 1530 |  | 9094 | 941 |  | 8066 | 925 | -4360 | -4360 | 0 | Critical Branch | Critical Branch | 0 | NA | 1028 | 16 | 1044 | 4360 | 1 | AT: 97; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 1630 |  | 9094 | 941 |  | 9094 | 925 | -4360 | -4360 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 4360 | 1 | AT: 97; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 1730 |  | 9094 | 941 |  | 9094 | 925 | -4360 | -4360 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 4360 | 1 | AT: 97; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 1830 |  | 8737 | 877 |  | 8737 | 868 | -4023 | -4023 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 4023 | 1 | AT: 93; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 1930 |  | 8737 | 877 |  | 8737 | 868 | -4023 | -4023 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 4023 | 1 | AT: 93; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 2030 |  | 8737 | 877 |  | 8737 | 868 | -4023 | -4023 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 4023 | 1 | AT: 93; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20251120 | November | 2130 | 9516 |  |  | 9155 |  |  | -4818 | -4818 | -4457 | Critical Branch | Validation phase | 0 | 361 | NA | NA | NA | 0 | 1 | AT: 192; AT: 70; CH: 8905; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251120 | November | 2230 | 9516 |  |  | 9155 |  |  | -4818 | -4818 | -4457 | Critical Branch | Validation phase | 0 | 361 | NA | NA | NA | 0 | 1 | AT: 192; AT: 70; CH: 8905; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251120 | November | 2330 | 8721 |  |  | 8360 |  |  | -4024 | -4024 | -3663 | Critical Branch | Validation phase | 0 | 361 | NA | NA | NA | 0 | 1 | AT: 191; AT: 70; CH: 8110; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251121 | November | 0030 | 9221 |  |  | 8297 |  |  | -4362 | -4362 | -3438 | Critical Branch | Validation phase | 0 | 924 | NA | NA | NA | 0 | 1 | AT: 202; AT: 70; CH: 3487; CH: 8047; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0130 | 9221 |  |  | 8297 |  |  | -4362 | -4362 | -3438 | Critical Branch | Validation phase | 0 | 924 | NA | NA | NA | 0 | 1 | AT: 202; AT: 70; CH: 3487; CH: 8047; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0230 | 9221 |  |  | 8297 |  |  | -4362 | -4362 | -3438 | Critical Branch | Validation phase | 0 | 924 | NA | NA | NA | 0 | 1 | AT: 202; AT: 70; CH: 3487; CH: 8047; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0330 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 0 | 492 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 3382; CH: 7813; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0430 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 0 | 492 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 3382; CH: 7813; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0530 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 0 | 492 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 3382; CH: 7813; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0630 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 0 | 492 | NA | NA | NA | 0 | 1 | AT: 187; AT: 70; CH: 3382; CH: 7813; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS; CH: 1910; CH: NTC correction
20251121 | November | 0730 |  | 8638 | 776 |  | 8638 | 775 | -2051 | -2051 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 2051 | 1 | AT: 92; AT: 69; CH: 4226; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 0830 |  | 8638 | 776 |  | 8638 | 775 | -2051 | -2051 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 2051 | 1 | AT: 92; AT: 69; CH: 4226; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 0930 | 8334 |  |  | 8333 |  |  | 5927 | 184 | 5744 | Minimum Margin | Minimum Margin | 5743 | 1 | NA | NA | NA | 11304 | 1 | AT: 167; AT: 70; CH: 3647; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 1030 | 8375 |  |  | 8375 |  |  | 5927 | 225 | 5703 | Minimum Margin | Minimum Margin | 5702 | 0 | NA | NA | NA | 11181 | 1 | AT: 168; AT: 70; CH: 3666; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 1130 | 8356 |  |  | 8140 |  |  | 5927 | 206 | 5937 | Minimum Margin | Minimum Margin | 5721 | 216 | NA | NA | NA | 11668 | 1 | AT: 168; AT: 70; CH: 3658; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 1230 |  | 7724 | 397 |  | 6308 | 397 | 4570 | 199 | 0 | Minimum Margin | Validation phase | 4371 | NA | 1416 | 0 | 1416 | -199 | 1 | AT: 168; AT: 70; CH: 3662; CH: NTC correction; CH: 1810; CH: NTC correction; FR: 3337; FR: Process fail during TSO validation phase; SI: 6191; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1330 |  | 7534 | 383 |  | 6016 | 324 | 4570 | 8 | 0 | Minimum Margin | Smoothing ramp | 4562 | NA | 1518 | 59 | 1577 | -8 | 1 | AT: 163; AT: 70; CH: 3566; CH: NTC correction; CH: 1810; CH: NTC correction; FR: 3338; FR: Process fail during TSO validation phase; SI: 6090; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1430 |  | 7620 | 389 |  | 6149 | 204 | 4570 | 95 | 0 | Minimum Margin | Smoothing ramp | 4475 | NA | 1471 | 185 | 1656 | -95 | 1 | AT: 165; AT: 70; CH: 3610; CH: NTC correction; CH: 1810; CH: NTC correction; FR: 3338; FR: Process fail during TSO validation phase; SI: 6136; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1530 |  | 7426 | 478 |  | 6751 | 129 | 6324 | 75 | 0 | Minimum Margin | Validation phase | 6249 | NA | 675 | 349 | 1024 | -75 | 1 | AT: 163; AT: 41; CH: 3601; CH: NTC correction; CH: 1810; CH: NTC correction; FR: 3337; FR: Process fail during TSO validation phase; IT: 73; IT: Forecasted security violation; SI: 6850; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1630 |  | 7430 | 479 |  | 6755 | 129 | 6324 | 79 | 0 | Minimum Margin | Validation phase | 6245 | NA | 675 | 350 | 1025 | -79 | 1 | AT: 163; AT: 41; CH: 3603; CH: NTC correction; CH: 1810; CH: NTC correction; FR: 3337; FR: Process fail during TSO validation phase; IT: 73; IT: Forecasted security violation; SI: 6850; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1730 |  | 7426 | 478 |  | 6751 | 129 | 6324 | 75 | 0 | Minimum Margin | Validation phase | 6249 | NA | 675 | 349 | 1024 | -75 | 1 | AT: 163; AT: 41; CH: 3601; CH: NTC correction; CH: 1810; CH: NTC correction; FR: 3337; FR: Process fail during TSO validation phase; IT: 73; IT: Forecasted security violation; SI: 6850; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1830 |  | 9459 | 925 |  | 8228 | 129 | -2406 | -2406 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1231 | 796 | 2027 | 2406 | 1 | AT: 98; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; CH: 4650; CH: NTC correction; CH: 1741; CH: NTC correction; IT: 73; IT: Forecasted security violation
20251121 | November | 1930 |  | 9572 | 1010 |  | 9537 | 462 | -2606 | -2606 | 0 | Critical Branch | Critical Branch | 0 | NA | 35 | 548 | 583 | 2606 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 4714; CH: NTC correction; CH: 1746; CH: NTC correction
20251121 | November | 2030 |  | 9572 | 1010 |  | 9572 | 764 | -2606 | -2606 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 246 | 246 | 2606 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; CH: 4714; CH: NTC correction; CH: 1746; CH: NTC correction
20251121 | November | 2130 | 9252 |  |  | 9252 |  |  | -3914 | -3914 | -3913 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 155; CH: 3978; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 2230 | 9252 |  |  | 9252 |  |  | -3914 | -3914 | -3913 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 155; CH: 3978; CH: NTC correction; CH: 1810; CH: NTC correction
20251121 | November | 2330 | 8442 |  |  | 8442 |  |  | -3106 | -3106 | -3105 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 373; AT: 170; CH: 3465; CH: NTC correction; CH: 1910; CH: NTC correction
20251122 | November | 0030 | 7875 |  |  | 7875 |  |  | 2761 | 195 | 2566 | Minimum Margin | Minimum Margin | 2566 | 0 | NA | NA | NA | 4937 | 0
20251122 | November | 0130 | 7818 |  |  | 7818 |  |  | 2761 | 138 | 2623 | Minimum Margin | Minimum Margin | 2623 | 0 | NA | NA | NA | 5108 | 0
20251122 | November | 0230 | 7818 |  |  | 7818 |  |  | 2761 | 138 | 2623 | Minimum Margin | Minimum Margin | 2623 | 0 | NA | NA | NA | 5108 | 0
20251122 | November | 0330 | 7852 |  |  | 7852 |  |  | 2947 | 172 | 2775 | Minimum Margin | Minimum Margin | 2775 | 0 | NA | NA | NA | 5378 | 0
20251122 | November | 0430 | 7852 |  |  | 7852 |  |  | 2947 | 172 | 2775 | Minimum Margin | Minimum Margin | 2775 | 0 | NA | NA | NA | 5378 | 0
20251122 | November | 0530 | 7852 |  |  | 7750 |  |  | 2947 | 172 | 2877 | Minimum Margin | Smoothing ramp | 2775 | 102 | NA | NA | NA | 5582 | 1
20251122 | November | 0630 | 7905 |  |  | 6250 |  |  | 2947 | 225 | 4377 | Minimum Margin | Validation phase | 2722 | 1655 | NA | NA | NA | 8529 | 1 | FR: 7901; FR: N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR]; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 0730 | 10560 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 2810 | NA | NA | NA | 0 | 1 | CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251122 | November | 0830 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251122 | November | 0930 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251122 | November | 1030 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251122 | November | 1130 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2012 | NA | NA | NA | 0 | 1 | CH: 8298; CH: D2CC failed. Correction of BackUp-values.
20251122 | November | 1230 | 8390 |  |  | 8390 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251122 | November | 1330 | 8390 |  |  | 8390 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251122 | November | 1430 | 8390 |  |  | 7750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Smoothing ramp | 0 | 640 | NA | NA | NA | 0 | 1
20251122 | November | 1530 | 8627 |  |  | 6250 |  |  | 3874 | 237 | 6014 | Minimum Margin | Validation phase | 3637 | 2377 | NA | NA | NA | 11791 | 1 | FR: 8623; FR: N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR]; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 1630 | 8413 |  |  | 6250 |  |  | 3874 | 23 | 6014 | Minimum Margin | Validation phase | 3851 | 2163 | NA | NA | NA | 12005 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 1730 | 8390 |  |  | 6250 |  |  | 3874 | 0 | 6014 | TTC Selection - LTTC | Validation phase | 3874 | 2140 | NA | NA | NA | 12028 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 1830 | 8390 |  |  | 7750 |  |  | -1374 | -1374 | -734 | TTC Selection - LTTC | Smoothing ramp | 0 | 640 | NA | NA | NA | 0 | 1
20251122 | November | 1930 | 8390 |  |  | 8390 |  |  | -1374 | -1374 | -1374 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251122 | November | 2030 | 8390 |  |  | 8390 |  |  | -1374 | -1374 | -1374 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20251122 | November | 2130 | 9591 |  |  | 9591 |  |  | -1926 | -1926 | -1926 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251122 | November | 2230 | 9591 |  |  | 9591 |  |  | -1926 | -1926 | -1926 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251122 | November | 2330 | 8781 |  |  | 8781 |  |  | -1220 | -1220 | -1220 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251123 | November | 0030 | 9696 |  |  | 9696 |  |  | -4561 | -4561 | -4561 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251123 | November | 0130 | 9696 |  |  | 9696 |  |  | -4561 | -4561 | -4561 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251123 | November | 0230 | 9696 |  |  | 9696 |  |  | -4561 | -4561 | -4561 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 432; AT: 170
20251123 | November | 0330 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170
20251123 | November | 0430 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170
20251123 | November | 0530 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170
20251123 | November | 0630 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170
20251123 | November | 0730 | 9606 |  |  | 9606 |  |  | -5566 | -5566 | -5566 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 428; AT: 170
20251123 | November | 0830 | 9606 |  |  | 9606 |  |  | -5566 | -5566 | -5566 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 428; AT: 170
20251123 | November | 0930 | 8594 |  |  | 8593 |  |  | -3313 | -3313 | -3312 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251123 | November | 1030 | 8594 |  |  | 8593 |  |  | -3313 | -3313 | -3312 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251123 | November | 1130 | 8594 |  |  | 8593 |  |  | -3313 | -3313 | -3312 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 170
20251123 | November | 1230 | 8960 |  |  | 8959 |  |  | -3453 | -3453 | -3452 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 397; AT: 170
20251123 | November | 1330 | 8960 |  |  | 8959 |  |  | -3453 | -3453 | -3452 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 397; AT: 170
20251123 | November | 1430 | 8960 |  |  | 8959 |  |  | -3453 | -3453 | -3452 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 397; AT: 170
20251123 | November | 1530 | 9885 |  |  | 9879 |  |  | -5655 | -5655 | -5649 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251123 | November | 1630 | 9885 |  |  | 9879 |  |  | -5655 | -5655 | -5649 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251123 | November | 1730 | 9885 |  |  | 9879 |  |  | -5655 | -5655 | -5649 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20251123 | November | 1830 | 9619 |  |  | 9618 |  |  | -4856 | -4856 | -4855 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 428; AT: 170
20251123 | November | 1930 | 9619 |  |  | 9618 |  |  | -4856 | -4856 | -4855 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 428; AT: 170
20251123 | November | 2030 | 9619 |  |  | 9618 |  |  | -4856 | -4856 | -4855 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 428; AT: 170
20251123 | November | 2130 | 9428 |  |  | 9427 |  |  | -4382 | -4382 | -4381 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170
20251123 | November | 2230 | 9428 |  |  | 9427 |  |  | -4382 | -4382 | -4381 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170
20251123 | November | 2330 | 9428 |  |  | 9427 |  |  | -4382 | -4382 | -4381 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 419; AT: 170
20251124 | November | 0030 | 8667 |  |  | 8667 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0130 | 8667 |  |  | 8667 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0230 | 8667 |  |  | 8667 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0330 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0430 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0530 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0630 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 9000; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 4138; FR: Process failed: missing input; FR: 2160; FR: Process failed: missing input
20251124 | November | 0730 | 9871 |  |  | 8864 |  |  | -4675 | -4675 | -3694 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1007 | NA | NA | NA | 0 | 1 | CH: 9810; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 0830 | 9871 |  |  | 8864 |  |  | -4675 | -4675 | -3694 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1007 | NA | NA | NA | 0 | 1 | CH: 9810; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 0930 | 9854 |  |  | 8210 |  |  | -4668 | -4668 | -3030 | Critical Branch | Validation phase | 0 | 1644 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 8512; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1030 | 9854 |  |  | 8210 |  |  | -4668 | -4668 | -3030 | Critical Branch | Validation phase | 0 | 1644 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 8512; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1130 | 9854 |  |  | 8210 |  |  | -4668 | -4668 | -3030 | Critical Branch | Validation phase | 0 | 1644 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 8512; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1230 | 9834 |  |  | 7498 |  |  | -2507 | -2507 | -174 | Critical Branch | Validation phase | 0 | 2336 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 7266; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1330 | 9834 |  |  | 7498 |  |  | -2507 | -2507 | -174 | Critical Branch | Validation phase | 0 | 2336 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 7266; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1430 | 9834 |  |  | 7498 |  |  | -2507 | -2507 | -174 | Critical Branch | Validation phase | 0 | 2336 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 7266; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1530 | 9250 |  |  | 7935 |  |  | -2337 | -2337 | -1066 | Critical Branch | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 8030; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1630 | 9250 |  |  | 7935 |  |  | -2337 | -2337 | -1066 | Critical Branch | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 8030; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1730 | 9250 |  |  | 7935 |  |  | -2337 | -2337 | -1066 | Critical Branch | Validation phase | 0 | 1315 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input; SI: 8030; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1830 | 10321 |  |  | 8924 |  |  | -3403 | -3403 | -2228 | Critical Branch | Validation phase | 0 | 1397 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 1930 | 10321 |  |  | 8924 |  |  | -3403 | -3403 | -2228 | Critical Branch | Validation phase | 0 | 1397 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 2030 | 10321 |  |  | 8924 |  |  | -3403 | -3403 | -2228 | Critical Branch | Validation phase | 0 | 1397 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 2130 | 9007 |  |  | 8350 |  |  | -3519 | -3519 | -2871 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 657 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 2230 | 9007 |  |  | 8350 |  |  | -3519 | -3519 | -2871 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 657 | NA | NA | NA | 0 | 1 | CH: 9760; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 1995; FR: Process failed: missing input
20251124 | November | 2330 | 8197 |  |  | 7720 |  |  | -2712 | -2712 | -2241 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 477 | NA | NA | NA | 0 | 1 | CH: 8950; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2985; FR: Outage - Venaus - Piossasco; FR: 2160; FR: Process failed: missing input
20251125 | November | 0030 | 8000 |  |  | 7612 |  |  | -4610 | -4610 | -4185 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 388 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0130 | 8000 |  |  | 7612 |  |  | -4610 | -4610 | -4185 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 388 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0230 | 8000 |  |  | 7612 |  |  | -4610 | -4610 | -4185 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 388 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0330 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 483 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0430 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 483 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0530 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 483 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0630 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 483 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0730 |  | 8048 | 797 |  | 7331 | 797 | -5864 | -5864 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 717 | 0 | 717 | 5864 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0830 |  | 8048 | 797 |  | 7331 | 797 | -5864 | -5864 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 717 | 0 | 717 | 5864 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 0930 |  | 7809 | 757 |  | 7209 | 757 | -5444 | -5444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 600 | 0 | 600 | 5444 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 1030 |  | 7809 | 757 |  | 7209 | 757 | -5444 | -5444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 600 | 0 | 600 | 5444 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 1130 |  | 7809 | 757 |  | 7209 | 757 | -5444 | -5444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 600 | 0 | 600 | 5444 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 1230 |  | 7557 | 699 |  | 7079 | 699 | -5409 | -5409 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 478 | 0 | 478 | 5409 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 1330 |  | 7557 | 699 |  | 7079 | 491 | -5409 | -5409 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 478 | 208 | 686 | 5409 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 1430 |  | 7557 | 699 |  | 7079 | 276 | -5409 | -5409 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 478 | 423 | 901 | 5409 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 1530 |  | 8162 | 826 |  | 7390 | 60 | -5905 | -5905 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 772 | 766 | 1538 | 5905 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251125 | November | 1630 |  | 8162 | 826 |  | 7390 | 60 | -5905 | -5905 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 772 | 766 | 1538 | 5905 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251125 | November | 1730 |  | 8162 | 826 |  | 7390 | 60 | -5905 | -5905 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 772 | 766 | 1538 | 5905 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251125 | November | 1830 |  | 7809 | 757 |  | 7209 | 60 | -5360 | -5360 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 600 | 697 | 1297 | 5360 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251125 | November | 1930 |  | 7809 | 757 |  | 7209 | 292 | -5360 | -5360 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 600 | 465 | 1065 | 5360 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 2030 |  | 7809 | 757 |  | 7209 | 524 | -5360 | -5360 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 600 | 233 | 833 | 5360 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 2130 | 8340 |  |  | 7969 |  |  | -2754 | -2754 | -2387 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 371 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 2230 | 8340 |  |  | 7969 |  |  | -2754 | -2754 | -2387 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 371 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251125 | November | 2330 | 7530 |  |  | 7353 |  |  | -1949 | -1949 | -1774 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 177 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0030 | 8103 |  |  | 7517 |  |  | -3789 | -3789 | -3163 | Critical Branch | Validation phase | 0 | 586 | NA | NA | NA | 0 | 1 | CH: 7678; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0130 | 8103 |  |  | 7517 |  |  | -3789 | -3789 | -3163 | Critical Branch | Validation phase | 0 | 586 | NA | NA | NA | 0 | 1 | CH: 7678; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0230 | 8103 |  |  | 7517 |  |  | -3789 | -3789 | -3163 | Critical Branch | Validation phase | 0 | 586 | NA | NA | NA | 0 | 1 | CH: 7678; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0330 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 0 | 526 | NA | NA | NA | 0 | 1 | CH: 7687; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0430 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 0 | 526 | NA | NA | NA | 0 | 1 | CH: 7687; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0530 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 0 | 526 | NA | NA | NA | 0 | 1 | CH: 7687; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0630 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 0 | 526 | NA | NA | NA | 0 | 1 | CH: 7687; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0730 | 8489 |  |  | 7994 |  |  | -5502 | -5502 | -4969 | Critical Branch | Validation phase | 0 | 495 | NA | NA | NA | 0 | 1 | CH: 8225; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0830 | 8489 |  |  | 7994 |  |  | -5502 | -5502 | -4969 | Critical Branch | Validation phase | 0 | 495 | NA | NA | NA | 0 | 1 | CH: 8225; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 0930 | 8307 |  |  | 7595 |  |  | 6778 | 177 | 7571 | Minimum Margin | Validation phase | 6601 | 712 | NA | NA | NA | 14965 | 1 | CH: 7554; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 1030 | 8327 |  |  | 7595 |  |  | 6778 | 197 | 7571 | Minimum Margin | Validation phase | 6581 | 732 | NA | NA | NA | 14945 | 1 | CH: 7554; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 1130 | 8327 |  |  | 7595 |  |  | 6778 | 197 | 7571 | Minimum Margin | Validation phase | 6581 | 732 | NA | NA | NA | 14945 | 1 | CH: 7554; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 1230 | 8325 |  |  | 6250 |  |  | 5301 | 195 | 7181 | Minimum Margin | Validation phase | 5106 | 2075 | NA | NA | NA | 14167 | 1 | CH: 7313; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251126 | November | 1330 | 8325 |  |  | 6250 |  |  | 5301 | 195 | 7181 | Minimum Margin | Validation phase | 5106 | 2075 | NA | NA | NA | 14167 | 1 | CH: 7313; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251126 | November | 1430 | 8361 |  |  | 6250 |  |  | 5301 | 231 | 7181 | Minimum Margin | Validation phase | 5070 | 2111 | NA | NA | NA | 14131 | 1 | CH: 7313; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - PRAZ VILLARODIN; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251126 | November | 1530 | 8293 |  |  | 7750 |  |  | -962 | -962 | -405 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 543 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251126 | November | 1630 | 8293 |  |  | 7871 |  |  | -962 | -962 | -525 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 422 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251126 | November | 1730 | 8293 |  |  | 7871 |  |  | -962 | -962 | -525 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 422 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251126 | November | 1830 | 8443 |  |  | 7955 |  |  | -1277 | -1277 | -773 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 488 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251126 | November | 1930 | 8443 |  |  | 7955 |  |  | -1277 | -1277 | -773 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 488 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN; IT: 0; IT: Forecasted security violation
20251126 | November | 2030 | 8443 |  |  | 7955 |  |  | -1277 | -1277 | -773 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 488 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 2130 | 8195 |  |  | 7815 |  |  | -4213 | -4213 | -3805 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 380 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 2230 | 8195 |  |  | 7815 |  |  | -4213 | -4213 | -3805 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 380 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251126 | November | 2330 | 7385 |  |  | 7201 |  |  | -3415 | -3415 | -3218 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 184 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - PRAZ VILLARODIN
20251127 | November | 0030 | 8041 |  |  | 7540 |  |  | -3467 | -3467 | -2923 | Critical Branch | Validation phase | 0 | 501 | NA | NA | NA | 0 | 1 | CH: 7764; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0130 | 8041 |  |  | 7540 |  |  | -3467 | -3467 | -2923 | Critical Branch | Validation phase | 0 | 501 | NA | NA | NA | 0 | 1 | CH: 7764; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0230 | 8041 |  |  | 7540 |  |  | -3467 | -3467 | -2923 | Critical Branch | Validation phase | 0 | 501 | NA | NA | NA | 0 | 1 | CH: 7764; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0330 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 0 | 497 | NA | NA | NA | 0 | 1 | CH: 7780; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0430 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 0 | 497 | NA | NA | NA | 0 | 1 | CH: 7780; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0530 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 0 | 497 | NA | NA | NA | 0 | 1 | CH: 7780; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0630 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 0 | 497 | NA | NA | NA | 0 | 1 | CH: 7780; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0730 | 8130 |  |  | 7779 |  |  | -4457 | -4457 | -4079 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 351 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0830 | 8130 |  |  | 7779 |  |  | -4457 | -4457 | -4079 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 351 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 0930 | 8193 |  |  | 7814 |  |  | -4262 | -4262 | -3858 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 379 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1030 | 8193 |  |  | 7814 |  |  | -4262 | -4262 | -3858 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 379 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1130 | 8193 |  |  | 7814 |  |  | -4262 | -4262 | -3858 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 379 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1230 | 8386 |  |  | 7665 |  |  | 2693 | 196 | 3504 | Minimum Margin | Validation phase | 2497 | 721 | NA | NA | NA | 6812 | 1 | CH: 7643; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1330 | 8386 |  |  | 7665 |  |  | 2693 | 196 | 3504 | Minimum Margin | Validation phase | 2497 | 721 | NA | NA | NA | 6812 | 1 | CH: 7643; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1430 | 8414 |  |  | 7665 |  |  | 2693 | 224 | 3504 | Minimum Margin | Validation phase | 2469 | 749 | NA | NA | NA | 6784 | 1 | CH: 7643; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE; FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1530 | 8190 |  |  | 7833 |  |  | -806 | -806 | -438 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1630 | 8190 |  |  | 7833 |  |  | -806 | -806 | -438 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1730 | 8190 |  |  | 7833 |  |  | -806 | -806 | -438 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1830 | 8190 |  |  | 7833 |  |  | -582 | -582 | -215 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 1930 | 8190 |  |  | 7833 |  |  | -582 | -582 | -215 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 2030 | 8190 |  |  | 7833 |  |  | -582 | -582 | -215 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 357 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 2130 | 8289 |  |  | 7889 |  |  | -3686 | -3686 | -3259 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 400 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 2230 | 8289 |  |  | 7889 |  |  | -3686 | -3686 | -3259 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 400 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251127 | November | 2330 | 7479 |  |  | 7273 |  |  | -2888 | -2888 | -2669 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 206 | NA | NA | NA | 0 | 1 | FR: 2985; FR: Outage - OUTAGE TD LA PRAZ
20251128 | November | 0030 | 7594 |  |  | 7335 |  |  | -2761 | -2761 | -2477 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 259 | NA | NA | NA | 0 | 1 | AT: 223; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0130 | 7594 |  |  | 7335 |  |  | -2761 | -2761 | -2477 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 259 | NA | NA | NA | 0 | 1 | AT: 223; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0230 | 7594 |  |  | 7335 |  |  | -2761 | -2761 | -2477 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 259 | NA | NA | NA | 0 | 1 | AT: 223; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0330 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 297 | NA | NA | NA | 0 | 1 | AT: 226; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0430 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 297 | NA | NA | NA | 0 | 1 | AT: 226; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0530 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 297 | NA | NA | NA | 0 | 1 | AT: 226; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0630 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 297 | NA | NA | NA | 0 | 1 | AT: 226; AT: 120; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0730 |  | 6832 | 680 |  | 6354 | 680 | -3571 | -3571 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 478 | 0 | 478 | 3571 | 1 | AT: 113; AT: 85; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0830 |  | 6832 | 680 |  | 6354 | 680 | -3571 | -3571 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 478 | 0 | 478 | 3571 | 1 | AT: 113; AT: 85; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 0930 | 7774 |  |  | 7280 |  |  | -3628 | -3628 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 494 | NA | NA | NA | 0 | 1 | AT: 243; AT: 105; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1030 | 7774 |  |  | 7280 |  |  | -3628 | -3628 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 494 | NA | NA | NA | 0 | 1 | AT: 243; AT: 105; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1130 | 7774 |  |  | 7280 |  |  | -3628 | -3628 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 494 | NA | NA | NA | 0 | 1 | AT: 243; AT: 105; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1230 | 7817 |  |  | 7302 |  |  | -3894 | -3894 | -3352 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 515 | NA | NA | NA | 0 | 1 | AT: 244; AT: 105; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1330 | 7817 |  |  | 7302 |  |  | -3894 | -3894 | -3352 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 515 | NA | NA | NA | 0 | 1 | AT: 244; AT: 105; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1430 | 7817 |  |  | 7302 |  |  | -3894 | -3894 | -3352 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 515 | NA | NA | NA | 0 | 1 | AT: 244; AT: 105; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1530 |  | 7527 | 801 |  | 6672 | 800 | -4485 | -4485 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 855 | 1 | 856 | 4485 | 1 | AT: 126; AT: 101; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1630 |  | 7577 | 801 |  | 6719 | 800 | -4537 | -4537 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 858 | 1 | 859 | 4537 | 1 | AT: 126; AT: 101; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1730 |  | 8474 | 801 |  | 7575 | 800 | -5473 | -5473 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 899 | 1 | 900 | 5473 | 1 | AT: 128; AT: 102; FR: 2985; FR: Outage - Outage TD LA PRAZ
20251128 | November | 1830 |  | 9650 | 959 |  | 9043 | 940 | -2853 | -2853 | 0 | Critical Branch | Critical Branch | 0 | NA | 607 | 19 | 626 | 2853 | 1 | AT: 147; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251128 | November | 1930 |  | 9650 | 959 |  | 9650 | 940 | -2853 | -2853 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 19 | 19 | 2853 | 1 | AT: 147; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251128 | November | 2030 |  | 9650 | 959 |  | 9650 | 940 | -2853 | -2853 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 19 | 19 | 2853 | 1 | AT: 147; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251128 | November | 2130 | 10240 |  |  | 9453 |  |  | -3059 | -3059 | -2272 | Critical Branch | Validation phase | 0 | 787 | NA | NA | NA | 0 | 1 | AT: 294; AT: 105; CH: 9203; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251128 | November | 2230 | 10240 |  |  | 9453 |  |  | -3059 | -3059 | -2272 | Critical Branch | Validation phase | 0 | 787 | NA | NA | NA | 0 | 1 | AT: 294; AT: 105; CH: 9203; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251128 | November | 2330 | 9430 |  |  | 8643 |  |  | -2244 | -2244 | -1457 | Critical Branch | Validation phase | 0 | 787 | NA | NA | NA | 0 | 1 | AT: 279; AT: 120; CH: 8393; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251129 | November | 0030 | 8526 |  |  | 8526 |  |  | -3508 | -3508 | -3508 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0130 | 8526 |  |  | 8526 |  |  | -3508 | -3508 | -3508 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0230 | 8526 |  |  | 8526 |  |  | -3508 | -3508 | -3508 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0330 | 8218 |  |  | 8218 |  |  | -3297 | -3297 | -3297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0430 | 8218 |  |  | 8218 |  |  | -3297 | -3297 | -3297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0530 | 8218 |  |  | 8218 |  |  | -3297 | -3297 | -3297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0630 | 8218 |  |  | 8218 |  |  | -3297 | -3297 | -3297 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20251129 | November | 0730 | 8240 |  |  | 8174 |  |  | -3443 | -3443 | -3377 | TTC Selection - LTTC | Validation phase | 0 | 66 | NA | NA | NA | 0 | 1 | CH: 7924; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 0830 | 8240 |  |  | 8174 |  |  | -3443 | -3443 | -3377 | TTC Selection - LTTC | Validation phase | 0 | 66 | NA | NA | NA | 0 | 1 | CH: 7924; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 0930 | 8240 |  |  | 8208 |  |  | -3613 | -3613 | -3581 | TTC Selection - LTTC | Validation phase | 0 | 32 | NA | NA | NA | 0 | 1 | CH: 7958; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1030 | 8240 |  |  | 8208 |  |  | -3613 | -3613 | -3581 | TTC Selection - LTTC | Validation phase | 0 | 32 | NA | NA | NA | 0 | 1 | CH: 7958; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1130 | 8240 |  |  | 8208 |  |  | -3613 | -3613 | -3581 | TTC Selection - LTTC | Validation phase | 0 | 32 | NA | NA | NA | 0 | 1 | CH: 7958; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1230 | 8240 |  |  | 8053 |  |  | -3532 | -3532 | -3345 | TTC Selection - LTTC | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | CH: 7803; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1330 | 8240 |  |  | 8053 |  |  | -3532 | -3532 | -3345 | TTC Selection - LTTC | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | CH: 7803; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1430 | 8240 |  |  | 8053 |  |  | -3532 | -3532 | -3345 | TTC Selection - LTTC | Validation phase | 0 | 187 | NA | NA | NA | 0 | 1 | CH: 7803; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1530 |  | 7776 | 678 |  | 7776 | 678 | -4141 | -4141 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 4141 | 0
20251129 | November | 1630 |  | 7776 | 678 |  | 7776 | 678 | -4141 | -4141 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 4141 | 0
20251129 | November | 1730 |  | 7776 | 678 |  | 7776 | 678 | -4141 | -4141 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 4141 | 0
20251129 | November | 1830 |  | 8235 | 89 |  | 8235 | 89 | -4208 | -4208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4208 | 0
20251129 | November | 1930 |  | 8235 | 89 |  | 8235 | 89 | -4208 | -4208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4208 | 0
20251129 | November | 2030 |  | 8235 | 89 |  | 8235 | 89 | -4208 | -4208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4208 | 0
20251129 | November | 2130 | 8240 |  |  | 8163 |  |  | -3279 | -3279 | -3202 | TTC Selection - LTTC | Validation phase | 0 | 77 | NA | NA | NA | 0 | 1 | CH: 7913; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 2230 | 8240 |  |  | 8163 |  |  | -3279 | -3279 | -3202 | TTC Selection - LTTC | Validation phase | 0 | 77 | NA | NA | NA | 0 | 1 | CH: 7913; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 2330 | 7430 |  |  | 7353 |  |  | -2483 | -2483 | -2406 | TTC Selection - LTTC | Validation phase | 0 | 77 | NA | NA | NA | 0 | 1 | CH: 7103; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251130 | November | 0030 | 10606 |  |  | 9589 |  |  | -3671 | -3671 | -2654 | Critical Branch | Validation phase | 0 | 1017 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9339; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0130 | 10606 |  |  | 9589 |  |  | -3671 | -3671 | -2654 | Critical Branch | Validation phase | 0 | 1017 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9339; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0230 | 10606 |  |  | 9589 |  |  | -3671 | -3671 | -2654 | Critical Branch | Validation phase | 0 | 1017 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9339; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0330 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 0 | 1145 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9192; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0430 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 0 | 1145 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9192; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0530 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 0 | 1145 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9192; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0630 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 0 | 1145 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9192; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0730 | 10587 |  |  | 9600 |  |  | -2438 | -2438 | -1451 | Critical Branch | Validation phase | 0 | 987 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9350; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0830 | 10587 |  |  | 9600 |  |  | -2438 | -2438 | -1451 | Critical Branch | Validation phase | 0 | 987 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9350; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0930 | 10443 |  |  | 9592 |  |  | -2134 | -2134 | -1283 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9342; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 1030 | 10443 |  |  | 9592 |  |  | -2134 | -2134 | -1283 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9342; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 1130 | 10443 |  |  | 9592 |  |  | -2134 | -2134 | -1283 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9342; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 1230 | 10380 |  |  | 9451 |  |  | -2017 | -2017 | -1088 | Critical Branch | Validation phase | 0 | 929 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9201; CH: Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251130 | November | 1330 | 10380 |  |  | 9451 |  |  | -2017 | -2017 | -1088 | Critical Branch | Validation phase | 0 | 929 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9201; CH: Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251130 | November | 1430 | 10380 |  |  | 9451 |  |  | -2017 | -2017 | -1088 | Critical Branch | Validation phase | 0 | 929 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9201; CH: Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251130 | November | 1530 |  | 9244 | 860 |  | 9233 | 860 | -3752 | -3752 | 0 | Critical Branch | Critical Branch | 0 | NA | 11 | 0 | 11 | 3752 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 115; AT: Reduction because NTC over thermal limit on border
20251130 | November | 1630 |  | 9244 | 860 |  | 9233 | 860 | -3752 | -3752 | 0 | Critical Branch | Critical Branch | 0 | NA | 11 | 0 | 11 | 3752 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 115; AT: Reduction because NTC over thermal limit on border
20251130 | November | 1730 |  | 9244 | 860 |  | 9233 | 860 | -3752 | -3752 | 0 | Critical Branch | Critical Branch | 0 | NA | 11 | 0 | 11 | 3752 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 115; AT: Reduction because NTC over thermal limit on border
20251130 | November | 1830 | 10511 |  |  | 9940 |  |  | -4416 | -4416 | -3849 | Critical Branch | Validation phase | 0 | 571 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9701; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 1930 | 10511 |  |  | 9940 |  |  | -4416 | -4416 | -3849 | Critical Branch | Validation phase | 0 | 571 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9701; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 2030 | 10511 |  |  | 9940 |  |  | -4416 | -4416 | -3849 | Critical Branch | Validation phase | 0 | 571 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9701; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 2130 | 10745 |  |  | 10032 |  |  | -3780 | -3780 | -3072 | Critical Branch | Validation phase | 0 | 713 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9796; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 2230 | 10745 |  |  | 10032 |  |  | -3780 | -3780 | -3072 | Critical Branch | Validation phase | 0 | 713 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9796; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 2330 | 10745 |  |  | 10032 |  |  | -3780 | -3780 | -3072 | Critical Branch | Validation phase | 0 | 713 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9796; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0030 | 10348 |  |  | 9748 |  |  | -5299 | -5299 | -4701 | Critical Branch | Validation phase | 0 | 600 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9503; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0130 | 10348 |  |  | 9748 |  |  | -5299 | -5299 | -4701 | Critical Branch | Validation phase | 0 | 600 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9503; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0230 | 10348 |  |  | 9748 |  |  | -5299 | -5299 | -4701 | Critical Branch | Validation phase | 0 | 600 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9503; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0330 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 0 | 452 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9655; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0430 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 0 | 452 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9655; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0530 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 0 | 452 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9655; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0630 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 0 | 452 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9655; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0730 |  | 9503 | 894 |  | 9503 | 884 | -2676 | -2676 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 2676 | 1 | AT: 144; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 0830 |  | 9503 | 894 |  | 9503 | 884 | -2676 | -2676 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 2676 | 1 | AT: 144; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 0930 | 9515 |  |  | 9490 |  |  | -2277 | -2277 | -2252 | Critical Branch | Validation phase | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 272; AT: 105; CH: 9240; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251201 | December | 1030 | 9515 |  |  | 9490 |  |  | -2277 | -2277 | -2252 | Critical Branch | Validation phase | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 272; AT: 105; CH: 9240; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251201 | December | 1130 | 9515 |  |  | 9490 |  |  | -2277 | -2277 | -2252 | Critical Branch | Validation phase | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 272; AT: 105; CH: 9240; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251201 | December | 1230 |  | 8932 | 862 |  | 8932 | 856 | -2009 | -2009 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 6 | 6 | 2009 | 1 | AT: 135; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1330 |  | 8932 | 862 |  | 8932 | 856 | -2009 | -2009 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 6 | 6 | 2009 | 1 | AT: 135; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1430 |  | 8932 | 862 |  | 8932 | 856 | -2009 | -2009 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 6 | 6 | 2009 | 1 | AT: 135; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1530 |  | 9591 | 921 |  | 9591 | 907 | -2774 | -2774 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 2774 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1630 |  | 9591 | 921 |  | 9591 | 907 | -2774 | -2774 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 2774 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1730 |  | 9591 | 921 |  | 9591 | 907 | -2774 | -2774 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 2774 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1830 |  | 9618 | 916 |  | 9618 | 903 | -5196 | -5196 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 13 | 13 | 5196 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 1930 |  | 9618 | 916 |  | 9618 | 903 | -5196 | -5196 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 13 | 13 | 5196 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 2030 |  | 9618 | 916 |  | 9618 | 903 | -5196 | -5196 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 13 | 13 | 5196 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251201 | December | 2130 | 10064 |  |  | 9480 |  |  | -3921 | -3921 | -3337 | Critical Branch | Validation phase | 0 | 584 | NA | NA | NA | 0 | 1 | AT: 289; AT: 105; CH: 9230; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251201 | December | 2230 | 10064 |  |  | 9480 |  |  | -3921 | -3921 | -3337 | Critical Branch | Validation phase | 0 | 584 | NA | NA | NA | 0 | 1 | AT: 289; AT: 105; CH: 9230; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251201 | December | 2330 | 9254 |  |  | 8670 |  |  | -3105 | -3105 | -2521 | Critical Branch | Validation phase | 0 | 584 | NA | NA | NA | 0 | 1 | AT: 274; AT: 120; CH: 8420; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251202 | December | 0030 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0130 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0230 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0330 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0430 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0530 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0630 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251202 | December | 0730 |  | 9772 | 921 |  | 9772 | 907 | -4840 | -4840 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 4840 | 1 | AT: 149; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 0830 |  | 9772 | 921 |  | 9772 | 907 | -4840 | -4840 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 4840 | 1 | AT: 149; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 0930 |  | 9270 | 932 |  | 9270 | 916 | -2190 | -2190 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 2190 | 1 | AT: 141; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1030 |  | 9270 | 932 |  | 9270 | 916 | -2190 | -2190 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 2190 | 1 | AT: 141; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1130 |  | 9270 | 932 |  | 9270 | 916 | -2190 | -2190 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 2190 | 1 | AT: 141; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1230 |  | 9375 | 921 |  | 9375 | 907 | -5385 | -5385 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 5385 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1330 |  | 9375 | 921 |  | 9375 | 907 | -5385 | -5385 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 5385 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1430 |  | 9375 | 921 |  | 9375 | 907 | -5385 | -5385 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 5385 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1530 |  | 9383 | 872 |  | 9383 | 865 | -3015 | -3015 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 7 | 7 | 3015 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1630 |  | 9383 | 872 |  | 9383 | 865 | -3015 | -3015 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 7 | 7 | 3015 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1730 |  | 9383 | 872 |  | 9383 | 865 | -3015 | -3015 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 7 | 7 | 3015 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1830 |  | 9669 | 902 |  | 9669 | 890 | 3734 | 34 | 0 | Minimum Margin | Minimum Margin | 3700 | NA | 0 | 12 | 12 | -34 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 1930 |  | 9669 | 902 |  | 9669 | 890 | 3734 | 34 | 0 | Minimum Margin | Minimum Margin | 3700 | NA | 0 | 12 | 12 | -34 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 2030 |  | 9669 | 902 |  | 9669 | 890 | 3734 | 34 | 0 | Minimum Margin | Minimum Margin | 3700 | NA | 0 | 12 | 12 | -34 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251202 | December | 2130 | 10100 |  |  | 9787 |  |  | -2886 | -2886 | -2573 | Critical Branch | Validation phase | 0 | 313 | NA | NA | NA | 0 | 1 | AT: 290; AT: 105; CH: 9537; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251202 | December | 2230 | 10100 |  |  | 9787 |  |  | -2886 | -2886 | -2573 | Critical Branch | Validation phase | 0 | 313 | NA | NA | NA | 0 | 1 | AT: 290; AT: 105; CH: 9537; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251202 | December | 2330 | 9290 |  |  | 8977 |  |  | -2061 | -2061 | -1748 | Critical Branch | Validation phase | 0 | 313 | NA | NA | NA | 0 | 1 | AT: 275; AT: 120; CH: 8727; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0030 | 9978 |  |  | 9156 |  |  | -2506 | -2506 | -1684 | Critical Branch | Validation phase | 0 | 822 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8906; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0130 | 9978 |  |  | 9156 |  |  | -2506 | -2506 | -1684 | Critical Branch | Validation phase | 0 | 822 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8906; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0230 | 9978 |  |  | 9156 |  |  | -2506 | -2506 | -1684 | Critical Branch | Validation phase | 0 | 822 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8906; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0330 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 0 | 622 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8990; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0430 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 0 | 622 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8990; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0530 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 0 | 622 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8990; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0630 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 0 | 622 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8990; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0730 |  | 9335 | 878 |  | 9335 | 870 | -3386 | -3386 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 8 | 8 | 3386 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 0830 |  | 9335 | 878 |  | 9335 | 870 | -3386 | -3386 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 8 | 8 | 3386 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 0930 |  | 9678 | 899 |  | 9678 | 888 | -3466 | -3466 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 11 | 11 | 3466 | 1 | AT: 147; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1030 |  | 9678 | 899 |  | 9678 | 888 | -3466 | -3466 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 11 | 11 | 3466 | 1 | AT: 147; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1130 |  | 9678 | 899 |  | 9678 | 888 | -3466 | -3466 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 11 | 11 | 3466 | 1 | AT: 147; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1230 |  | 9421 | 883 |  | 9421 | 874 | -2923 | -2923 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 9 | 9 | 2923 | 1 | AT: 143; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1330 |  | 9421 | 883 |  | 9421 | 863 | -2923 | -2923 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 20 | 20 | 2923 | 1 | AT: 143; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1430 |  | 9421 | 883 |  | 9421 | 593 | -2923 | -2923 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 290 | 290 | 2923 | 1 | AT: 143; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1530 |  | 9683 | 864 |  | 9682 | 317 | 4105 | 150 | 0 | Minimum Margin | Minimum Margin | 3955 | NA | 1 | 547 | 548 | -150 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251203 | December | 1630 |  | 9683 | 864 |  | 9683 | 53 | 4105 | 151 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3954 | NA | 0 | 811 | 811 | -151 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; IT: 0; IT: Forecasted security violation
20251203 | December | 1730 |  | 9567 | 854 |  | 9567 | 53 | 4105 | 35 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4070 | NA | 0 | 801 | 801 | -35 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; IT: 0; IT: Forecasted security violation
20251203 | December | 1830 |  | 9090 | 794 |  | 9090 | 53 | 4757 | 35 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4722 | NA | 0 | 741 | 741 | -35 | 1 | AT: 137; AT: 101; IT: 0; IT: Forecasted security violation
20251203 | December | 1930 |  | 9090 | 794 |  | 9090 | 53 | 4757 | 35 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4722 | NA | 0 | 741 | 741 | -35 | 1 | AT: 137; AT: 101; IT: 0; IT: Forecasted security violation
20251203 | December | 2030 |  | 9090 | 794 |  | 9090 | 297 | 4757 | 35 | 0 | Minimum Margin | Minimum Margin | 4722 | NA | 0 | 497 | 497 | -35 | 1 | AT: 137; AT: 101
20251203 | December | 2130 | 10485 |  |  | 9798 |  |  | -4258 | -4258 | -3571 | Critical Branch | Smoothing ramp | 0 | 687 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9548; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251203 | December | 2230 | 10485 |  |  | 9798 |  |  | -4258 | -4258 | -3571 | Critical Branch | Smoothing ramp | 0 | 687 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9548; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251203 | December | 2330 | 9675 |  |  | 8988 |  |  | -3445 | -3445 | -2758 | Critical Branch | Validation phase | 0 | 687 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8738; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 0030 | 10195 |  |  | 9344 |  |  | -2784 | -2784 | -1933 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9094; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0130 | 10195 |  |  | 9344 |  |  | -2784 | -2784 | -1933 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9094; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0230 | 10195 |  |  | 9344 |  |  | -2784 | -2784 | -1933 | Critical Branch | Validation phase | 0 | 851 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9094; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0330 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 0 | 659 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9018; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0430 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 0 | 659 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9018; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0530 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 0 | 659 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9018; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0630 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 0 | 659 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9018; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0730 |  | 10333 | 113 |  | 9900 | 108 | -3002 | -3002 | 0 | Critical Branch | Validation phase | 0 | NA | 433 | 5 | 438 | 3002 | 1 | AT: 151; AT: 97; CH: 9967; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 0830 |  | 10333 | 113 |  | 9900 | 108 | -3002 | -3002 | 0 | Critical Branch | Validation phase | 0 | NA | 433 | 5 | 438 | 3002 | 1 | AT: 151; AT: 97; CH: 9967; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 0930 | 10412 |  |  | 9539 |  |  | -6110 | -6110 | -5237 | Critical Branch | Validation phase | 0 | 873 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105; CH: 9289; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251204 | December | 1030 | 10412 |  |  | 9539 |  |  | -6110 | -6110 | -5237 | Critical Branch | Validation phase | 0 | 873 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105; CH: 9289; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251204 | December | 1130 | 10412 |  |  | 9539 |  |  | -6110 | -6110 | -5237 | Critical Branch | Validation phase | 0 | 873 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105; CH: 9289; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251204 | December | 1230 |  | 10078 | 112 |  | 9397 | 105 | -3079 | -3079 | 0 | Critical Branch | Validation phase | 0 | NA | 681 | 7 | 688 | 3079 | 1 | AT: 147; AT: 96; CH: 9457; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 1330 |  | 10078 | 112 |  | 9397 | 105 | -3079 | -3079 | 0 | Critical Branch | Validation phase | 0 | NA | 681 | 7 | 688 | 3079 | 1 | AT: 147; AT: 96; CH: 9457; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 1430 |  | 10078 | 112 |  | 9397 | 105 | -3079 | -3079 | 0 | Critical Branch | Validation phase | 0 | NA | 681 | 7 | 688 | 3079 | 1 | AT: 147; AT: 96; CH: 9457; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 1530 | 10515 |  |  | 9458 |  |  | -4513 | -4513 | -3456 | Critical Branch | Validation phase | 0 | 1057 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9208; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1630 | 10515 |  |  | 9458 |  |  | -4513 | -4513 | -3456 | Critical Branch | Validation phase | 0 | 1057 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9208; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1730 | 10515 |  |  | 9458 |  |  | -4513 | -4513 | -3456 | Critical Branch | Validation phase | 0 | 1057 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9208; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1830 | 10260 |  |  | 9965 |  |  | -1750 | -1750 | -1455 | Critical Branch | Validation phase | 0 | 295 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105; CH: 9715; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1930 | 10260 |  |  | 9965 |  |  | -1750 | -1750 | -1455 | Critical Branch | Validation phase | 0 | 295 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105; CH: 9715; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2030 | 10260 |  |  | 9965 |  |  | -1750 | -1750 | -1455 | Critical Branch | Validation phase | 0 | 295 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105; CH: 9715; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2130 | 10002 |  |  | 9285 |  |  | -2548 | -2548 | -1831 | Critical Branch | Validation phase | 0 | 717 | NA | NA | NA | 0 | 1 | AT: 287; AT: 105; CH: 9035; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2230 | 10002 |  |  | 9285 |  |  | -2548 | -2548 | -1831 | Critical Branch | Validation phase | 0 | 717 | NA | NA | NA | 0 | 1 | AT: 287; AT: 105; CH: 9035; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2330 | 9192 |  |  | 8475 |  |  | -1724 | -1724 | -1007 | Critical Branch | Validation phase | 0 | 717 | NA | NA | NA | 0 | 1 | AT: 272; AT: 120; CH: 8225; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0030 | 10681 |  |  | 10170 |  |  | -2440 | -2440 | -1929 | Critical Branch | Validation phase | 0 | 511 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9938; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251205 | December | 0130 | 10681 |  |  | 10170 |  |  | -2440 | -2440 | -1929 | Critical Branch | Validation phase | 0 | 511 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9938; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251205 | December | 0230 | 10681 |  |  | 10170 |  |  | -2440 | -2440 | -1929 | Critical Branch | Validation phase | 0 | 511 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9938; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251205 | December | 0330 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Validation phase | 0 | 512 | NA | NA | NA | 0 | 1 | AT: 283; AT: 120; CH: 8782; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0430 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Validation phase | 0 | 512 | NA | NA | NA | 0 | 1 | AT: 283; AT: 120; CH: 8782; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0530 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Smoothing ramp | 0 | 512 | NA | NA | NA | 0 | 1 | AT: 283; AT: 120; CH: 8782; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0630 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Smoothing ramp | 0 | 512 | NA | NA | NA | 0 | 1 | AT: 283; AT: 120; CH: 8782; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0730 |  | 9537 | 878 |  | 9537 | 322 | -5650 | -5650 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 556 | 556 | 5650 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251205 | December | 0830 |  | 9537 | 878 |  | 8441 | 53 | -5650 | -5650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1096 | 825 | 1921 | 5650 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; IT: 0; IT: Forecasted security violation
20251205 | December | 0930 |  | 7794 | 673 |  | 6943 | 53 | -1282 | -1282 | 0 | Critical Branch | Validation phase | 0 | NA | 851 | 620 | 1471 | 1282 | 1 | AT: 254; AT: 85; CH: 7639; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE; IT: 0; IT: Forecasted security violation
20251205 | December | 1030 |  | 7794 | 673 |  | 6943 | 53 | -1282 | -1282 | 0 | Critical Branch | Validation phase | 0 | NA | 851 | 620 | 1471 | 1282 | 1 | AT: 254; AT: 85; CH: 7639; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE; IT: 0; IT: Forecasted security violation
20251205 | December | 1130 |  | 7794 | 673 |  | 6943 | 241 | -1282 | -1282 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 851 | 432 | 1283 | 1282 | 1 | AT: 254; AT: 85; CH: 7639; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1230 |  | 9482 | 818 |  | 8316 | 499 | -3897 | -3897 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 1166 | 319 | 1485 | 3897 | 1 | AT: 166; AT: 104; CH: 8821; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1330 |  | 9482 | 818 |  | 8316 | 717 | -3897 | -3897 | 0 | Critical Branch | Validation phase | 0 | NA | 1166 | 101 | 1267 | 3897 | 1 | AT: 166; AT: 104; CH: 8821; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1430 |  | 9482 | 818 |  | 8316 | 499 | -3897 | -3897 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 1166 | 319 | 1485 | 3897 | 1 | AT: 166; AT: 104; CH: 8821; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1530 |  | 9210 | 835 |  | 8571 | 295 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 639 | 540 | 1179 | 3169 | 1 | AT: 140; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9158; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1630 |  | 9210 | 835 |  | 8571 | 53 | -3169 | -3169 | 0 | Critical Branch | Validation phase | 0 | NA | 639 | 782 | 1421 | 3169 | 1 | AT: 140; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9158; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE; IT: 0; IT: Forecasted security violation
20251205 | December | 1730 |  | 9210 | 835 |  | 8571 | 53 | -3169 | -3169 | 0 | Critical Branch | Validation phase | 0 | NA | 639 | 782 | 1421 | 3169 | 1 | AT: 140; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9158; CH: Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE; IT: 0; IT: Forecasted security violation
20251205 | December | 1830 |  | 9032 | 650 |  | 9031 | 38 | -6266 | -6266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 612 | 613 | 6266 | 1 | AT: 280; AT: 105; IT: 0; IT: Forecasted security violation
20251205 | December | 1930 |  | 9032 | 650 |  | 9031 | 241 | -6266 | -6266 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 409 | 410 | 6266 | 1 | AT: 280; AT: 105
20251205 | December | 2030 |  | 9032 | 650 |  | 9031 | 444 | -6266 | -6266 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 206 | 207 | 6266 | 1 | AT: 280; AT: 105
20251205 | December | 2130 | 9740 |  |  | 8894 |  |  | -2646 | -2646 | -1800 | Critical Branch | Smoothing ramp | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 279; AT: 105; CH: 8644; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 2230 | 9740 |  |  | 8894 |  |  | -2646 | -2646 | -1800 | Critical Branch | Validation phase | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 279; AT: 105; CH: 8644; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 2330 | 8930 |  |  | 8084 |  |  | -1826 | -1826 | -980 | Critical Branch | Validation phase | 0 | 846 | NA | NA | NA | 0 | 1 | AT: 264; AT: 120; CH: 7834; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0030 | 10488 |  |  | 9686 |  |  | -2472 | -2472 | -1670 | Critical Branch | Validation phase | 0 | 802 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9439; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0130 | 10488 |  |  | 9686 |  |  | -2472 | -2472 | -1670 | Critical Branch | Validation phase | 0 | 802 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9439; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0230 | 10488 |  |  | 9686 |  |  | -2472 | -2472 | -1670 | Critical Branch | Validation phase | 0 | 802 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9439; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0330 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251206 | December | 0430 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251206 | December | 0530 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251206 | December | 0630 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251206 | December | 0730 | 9539 |  |  | 9523 |  |  | -5922 | -5922 | -5906 | Critical Branch | Validation phase | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 297; AT: 105; CH: 9273; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0830 | 9539 |  |  | 9523 |  |  | -5922 | -5922 | -5906 | Critical Branch | Validation phase | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 297; AT: 105; CH: 9273; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0930 | 9659 |  |  | 9657 |  |  | -5822 | -5822 | -5821 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251206 | December | 1030 | 9659 |  |  | 9657 |  |  | -5822 | -5822 | -5821 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251206 | December | 1130 | 9659 |  |  | 9657 |  |  | -5822 | -5822 | -5821 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251206 | December | 1230 |  | 9186 | 832 |  | 9173 | 832 | -5086 | -5086 | 0 | Critical Branch | Critical Branch | 0 | NA | 13 | 0 | 13 | 5086 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 101; AT: Reduction because NTC over thermal limit on border
20251206 | December | 1330 |  | 9186 | 832 |  | 9173 | 832 | -5086 | -5086 | 0 | Critical Branch | Critical Branch | 0 | NA | 13 | 0 | 13 | 5086 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 101; AT: Reduction because NTC over thermal limit on border
20251206 | December | 1430 |  | 9186 | 832 |  | 9173 | 832 | -5086 | -5086 | 0 | Critical Branch | Critical Branch | 0 | NA | 13 | 0 | 13 | 5086 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 101; AT: Reduction because NTC over thermal limit on border
20251206 | December | 1530 | 9581 |  |  | 9581 |  |  | -5348 | -5348 | -5348 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 299; AT: 105
20251206 | December | 1630 | 9581 |  |  | 9581 |  |  | -5348 | -5348 | -5348 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 299; AT: 105
20251206 | December | 1730 | 10381 |  |  | 10381 |  |  | -6195 | -6195 | -6195 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 299; AT: 105
20251206 | December | 1830 | 10410 |  |  | 10410 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105
20251206 | December | 1930 | 10410 |  |  | 10410 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105
20251206 | December | 2030 | 10410 |  |  | 10410 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105
20251206 | December | 2130 | 10403 |  |  | 9890 |  |  | -3075 | -3075 | -2562 | Critical Branch | Validation phase | 0 | 513 | NA | NA | NA | 0 | 1 | AT: 299; AT: 105; CH: 9640; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251206 | December | 2230 | 10403 |  |  | 9890 |  |  | -3075 | -3075 | -2562 | Critical Branch | Validation phase | 0 | 513 | NA | NA | NA | 0 | 1 | AT: 299; AT: 105; CH: 9640; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251206 | December | 2330 | 9593 |  |  | 9080 |  |  | -2232 | -2232 | -1719 | Critical Branch | Validation phase | 0 | 513 | NA | NA | NA | 0 | 1 | AT: 284; AT: 120; CH: 8830; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0030 | 9682 |  |  | 9151 |  |  | -2941 | -2941 | -2410 | Critical Branch | Validation phase | 0 | 531 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8901; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0130 | 9682 |  |  | 9151 |  |  | -2941 | -2941 | -2410 | Critical Branch | Validation phase | 0 | 531 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8901; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0230 | 9682 |  |  | 9151 |  |  | -2941 | -2941 | -2410 | Critical Branch | Validation phase | 0 | 531 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 8901; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0330 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 0 | 146 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9619; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0430 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 0 | 146 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9619; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0530 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 0 | 146 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9619; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0630 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 0 | 146 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9619; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0730 | 10479 |  |  | 10234 |  |  | -2837 | -2837 | -2595 | Critical Branch | Validation phase | 0 | 245 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 10005; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0830 | 10479 |  |  | 10234 |  |  | -2837 | -2837 | -2595 | Critical Branch | Validation phase | 0 | 245 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 10005; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0930 | 10416 |  |  | 10390 |  |  | -2641 | -2641 | -2618 | Critical Branch | Critical Branch | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251207 | December | 1030 | 10416 |  |  | 10390 |  |  | -2641 | -2641 | -2618 | Critical Branch | Critical Branch | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251207 | December | 1130 | 10416 |  |  | 10390 |  |  | -2641 | -2641 | -2618 | Critical Branch | Critical Branch | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251207 | December | 1230 | 10132 |  |  | 10115 |  |  | -2994 | -2994 | -2978 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251207 | December | 1330 | 10132 |  |  | 10115 |  |  | -2994 | -2994 | -2978 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251207 | December | 1430 | 10132 |  |  | 10115 |  |  | -2994 | -2994 | -2978 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251207 | December | 1530 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251207 | December | 1630 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251207 | December | 1730 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251207 | December | 1830 | 10028 |  |  | 9389 |  |  | -3354 | -3354 | -2715 | Critical Branch | Validation phase | 0 | 639 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9139; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251207 | December | 1930 | 10028 |  |  | 9389 |  |  | -3354 | -3354 | -2715 | Critical Branch | Validation phase | 0 | 639 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9139; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251207 | December | 2030 | 10028 |  |  | 9389 |  |  | -3354 | -3354 | -2715 | Critical Branch | Validation phase | 0 | 639 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9139; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251207 | December | 2130 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251207 | December | 2230 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251207 | December | 2330 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251208 | December | 0030 | 10403 |  |  | 10092 |  |  | -4964 | -4964 | -4659 | Critical Branch | Validation phase | 0 | 311 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9858; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251208 | December | 0130 | 10403 |  |  | 10092 |  |  | -4964 | -4964 | -4659 | Critical Branch | Validation phase | 0 | 311 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9858; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251208 | December | 0230 | 10403 |  |  | 10092 |  |  | -4964 | -4964 | -4659 | Critical Branch | Validation phase | 0 | 311 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9858; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251208 | December | 0330 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251208 | December | 0430 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251208 | December | 0530 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251208 | December | 0630 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251208 | December | 0730 | 9242 |  |  | 9241 |  |  | -4813 | -4813 | -4812 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 273; AT: 120
20251208 | December | 0830 | 9242 |  |  | 9241 |  |  | -4813 | -4813 | -4812 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 273; AT: 120
20251208 | December | 0930 | 8996 |  |  | 8996 |  |  | -6142 | -6142 | -6142 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 266; AT: 120
20251208 | December | 1030 | 8996 |  |  | 8996 |  |  | -6142 | -6142 | -6142 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 266; AT: 120
20251208 | December | 1130 | 8996 |  |  | 8996 |  |  | -6142 | -6142 | -6142 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 266; AT: 120
20251208 | December | 1230 |  | 9584 | 770 |  | 9562 | 770 | -5748 | -5748 | 0 | Critical Branch | Critical Branch | 0 | NA | 22 | 0 | 22 | 5748 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 118; AT: Reduction because NTC over thermal limit on border
20251208 | December | 1330 |  | 9584 | 770 |  | 9562 | 770 | -5748 | -5748 | 0 | Critical Branch | Critical Branch | 0 | NA | 22 | 0 | 22 | 5748 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 118; AT: Reduction because NTC over thermal limit on border
20251208 | December | 1430 |  | 9584 | 770 |  | 9562 | 770 | -5748 | -5748 | 0 | Critical Branch | Critical Branch | 0 | NA | 22 | 0 | 22 | 5748 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 118; AT: Reduction because NTC over thermal limit on border
20251208 | December | 1530 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251208 | December | 1630 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251208 | December | 1730 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251208 | December | 1830 |  | 9733 | 810 |  | 9706 | 810 | -6514 | -6514 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 6514 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border
20251208 | December | 1930 |  | 9733 | 810 |  | 9706 | 810 | -6514 | -6514 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 6514 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border
20251208 | December | 2030 |  | 9733 | 810 |  | 9706 | 810 | -6514 | -6514 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 6514 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border
20251208 | December | 2130 | 9867 |  |  | 9541 |  |  | -2783 | -2783 | -2457 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9291; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251208 | December | 2230 | 9867 |  |  | 9541 |  |  | -2783 | -2783 | -2457 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9291; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251208 | December | 2330 | 9867 |  |  | 9541 |  |  | -2783 | -2783 | -2457 | Critical Branch | Validation phase | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9291; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0030 | 9352 |  |  | 8975 |  |  | -2984 | -2984 | -2607 | Critical Branch | Validation phase | 0 | 377 | NA | NA | NA | 0 | 1 | AT: 277; AT: 120; CH: 8725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0130 | 9352 |  |  | 8975 |  |  | -2984 | -2984 | -2607 | Critical Branch | Validation phase | 0 | 377 | NA | NA | NA | 0 | 1 | AT: 277; AT: 120; CH: 8725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0230 | 9352 |  |  | 8975 |  |  | -2984 | -2984 | -2607 | Critical Branch | Validation phase | 0 | 377 | NA | NA | NA | 0 | 1 | AT: 277; AT: 120; CH: 8725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0330 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 273; AT: 120; CH: 8481; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0430 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 273; AT: 120; CH: 8481; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0530 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 273; AT: 120; CH: 8481; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0630 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 0 | 505 | NA | NA | NA | 0 | 1 | AT: 273; AT: 120; CH: 8481; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0730 | 9795 |  |  | 9531 |  |  | -6252 | -6252 | -5988 | Critical Branch | Validation phase | 0 | 264 | NA | NA | NA | 0 | 1 | AT: 285; AT: 105; CH: 9281; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0830 | 9795 |  |  | 9531 |  |  | -6252 | -6252 | -5988 | Critical Branch | Validation phase | 0 | 264 | NA | NA | NA | 0 | 1 | AT: 285; AT: 105; CH: 9281; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0930 | 9785 |  |  | 9785 |  |  | -2572 | -2572 | -2572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 105
20251209 | December | 1030 | 9785 |  |  | 9785 |  |  | -2572 | -2572 | -2572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 105
20251209 | December | 1130 | 9785 |  |  | 9785 |  |  | -2572 | -2572 | -2572 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 105
20251209 | December | 1230 | 9956 |  |  | 9956 |  |  | -2729 | -2729 | -2728 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 286; AT: 105
20251209 | December | 1330 | 9956 |  |  | 9956 |  |  | -2729 | -2729 | -2728 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 286; AT: 105
20251209 | December | 1430 | 9956 |  |  | 9956 |  |  | -2729 | -2729 | -2728 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 286; AT: 105
20251209 | December | 1530 |  | 9910 | 727 |  | 9900 | 727 | -6577 | -6577 | 0 | Critical Branch | Critical Branch | 0 | NA | 10 | 0 | 10 | 6577 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 104; AT: Reduction because NTC over thermal limit on border
20251209 | December | 1630 |  | 9910 | 727 |  | 9900 | 727 | -6577 | -6577 | 0 | Critical Branch | Critical Branch | 0 | NA | 10 | 0 | 10 | 6577 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 104; AT: Reduction because NTC over thermal limit on border
20251209 | December | 1730 |  | 9910 | 727 |  | 9900 | 727 | -6577 | -6577 | 0 | Critical Branch | Critical Branch | 0 | NA | 10 | 0 | 10 | 6577 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 104; AT: Reduction because NTC over thermal limit on border
20251209 | December | 1830 | 10410 |  |  | 9900 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 510 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105; CH: 9650; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 1930 | 10410 |  |  | 9900 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 510 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105; CH: 9650; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 2030 | 10410 |  |  | 9900 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 510 | NA | NA | NA | 0 | 1 | AT: 300; AT: 105; CH: 9650; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 2130 | 10253 |  |  | 10253 |  |  | -5645 | -5645 | -5645 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105
20251209 | December | 2230 | 10253 |  |  | 10253 |  |  | -5645 | -5645 | -5645 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105
20251209 | December | 2330 | 9443 |  |  | 9443 |  |  | -4831 | -4831 | -4831 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 280; AT: 120
20251210 | December | 0030 | 10210 |  |  | 10191 |  |  | -5017 | -5017 | -5004 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0130 | 10210 |  |  | 10191 |  |  | -5017 | -5017 | -5004 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0230 | 10210 |  |  | 10191 |  |  | -5017 | -5017 | -5004 | Critical Branch | Critical Branch | 0 | 19 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0330 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0430 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0530 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0630 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251210 | December | 0730 |  | 9234 | 673 |  | 9233 | 673 | -6352 | -6352 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 6352 | 1 | AT: 287; AT: 105
20251210 | December | 0830 |  | 9234 | 673 |  | 9233 | 673 | -6352 | -6352 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 6352 | 1 | AT: 287; AT: 105
20251210 | December | 0930 |  | 8596 | 786 |  | 8595 | 786 | -4916 | -4916 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4916 | 1 | AT: 266; AT: 102
20251210 | December | 1030 |  | 8596 | 786 |  | 8595 | 786 | -4916 | -4916 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4916 | 1 | AT: 266; AT: 102
20251210 | December | 1130 |  | 8596 | 786 |  | 8595 | 786 | -4916 | -4916 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 4916 | 1 | AT: 266; AT: 102
20251210 | December | 1230 |  | 9007 | 759 |  | 9006 | 759 | -2948 | -2948 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2948 | 1 | AT: 279; AT: 103
20251210 | December | 1330 |  | 9007 | 759 |  | 9006 | 759 | -2948 | -2948 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2948 | 1 | AT: 279; AT: 103
20251210 | December | 1430 |  | 9007 | 759 |  | 9006 | 759 | -2948 | -2948 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2948 | 1 | AT: 279; AT: 103
20251210 | December | 1530 |  | 9334 | 899 |  | 9334 | 888 | -6453 | -6453 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 11 | 11 | 6453 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251210 | December | 1630 |  | 9334 | 899 |  | 9334 | 888 | -6453 | -6453 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 11 | 11 | 6453 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251210 | December | 1730 |  | 9334 | 899 |  | 9334 | 888 | -6453 | -6453 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 11 | 11 | 6453 | 1 | AT: 142; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251210 | December | 1830 |  | 9975 | 772 |  | 9963 | 772 | -3824 | -3824 | 0 | Critical Branch | Critical Branch | 0 | NA | 12 | 0 | 12 | 3824 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 103; AT: Reduction because NTC over thermal limit on border
20251210 | December | 1930 |  | 9975 | 772 |  | 9963 | 772 | -3824 | -3824 | 0 | Critical Branch | Critical Branch | 0 | NA | 12 | 0 | 12 | 3824 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 103; AT: Reduction because NTC over thermal limit on border
20251210 | December | 2030 |  | 9975 | 772 |  | 9963 | 772 | -3824 | -3824 | 0 | Critical Branch | Critical Branch | 0 | NA | 12 | 0 | 12 | 3824 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 103; AT: Reduction because NTC over thermal limit on border
20251210 | December | 2130 | 10025 |  |  | 10025 |  |  | -5205 | -5205 | -5204 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 288; AT: 105
20251210 | December | 2230 | 10025 |  |  | 10025 |  |  | -5205 | -5205 | -5204 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 288; AT: 105
20251210 | December | 2330 | 9215 |  |  | 9214 |  |  | -4389 | -4389 | -4388 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 272; AT: 120
20251211 | December | 0030 | 10259 |  |  | 10238 |  |  | -3474 | -3474 | -3455 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0130 | 10259 |  |  | 10238 |  |  | -3474 | -3474 | -3455 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0230 | 10259 |  |  | 10238 |  |  | -3474 | -3474 | -3455 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0330 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0430 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0530 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0630 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251211 | December | 0730 | 9435 |  |  | 9434 |  |  | -5285 | -5285 | -5285 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 297; AT: 105
20251211 | December | 0830 | 9435 |  |  | 9434 |  |  | -5285 | -5285 | -5285 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 297; AT: 105
20251211 | December | 0930 | 8962 |  |  | 8961 |  |  | -4935 | -4935 | -4934 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 281; AT: 105
20251211 | December | 1030 | 8962 |  |  | 8961 |  |  | -4935 | -4935 | -4934 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 281; AT: 105
20251211 | December | 1130 | 8962 |  |  | 8961 |  |  | -4935 | -4935 | -4934 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 281; AT: 105
20251211 | December | 1230 | 9735 |  |  | 9728 |  |  | -5368 | -5368 | -5364 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251211 | December | 1330 | 9735 |  |  | 9728 |  |  | -5368 | -5368 | -5364 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251211 | December | 1430 | 9735 |  |  | 9728 |  |  | -5368 | -5368 | -5364 | Critical Branch | Critical Branch | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251211 | December | 1530 | 8836 |  |  | 8835 |  |  | -5298 | -5298 | -5298 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 277; AT: 105
20251211 | December | 1630 | 8836 |  |  | 8835 |  |  | -5298 | -5298 | -5298 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 277; AT: 105
20251211 | December | 1730 | 9736 |  |  | 9735 |  |  | -6137 | -6137 | -6137 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 279; AT: 105
20251211 | December | 1830 | 9510 |  |  | 9509 |  |  | -5258 | -5258 | -5258 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 272; AT: 105
20251211 | December | 1930 | 9510 |  |  | 9509 |  |  | -5258 | -5258 | -5258 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 272; AT: 105
20251211 | December | 2030 | 9510 |  |  | 9509 |  |  | -5258 | -5258 | -5258 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 272; AT: 105
20251211 | December | 2130 | 10245 |  |  | 10245 |  |  | -6618 | -6618 | -6618 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105
20251211 | December | 2230 | 10245 |  |  | 10245 |  |  | -6618 | -6618 | -6618 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 295; AT: 105
20251211 | December | 2330 | 9435 |  |  | 9434 |  |  | -5847 | -5847 | -5846 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 279; AT: 120
20251212 | December | 0030 | 9664 |  |  | 9612 |  |  | -5248 | -5248 | -5195 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9362; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251212 | December | 0130 | 9664 |  |  | 9612 |  |  | -5248 | -5248 | -5195 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9362; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251212 | December | 0230 | 9664 |  |  | 9612 |  |  | -5248 | -5248 | -5195 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9362; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251212 | December | 0330 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251212 | December | 0430 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251212 | December | 0530 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251212 | December | 0630 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251212 | December | 0730 |  | 9180 | 808 |  | 9180 | 807 | -6082 | -6082 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6082 | 1 | AT: 139; AT: 103
20251212 | December | 0830 |  | 9180 | 808 |  | 9180 | 807 | -6082 | -6082 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6082 | 1 | AT: 139; AT: 103
20251212 | December | 0930 |  | 10021 | 111 |  | 10021 | 110 | -6709 | -6709 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6709 | 1 | AT: 146; AT: 95
20251212 | December | 1030 |  | 10021 | 111 |  | 10021 | 110 | -6709 | -6709 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6709 | 1 | AT: 146; AT: 95
20251212 | December | 1130 |  | 10021 | 111 |  | 10021 | 110 | -6709 | -6709 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6709 | 1 | AT: 146; AT: 95
20251212 | December | 1230 |  | 9610 | 921 |  | 9610 | 907 | -6793 | -6793 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 6793 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251212 | December | 1330 |  | 9610 | 921 |  | 9610 | 907 | -6793 | -6793 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 14 | 14 | 6793 | 1 | AT: 146; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251212 | December | 1430 |  | 9610 | 921 |  | 9242 | 907 | -6793 | -6793 | 0 | Critical Branch | Critical Branch | 0 | NA | 368 | 14 | 382 | 6793 | 1 | AT: 141; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border
20251212 | December | 1530 |  | 7693 | 664 |  | 7650 | 663 | 726 | 86 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 640 | NA | 43 | 1 | 44 | -86 | 1 | AT: 165; AT: 83; FR: 3463; FR: Process fail during TSO validation phase
20251212 | December | 1630 |  | 7753 | 670 |  | 7681 | 669 | 726 | 146 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 580 | NA | 72 | 1 | 73 | -146 | 1 | AT: 165; AT: 84; FR: 3463; FR: Process fail during TSO validation phase
20251212 | December | 1730 |  | 7720 | 667 |  | 7664 | 667 | 726 | 113 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 613 | NA | 56 | 0 | 56 | -113 | 1 | AT: 165; AT: 84; FR: 3463; FR: Process fail during TSO validation phase
20251212 | December | 1830 |  | 9784 | 107 |  | 9643 | 106 | -4669 | -4669 | 0 | Critical Branch | Critical Branch | 0 | NA | 141 | 1 | 142 | 4669 | 1 | AT: 141; AT: 91
20251212 | December | 1930 |  | 9784 | 107 |  | 9784 | 106 | -4669 | -4669 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 4669 | 1 | AT: 142; AT: 91
20251212 | December | 2030 |  | 9784 | 107 |  | 9784 | 106 | -4669 | -4669 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 4669 | 1 | AT: 142; AT: 91
20251212 | December | 2130 | 9880 |  |  | 9879 |  |  | -5125 | -5125 | -5124 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 283; AT: 105
20251212 | December | 2230 | 9880 |  |  | 9879 |  |  | -5125 | -5125 | -5124 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 283; AT: 105
20251212 | December | 2330 | 9070 |  |  | 9070 |  |  | -4312 | -4312 | -4312 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 268; AT: 120
20251213 | December | 0030 | 10266 |  |  | 10245 |  |  | -5439 | -5439 | -5425 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0130 | 10266 |  |  | 10245 |  |  | -5439 | -5439 | -5425 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0230 | 10266 |  |  | 10245 |  |  | -5439 | -5439 | -5425 | Critical Branch | Critical Branch | 0 | 21 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0330 | 10323 |  |  | 10300 |  |  | -2796 | -2796 | -2775 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0430 | 10323 |  |  | 10300 |  |  | -2796 | -2796 | -2775 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0530 | 10323 |  |  | 10300 |  |  | -2796 | -2796 | -2775 | Critical Branch | Critical Branch | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0630 | 10323 |  |  | 9928 |  |  | -2796 | -2796 | -2402 | Critical Branch | Critical Branch | 0 | 395 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border
20251213 | December | 0730 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | AT: 300; AT: 85; CH: 8178; CH: D2CC failed. Correction of BackUp-values.
20251213 | December | 0830 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | AT: 300; AT: 85; CH: 8178; CH: D2CC failed. Correction of BackUp-values.
20251213 | December | 0930 | 10193 |  |  | 9401 |  |  | -5353 | -5353 | -4561 | Critical Branch | Validation phase | 0 | 792 | NA | NA | NA | 0 | 1 | AT: 293; AT: 85; CH: 9151; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1030 | 10193 |  |  | 9401 |  |  | -5353 | -5353 | -4561 | Critical Branch | Validation phase | 0 | 792 | NA | NA | NA | 0 | 1 | AT: 293; AT: 85; CH: 9151; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1130 | 10193 |  |  | 9401 |  |  | -5353 | -5353 | -4561 | Critical Branch | Validation phase | 0 | 792 | NA | NA | NA | 0 | 1 | AT: 293; AT: 85; CH: 9151; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1230 | 10072 |  |  | 9201 |  |  | -5380 | -5380 | -4509 | Critical Branch | Validation phase | 0 | 871 | NA | NA | NA | 0 | 1 | AT: 289; AT: 85; CH: 8951; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1330 | 10072 |  |  | 9201 |  |  | -5380 | -5380 | -4509 | Critical Branch | Validation phase | 0 | 871 | NA | NA | NA | 0 | 1 | AT: 289; AT: 85; CH: 8951; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1430 | 10072 |  |  | 9201 |  |  | -5380 | -5380 | -4509 | Critical Branch | Validation phase | 0 | 871 | NA | NA | NA | 0 | 1 | AT: 289; AT: 85; CH: 8951; CH: Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1530 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | AT: 300; AT: 85; CH: 8178; CH: D2CC failed. Correction of BackUp-values.
20251213 | December | 1630 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | AT: 300; AT: 85; CH: 8178; CH: D2CC failed. Correction of BackUp-values.
20251213 | December | 1730 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | AT: 300; AT: 85; CH: 8178; CH: D2CC failed. Correction of BackUp-values.
20251213 | December | 1830 | 10150 |  |  | 9928 |  |  | -5453 | -5453 | -5231 | Critical Branch | Critical Branch | 0 | 222 | NA | NA | NA | 0 | 1 | AT: 292; AT: 85
20251213 | December | 1930 | 10150 |  |  | 10150 |  |  | -5453 | -5453 | -5453 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 292; AT: 85
20251213 | December | 2030 | 10150 |  |  | 10150 |  |  | -5453 | -5453 | -5453 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 292; AT: 85
20251213 | December | 2130 | 10609 |  |  | 10551 |  |  | -3314 | -3314 | -3256 | Critical Branch | Validation phase | 0 | 58 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 85; AT: Reduction because NTC over thermal limit on border; CH: 10305; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251213 | December | 2230 | 10609 |  |  | 10551 |  |  | -3314 | -3314 | -3256 | Critical Branch | Validation phase | 0 | 58 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 85; AT: Reduction because NTC over thermal limit on border; CH: 10305; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251213 | December | 2330 | 9799 |  |  | 9740 |  |  | -2470 | -2470 | -2412 | Critical Branch | Validation phase | 0 | 59 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 100; AT: Reduction because NTC over thermal limit on border; CH: 9495; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251214 | December | 0030 | 10604 |  |  | 10573 |  |  | -3353 | -3353 | -3324 | Critical Branch | Critical Branch | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 0130 | 10604 |  |  | 10573 |  |  | -3353 | -3353 | -3324 | Critical Branch | Critical Branch | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 0230 | 10604 |  |  | 10573 |  |  | -3353 | -3353 | -3324 | Critical Branch | Critical Branch | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 0330 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 0 | 296 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9969; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0430 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 0 | 296 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9969; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0530 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 0 | 296 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9969; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0630 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 0 | 296 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9969; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0730 | 10176 |  |  | 10158 |  |  | -5288 | -5288 | -5276 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 0830 | 10176 |  |  | 10158 |  |  | -5288 | -5288 | -5276 | Critical Branch | Critical Branch | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 0930 | 9804 |  |  | 9798 |  |  | -5310 | -5310 | -5306 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 1030 | 9804 |  |  | 9798 |  |  | -5310 | -5310 | -5306 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 1130 | 9804 |  |  | 9798 |  |  | -5310 | -5310 | -5306 | Critical Branch | Critical Branch | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 1230 | 9896 |  |  | 9887 |  |  | -5180 | -5180 | -5174 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 1330 | 9896 |  |  | 9887 |  |  | -5180 | -5180 | -5174 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 1430 | 9896 |  |  | 9887 |  |  | -5180 | -5180 | -5174 | Critical Branch | Critical Branch | 0 | 9 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251214 | December | 1530 | 10072 |  |  | 10049 |  |  | -6097 | -6097 | -6080 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9814; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 1630 | 10072 |  |  | 10049 |  |  | -6097 | -6097 | -6080 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9814; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 1730 | 10072 |  |  | 10049 |  |  | -6097 | -6097 | -6080 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9814; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 1830 | 9040 |  |  | 9040 |  |  | -5438 | -5438 | -5438 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 267; AT: 120
20251214 | December | 1930 | 9040 |  |  | 9040 |  |  | -5438 | -5438 | -5438 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 267; AT: 120
20251214 | December | 2030 | 9040 |  |  | 9040 |  |  | -5438 | -5438 | -5438 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 267; AT: 120
20251214 | December | 2130 | 10332 |  |  | 10083 |  |  | -6272 | -6272 | -6029 | Critical Branch | Validation phase | 0 | 249 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9849; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 2230 | 10332 |  |  | 10083 |  |  | -6272 | -6272 | -6029 | Critical Branch | Validation phase | 0 | 249 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9849; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 2330 | 10332 |  |  | 10083 |  |  | -6272 | -6272 | -6029 | Critical Branch | Validation phase | 0 | 249 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9849; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251215 | December | 0030 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251215 | December | 0130 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251215 | December | 0230 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 285; AT: 120
20251215 | December | 0330 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 241; AT: 120
20251215 | December | 0430 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 241; AT: 120
20251215 | December | 0530 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 241; AT: 120
20251215 | December | 0630 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 241; AT: 120
20251215 | December | 0730 | 10499 |  |  | 9720 |  |  | -6657 | -6657 | -5886 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 779 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105; CH: 10150; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251215 | December | 0830 | 9746 |  |  | 9641 |  |  | -6024 | -6024 | -5922 | Critical Branch | Validation phase | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 300; AT: Reduction because NTC over thermal limit on border; AT: 105; AT: Reduction because NTC over thermal limit on border; CH: 9397; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251215 | December | 0930 | 8914 |  |  | 8913 |  |  | -4163 | -4163 | -4162 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 281; AT: 105
20251215 | December | 1030 | 8914 |  |  | 8913 |  |  | -4163 | -4163 | -4162 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 281; AT: 105
20251215 | December | 1130 | 8914 |  |  | 8913 |  |  | -4163 | -4163 | -4162 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 281; AT: 105
20251215 | December | 1230 | 8989 |  |  | 8989 |  |  | -4312 | -4312 | -4311 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105
20251215 | December | 1330 | 8989 |  |  | 8989 |  |  | -4312 | -4312 | -4311 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105
20251215 | December | 1430 | 8989 |  |  | 8989 |  |  | -4312 | -4312 | -4311 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105
20251215 | December | 1530 | 9366 |  |  | 9365 |  |  | -5087 | -5087 | -5086 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 296; AT: 105
20251215 | December | 1630 | 9366 |  |  | 9365 |  |  | -5087 | -5087 | -5086 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 296; AT: 105
20251215 | December | 1730 | 10119 |  |  | 10119 |  |  | -5765 | -5765 | -5765 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 297; AT: 105
20251215 | December | 1830 | 9900 |  |  | 9858 |  |  | -5968 | -5968 | -5926 | Critical Branch | Validation phase | 0 | 42 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105; CH: 9608; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251215 | December | 1930 | 9900 |  |  | 9858 |  |  | -5968 | -5968 | -5926 | Critical Branch | Validation phase | 0 | 42 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105; CH: 9608; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251215 | December | 2030 | 9900 |  |  | 9858 |  |  | -5968 | -5968 | -5926 | Critical Branch | Validation phase | 0 | 42 | NA | NA | NA | 0 | 1 | AT: 284; AT: 105; CH: 9608; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251215 | December | 2130 | 10003 |  |  | 10002 |  |  | -5130 | -5130 | -5130 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 287; AT: 105
20251215 | December | 2230 | 10003 |  |  | 10002 |  |  | -5130 | -5130 | -5130 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 287; AT: 105
20251215 | December | 2330 | 9193 |  |  | 9193 |  |  | -4316 | -4316 | -4316 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 272; AT: 120
20251216 | December | 0030 | 10074 |  |  | 10059 |  |  | -5560 | -5560 | -5550 | Critical Branch | Critical Branch | 0 | 15 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0130 | 10074 |  |  | 10059 |  |  | -5560 | -5560 | -5550 | Critical Branch | Critical Branch | 0 | 15 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0230 | 10074 |  |  | 10059 |  |  | -5560 | -5560 | -5550 | Critical Branch | Critical Branch | 0 | 15 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0330 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0430 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0530 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0630 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 285; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251216 | December | 0730 | 9452 |  |  | 9451 |  |  | -5583 | -5583 | -5583 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 276; AT: 105
20251216 | December | 0830 | 9212 |  |  | 9212 |  |  | -5374 | -5374 | -5374 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 55; AT: 20
20251216 | December | 0930 | 9871 |  |  | 9844 |  |  | -5425 | -5425 | -5398 | Critical Branch | Validation phase | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20; CH: 9594; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251216 | December | 1030 | 9871 |  |  | 9844 |  |  | -5425 | -5425 | -5398 | Critical Branch | Validation phase | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20; CH: 9594; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251216 | December | 1130 | 9871 |  |  | 9844 |  |  | -5425 | -5425 | -5398 | Critical Branch | Validation phase | 0 | 27 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20; CH: 9594; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251216 | December | 1230 | 9825 |  |  | 9825 |  |  | -3764 | -3764 | -3764 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251216 | December | 1330 | 9825 |  |  | 9825 |  |  | -3764 | -3764 | -3764 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251216 | December | 1430 | 9825 |  |  | 9825 |  |  | -3764 | -3764 | -3764 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251216 | December | 1530 | 9288 |  |  | 9287 |  |  | -6173 | -6173 | -6173 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 55; AT: 20
20251216 | December | 1630 | 9288 |  |  | 9287 |  |  | -6173 | -6173 | -6173 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 55; AT: 20
20251216 | December | 1730 | 9288 |  |  | 9287 |  |  | -6173 | -6173 | -6173 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 55; AT: 20
20251216 | December | 1830 | 9740 |  |  | 9740 |  |  | -6991 | -6991 | -6991 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 57; AT: 20
20251216 | December | 1930 | 9740 |  |  | 9740 |  |  | -6991 | -6991 | -6991 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 57; AT: 20
20251216 | December | 2030 | 9740 |  |  | 9740 |  |  | -6991 | -6991 | -6991 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 57; AT: 20
20251216 | December | 2130 | 10139 |  |  | 10138 |  |  | -5551 | -5551 | -5550 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251216 | December | 2230 | 10139 |  |  | 10138 |  |  | -5551 | -5551 | -5550 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251216 | December | 2330 | 9344 |  |  | 9343 |  |  | -4811 | -4811 | -4810 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0030 | 9317 |  |  | 9316 |  |  | -2687 | -2687 | -2686 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0130 | 9317 |  |  | 9316 |  |  | -2687 | -2687 | -2686 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0230 | 9317 |  |  | 9316 |  |  | -2687 | -2687 | -2686 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0330 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0430 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0530 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0630 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 0730 |  | 9545 | 792 |  | 9545 | 790 | -4567 | -4567 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 2 | 2 | 4567 | 1 | AT: 30; AT: Reduction because NTC over thermal limit on border; AT: 20; AT: Reduction because NTC over thermal limit on border
20251217 | December | 0830 |  | 9545 | 792 |  | 9545 | 790 | -4567 | -4567 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 2 | 2 | 4567 | 1 | AT: 30; AT: Reduction because NTC over thermal limit on border; AT: 20; AT: Reduction because NTC over thermal limit on border
20251217 | December | 0930 | 9859 |  |  | 9859 |  |  | -3214 | -3214 | -3214 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 1030 | 9859 |  |  | 9859 |  |  | -3214 | -3214 | -3214 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 1130 | 9859 |  |  | 9859 |  |  | -3214 | -3214 | -3214 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 59; AT: 20
20251217 | December | 1230 |  | 8785 | 18 |  | 8785 | 17 | -1997 | -1997 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 1997 | 1 | AT: 53; AT: 14
20251217 | December | 1330 |  | 8785 | 18 |  | 8785 | 17 | -1997 | -1997 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 1997 | 1 | AT: 53; AT: 14
20251217 | December | 1430 |  | 8785 | 18 |  | 8785 | 17 | -1997 | -1997 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 1997 | 1 | AT: 53; AT: 14
20251217 | December | 1530 |  | 9059 | 748 |  | 9059 | 747 | -5325 | -5325 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 5325 | 1 | AT: 28; AT: 20
20251217 | December | 1630 |  | 9059 | 748 |  | 9059 | 747 | -5325 | -5325 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 5325 | 1 | AT: 28; AT: 20
20251217 | December | 1730 |  | 9100 | 763 |  | 9100 | 762 | -5397 | -5397 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 5397 | 1 | AT: 68; AT: Reduction because NTC over thermal limit on border; AT: 35; AT: Reduction because NTC over thermal limit on border
20251217 | December | 1830 |  | 8814 | 646 |  | 8813 | 646 | -5011 | -5011 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5011 | 1 | AT: 134; AT: 35
20251217 | December | 1930 |  | 8814 | 646 |  | 8813 | 646 | -5011 | -5011 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5011 | 1 | AT: 134; AT: 35
20251217 | December | 2030 |  | 8814 | 646 |  | 8813 | 646 | -5011 | -5011 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 5011 | 1 | AT: 134; AT: 35
20251217 | December | 2130 | 10396 |  |  | 10291 |  |  | -5701 | -5701 | -5597 | Critical Branch | Validation phase | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 35; AT: Reduction because NTC over thermal limit on border; CH: 10042; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251217 | December | 2230 | 10396 |  |  | 10291 |  |  | -5701 | -5701 | -5597 | Critical Branch | Validation phase | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 35; AT: Reduction because NTC over thermal limit on border; CH: 10042; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251217 | December | 2330 | 9596 |  |  | 9491 |  |  | -4899 | -4899 | -4794 | Critical Branch | Validation phase | 0 | 105 | NA | NA | NA | 0 | 1 | AT: 140; AT: Reduction because NTC over thermal limit on border; AT: 65; AT: Reduction because NTC over thermal limit on border; CH: 9242; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251218 | December | 0030 | 8904 |  |  | 8904 |  |  | -4655 | -4655 | -4654 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 131; AT: 65
20251218 | December | 0130 | 8904 |  |  | 8904 |  |  | -4655 | -4655 | -4654 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 131; AT: 65
20251218 | December | 0230 | 8904 |  |  | 8904 |  |  | -4655 | -4655 | -4654 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 131; AT: 65
20251218 | December | 0330 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 140; AT: 65
20251218 | December | 0430 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 140; AT: 65
20251218 | December | 0530 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 140; AT: 65
20251218 | December | 0630 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 140; AT: 65
20251218 | December | 0730 | 10169 |  |  | 10167 |  |  | -5959 | -5959 | -5958 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 35; AT: Reduction because NTC over thermal limit on border
20251218 | December | 0830 | 10169 |  |  | 10167 |  |  | -5959 | -5959 | -5958 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 145; AT: Reduction because NTC over thermal limit on border; AT: 35; AT: Reduction because NTC over thermal limit on border
20251218 | December | 0930 | 9783 |  |  | 9782 |  |  | -5086 | -5086 | -5085 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 140; AT: 35
20251218 | December | 1030 | 9783 |  |  | 9782 |  |  | -5086 | -5086 | -5085 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 140; AT: 35
20251218 | December | 1130 | 9783 |  |  | 9782 |  |  | -5086 | -5086 | -5085 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 140; AT: 35
20251218 | December | 1230 | 8540 |  |  | 8540 |  |  | -5928 | -5928 | -5928 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 122; AT: 35
20251218 | December | 1330 | 8540 |  |  | 8540 |  |  | -5928 | -5928 | -5928 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 122; AT: 35
20251218 | December | 1430 | 8540 |  |  | 8540 |  |  | -5928 | -5928 | -5928 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 122; AT: 35
20251218 | December | 1530 | 8633 |  |  | 8633 |  |  | -4721 | -4721 | -4721 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 123; AT: 35
20251218 | December | 1630 | 8633 |  |  | 8633 |  |  | -4721 | -4721 | -4721 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 123; AT: 35
20251218 | December | 1730 | 8873 |  |  | 8873 |  |  | -4926 | -4926 | -4926 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 329; AT: 120
20251218 | December | 1830 | 10495 |  |  | 10373 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 122 | NA | NA | NA | 0 | 1 | AT: 380; AT: 120
20251218 | December | 1930 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251218 | December | 2030 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251218 | December | 2130 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251218 | December | 2230 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251218 | December | 2330 | 9680 |  |  | 9680 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 365; AT: 165
20251219 | December | 0030 | 9506 |  |  | 9506 |  |  | -3440 | -3440 | -3440 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 358; AT: 165
20251219 | December | 0130 | 9506 |  |  | 9506 |  |  | -3440 | -3440 | -3440 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 358; AT: 165
20251219 | December | 0230 | 9506 |  |  | 9506 |  |  | -3440 | -3440 | -3440 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 358; AT: 165
20251219 | December | 0330 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 355; AT: 165
20251219 | December | 0430 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 355; AT: 165
20251219 | December | 0530 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 355; AT: 165
20251219 | December | 0630 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 355; AT: 165
20251219 | December | 0730 |  | 9822 | 805 |  | 9808 | 805 | -4172 | -4172 | 0 | Critical Branch | Critical Branch | 0 | NA | 14 | 0 | 14 | 4172 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 116; AT: Reduction because NTC over thermal limit on border
20251219 | December | 0830 |  | 9822 | 805 |  | 9808 | 805 | -4172 | -4172 | 0 | Critical Branch | Critical Branch | 0 | NA | 14 | 0 | 14 | 4172 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 116; AT: Reduction because NTC over thermal limit on border
20251219 | December | 0930 | 9522 |  |  | 9521 |  |  | -3295 | -3295 | -3295 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 354; AT: 120
20251219 | December | 1030 | 9522 |  |  | 9521 |  |  | -3295 | -3295 | -3295 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 354; AT: 120
20251219 | December | 1130 | 9522 |  |  | 9521 |  |  | -3295 | -3295 | -3295 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 354; AT: 120
20251219 | December | 1230 |  | 9284 | 121 |  | 9284 | 121 | -3311 | -3311 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3311 | 1 | AT: 176; AT: 101
20251219 | December | 1330 |  | 9284 | 121 |  | 9284 | 121 | -3311 | -3311 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3311 | 1 | AT: 176; AT: 101
20251219 | December | 1430 |  | 9284 | 121 |  | 9284 | 121 | -3311 | -3311 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3311 | 1 | AT: 176; AT: 101
20251219 | December | 1530 |  | 8447 | 808 |  | 8447 | 808 | -3720 | -3720 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3720 | 1 | AT: 167; AT: 115
20251219 | December | 1630 |  | 8447 | 808 |  | 8447 | 808 | -3720 | -3720 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3720 | 1 | AT: 167; AT: 115
20251219 | December | 1730 |  | 8447 | 808 |  | 8447 | 808 | -3720 | -3720 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3720 | 1 | AT: 167; AT: 115
20251219 | December | 1830 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251219 | December | 1930 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251219 | December | 2030 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251219 | December | 2130 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251219 | December | 2230 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251219 | December | 2330 | 9680 |  |  | 9680 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 365; AT: 165
20251220 | December | 0030 | 9875 |  |  | 9795 |  |  | -5615 | -5615 | -5536 | Critical Branch | Validation phase | 0 | 80 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9550; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0130 | 9875 |  |  | 9795 |  |  | -5615 | -5615 | -5536 | Critical Branch | Validation phase | 0 | 80 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9550; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0230 | 9875 |  |  | 9795 |  |  | -5615 | -5615 | -5536 | Critical Branch | Validation phase | 0 | 80 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9550; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0330 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 337; AT: 165
20251220 | December | 0430 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 337; AT: 165
20251220 | December | 0530 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 337; AT: 165
20251220 | December | 0630 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 337; AT: 165
20251220 | December | 0730 | 9641 |  |  | 9463 |  |  | -2342 | -2342 | -2164 | Critical Branch | Validation phase | 0 | 178 | NA | NA | NA | 0 | 1 | AT: 352; AT: 120; CH: 9213; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0830 | 9641 |  |  | 9463 |  |  | -2342 | -2342 | -2164 | Critical Branch | Validation phase | 0 | 178 | NA | NA | NA | 0 | 1 | AT: 352; AT: 120; CH: 9213; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0930 | 8364 |  |  | 8363 |  |  | -2906 | -2906 | -2905 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 302; AT: 120
20251220 | December | 1030 | 8364 |  |  | 8363 |  |  | -2906 | -2906 | -2905 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 302; AT: 120
20251220 | December | 1130 | 8364 |  |  | 8363 |  |  | -2906 | -2906 | -2905 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 302; AT: 120
20251220 | December | 1230 | 10495 |  |  | 9863 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 632 | NA | NA | NA | 0 | 1 | AT: 360; AT: 120
20251220 | December | 1330 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251220 | December | 1430 | 10495 |  |  | 10316 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 179 | NA | NA | NA | 0 | 1 | AT: 378; AT: 120
20251220 | December | 1530 | 8816 |  |  | 8816 |  |  | -4261 | -4261 | -4260 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 320; AT: 120
20251220 | December | 1630 | 8816 |  |  | 8816 |  |  | -4261 | -4261 | -4260 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 320; AT: 120
20251220 | December | 1730 | 8816 |  |  | 8816 |  |  | -4261 | -4261 | -4260 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 320; AT: 120
20251220 | December | 1830 | 10495 |  |  | 10316 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 179 | NA | NA | NA | 0 | 1 | AT: 378; AT: 120
20251220 | December | 1930 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251220 | December | 2030 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251220 | December | 2130 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251220 | December | 2230 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120
20251220 | December | 2330 | 9680 |  |  | 9680 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 365; AT: 165
20251221 | December | 0030 | 10659 |  |  | 9547 |  |  | -3654 | -3654 | -2542 | Critical Branch | Validation phase | 0 | 1112 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9217; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0130 | 10659 |  |  | 9547 |  |  | -3654 | -3654 | -2542 | Critical Branch | Validation phase | 0 | 1112 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9217; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0230 | 10659 |  |  | 9547 |  |  | -3654 | -3654 | -2542 | Critical Branch | Validation phase | 0 | 1112 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9217; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0330 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9077; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0430 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9077; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0530 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9077; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0630 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9077; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0730 | 10649 |  |  | 9258 |  |  | -6815 | -6815 | -5424 | Critical Branch | Validation phase | 0 | 1391 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8928; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0830 | 10649 |  |  | 9258 |  |  | -6815 | -6815 | -5424 | Critical Branch | Validation phase | 0 | 1391 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8928; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0930 |  | 10297 | 830 |  | 9743 | 788 | -7696 | -7696 | 0 | Critical Branch | Validation phase | 0 | NA | 554 | 42 | 596 | 7696 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 161; AT: Reduction because NTC over thermal limit on border; CH: 10106; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251221 | December | 1030 |  | 10297 | 830 |  | 9743 | 788 | -7696 | -7696 | 0 | Critical Branch | Validation phase | 0 | NA | 554 | 42 | 596 | 7696 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 161; AT: Reduction because NTC over thermal limit on border; CH: 10106; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251221 | December | 1130 |  | 10297 | 830 |  | 9743 | 788 | -7696 | -7696 | 0 | Critical Branch | Validation phase | 0 | NA | 554 | 42 | 596 | 7696 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 161; AT: Reduction because NTC over thermal limit on border; CH: 10106; CH: Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251221 | December | 1230 | 10570 |  |  | 9072 |  |  | -3182 | -3182 | -1684 | Critical Branch | Validation phase | 0 | 1498 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8742; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251221 | December | 1330 | 10570 |  |  | 9072 |  |  | -3182 | -3182 | -1684 | Critical Branch | Validation phase | 0 | 1498 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8742; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251221 | December | 1430 | 10570 |  |  | 9072 |  |  | -3182 | -3182 | -1684 | Critical Branch | Validation phase | 0 | 1498 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8742; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251221 | December | 1530 |  | 10232 | 870 |  | 10183 | 870 | -6091 | -6091 | 0 | Critical Branch | Critical Branch | 0 | NA | 49 | 0 | 49 | 6091 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20251221 | December | 1630 |  | 10232 | 870 |  | 10191 | 870 | -6091 | -6091 | 0 | Critical Branch | Critical Branch | 0 | NA | 41 | 0 | 41 | 6091 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20251221 | December | 1730 |  | 10232 | 870 |  | 10191 | 870 | -6091 | -6091 | 0 | Critical Branch | Critical Branch | 0 | NA | 41 | 0 | 41 | 6091 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20251221 | December | 1830 |  | 10394 | 885 |  | 10347 | 885 | -6063 | -6063 | 0 | Critical Branch | Critical Branch | 0 | NA | 47 | 0 | 47 | 6063 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20251221 | December | 1930 |  | 10394 | 885 |  | 10347 | 885 | -6063 | -6063 | 0 | Critical Branch | Critical Branch | 0 | NA | 47 | 0 | 47 | 6063 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20251221 | December | 2030 |  | 10394 | 885 |  | 10347 | 885 | -6063 | -6063 | 0 | Critical Branch | Critical Branch | 0 | NA | 47 | 0 | 47 | 6063 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20251221 | December | 2130 | 10721 |  |  | 9276 |  |  | -5604 | -5604 | -4159 | Critical Branch | Validation phase | 0 | 1445 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8946; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 2230 | 10721 |  |  | 9276 |  |  | -5604 | -5604 | -4159 | Critical Branch | Validation phase | 0 | 1445 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8946; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 2330 | 10721 |  |  | 9276 |  |  | -5604 | -5604 | -4159 | Critical Branch | Validation phase | 0 | 1445 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 8946; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 0030 | 10033 |  |  | 7700 |  |  | -5314 | -5314 | -2981 | Critical Branch | Validation phase | 0 | 2333 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 7370; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0130 | 10033 |  |  | 7700 |  |  | -5314 | -5314 | -2981 | Critical Branch | Validation phase | 0 | 2333 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 7370; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0230 | 10033 |  |  | 7700 |  |  | -5314 | -5314 | -2981 | Critical Branch | Validation phase | 0 | 2333 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 7370; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0330 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 361; AT: 165; CH: 7725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0430 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 361; AT: 165; CH: 7725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0530 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 361; AT: 165; CH: 7725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0630 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 0 | 1526 | NA | NA | NA | 0 | 1 | AT: 361; AT: 165; CH: 7725; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0730 | 10495 |  |  | 8130 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2365 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120; CH: 7795; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0830 | 9095 |  |  | 8130 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 965 | NA | NA | NA | 0 | 1 | AT: 385; AT: 120; CH: 7795; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0930 |  | 8213 | 814 |  | 8086 | 803 | -2822 | -2822 | 0 | Critical Branch | Validation phase | 0 | NA | 127 | 11 | 138 | 2822 | 1 | AT: 381; AT: 117; CH: 8277; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251222 | December | 1030 |  | 8213 | 814 |  | 8086 | 803 | -2822 | -2822 | 0 | Critical Branch | Validation phase | 0 | NA | 127 | 11 | 138 | 2822 | 1 | AT: 381; AT: 117; CH: 8277; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251222 | December | 1130 |  | 8213 | 814 |  | 8086 | 803 | -2822 | -2822 | 0 | Critical Branch | Validation phase | 0 | NA | 127 | 11 | 138 | 2822 | 1 | AT: 381; AT: 117; CH: 8277; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251222 | December | 1230 |  | 7960 | 782 |  | 7959 | 782 | -2468 | -2468 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2468 | 1 | AT: 371; AT: 117
20251222 | December | 1330 |  | 7960 | 782 |  | 7959 | 782 | -2468 | -2468 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2468 | 1 | AT: 371; AT: 117
20251222 | December | 1430 |  | 7960 | 782 |  | 7959 | 782 | -2468 | -2468 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2468 | 1 | AT: 371; AT: 117
20251222 | December | 1530 |  | 8559 | 804 |  | 8283 | 784 | -1139 | -1139 | 0 | Critical Branch | Validation phase | 0 | NA | 276 | 20 | 296 | 1139 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border; CH: 8639; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 1630 |  | 9964 | 804 |  | 9689 | 784 | -2852 | -2852 | 0 | Critical Branch | Validation phase | 0 | NA | 275 | 20 | 295 | 2852 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border; CH: 10039; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 1730 |  | 9964 | 804 |  | 9689 | 784 | -2852 | -2852 | 0 | Critical Branch | Validation phase | 0 | NA | 275 | 20 | 295 | 2852 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border; CH: 10039; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 1830 |  | 10020 | 799 |  | 10010 | 799 | -5933 | -5933 | 0 | Critical Branch | Critical Branch | 0 | NA | 10 | 0 | 10 | 5933 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border
20251222 | December | 1930 |  | 10020 | 799 |  | 8857 | 799 | -5933 | -5933 | 0 | Critical Branch | Critical Branch | 0 | NA | 1163 | 0 | 1163 | 5933 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border
20251222 | December | 2030 |  | 10020 | 799 |  | 7414 | 799 | -5933 | -5933 | 0 | Critical Branch | Critical Branch | 0 | NA | 2606 | 0 | 2606 | 5933 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 117; AT: Reduction because NTC over thermal limit on border
20251222 | December | 2130 | 10577 |  |  | 6224 |  |  | -3078 | -3078 | 1275 | Critical Branch | Validation phase | 0 | 4353 | NA | NA | NA | 5628 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 5889; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 2230 | 10577 |  |  | 6224 |  |  | -3078 | -3078 | 1275 | Critical Branch | Validation phase | 0 | 4353 | NA | NA | NA | 5628 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 5889; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 2330 | 9762 |  |  | 5409 |  |  | -2221 | -2221 | 2132 | Critical Branch | Validation phase | 0 | 4353 | NA | NA | NA | 6485 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 5079; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 0030 | 9995 |  |  | 8000 |  |  | -5307 | -5307 | -3312 | Critical Branch | Validation phase | 0 | 1995 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 7670; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0130 | 9995 |  |  | 8000 |  |  | -5307 | -5307 | -3312 | Critical Branch | Validation phase | 0 | 1995 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 7670; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0230 | 9995 |  |  | 8000 |  |  | -5307 | -5307 | -3312 | Critical Branch | Validation phase | 0 | 1995 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 7670; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0330 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 0 | 1661 | NA | NA | NA | 0 | 1 | AT: 363; AT: 165; CH: 7646; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0430 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 0 | 1661 | NA | NA | NA | 0 | 1 | AT: 363; AT: 165; CH: 7646; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0530 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 0 | 1661 | NA | NA | NA | 0 | 1 | AT: 363; AT: 165; CH: 7646; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0630 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 0 | 1661 | NA | NA | NA | 0 | 1 | AT: 363; AT: 165; CH: 7646; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0730 | 10015 |  |  | 7727 |  |  | -3329 | -3329 | -1041 | Critical Branch | Validation phase | 0 | 2288 | NA | NA | NA | 0 | 1 | AT: 370; AT: 120; CH: 7392; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0830 | 10015 |  |  | 7727 |  |  | -3329 | -3329 | -1041 | Critical Branch | Validation phase | 0 | 2288 | NA | NA | NA | 0 | 1 | AT: 370; AT: 120; CH: 7392; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0930 | 9580 |  |  | 7153 |  |  | -3010 | -3010 | -583 | Critical Branch | Validation phase | 0 | 2427 | NA | NA | NA | 0 | 1 | AT: 357; AT: 120; CH: 6818; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1030 | 9580 |  |  | 7153 |  |  | -3010 | -3010 | -583 | Critical Branch | Validation phase | 0 | 2427 | NA | NA | NA | 0 | 1 | AT: 357; AT: 120; CH: 6818; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1130 | 9580 |  |  | 7153 |  |  | -3010 | -3010 | -583 | Critical Branch | Validation phase | 0 | 2427 | NA | NA | NA | 0 | 1 | AT: 357; AT: 120; CH: 6818; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1230 |  | 9097 | 650 |  | 8296 | 625 | -2487 | -2487 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 801 | 25 | 826 | 2487 | 1 | AT: 365; AT: 120; CH: 9046; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1330 |  | 9097 | 650 |  | 8752 | 625 | -2487 | -2487 | 0 | Critical Branch | Validation phase | 0 | NA | 345 | 25 | 370 | 2487 | 1 | AT: 365; AT: 120; CH: 9046; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1430 |  | 9097 | 650 |  | 8752 | 625 | -2487 | -2487 | 0 | Critical Branch | Validation phase | 0 | NA | 345 | 25 | 370 | 2487 | 1 | AT: 365; AT: 120; CH: 9046; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1530 | 9923 |  |  | 9163 |  |  | -33 | -33 | 727 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 1487 | 1 | AT: 367; AT: 120; CH: 8828; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 1630 | 9923 |  |  | 9163 |  |  | -33 | -33 | 727 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 1487 | 1 | AT: 367; AT: 120; CH: 8828; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 1730 | 9923 |  |  | 9163 |  |  | -33 | -33 | 727 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 1487 | 1 | AT: 367; AT: 120; CH: 8828; CH: Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 1830 |  | 9186 | 777 |  | 9186 | 777 | -539 | -539 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 539 | 1 | AT: 368; AT: 117
20251223 | December | 1930 |  | 9186 | 777 |  | 9186 | 777 | -539 | -539 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 539 | 1 | AT: 368; AT: 117
20251223 | December | 2030 |  | 9186 | 777 |  | 9166 | 777 | -539 | -539 | 0 | Critical Branch | Critical Branch | 0 | NA | 20 | 0 | 20 | 539 | 1 | AT: 368; AT: 117
20251223 | December | 2130 | 10260 |  |  | 8044 |  |  | -3850 | -3850 | -1634 | Critical Branch | Validation phase | 0 | 2216 | NA | NA | NA | 0 | 1 | AT: 377; AT: 120; CH: 7709; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251223 | December | 2230 | 10260 |  |  | 8044 |  |  | -3850 | -3850 | -1634 | Critical Branch | Validation phase | 0 | 2216 | NA | NA | NA | 0 | 1 | AT: 377; AT: 120; CH: 7709; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251223 | December | 2330 | 9445 |  |  | 7229 |  |  | -3025 | -3025 | -809 | Critical Branch | Validation phase | 0 | 2216 | NA | NA | NA | 0 | 1 | AT: 357; AT: 165; CH: 6899; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251224 | December | 0030 |  | 9917 | 187 |  | 9917 | 181 | -3735 | -3735 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 6 | 6 | 3735 | 1 | AT: 189; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0130 |  | 9917 | 187 |  | 9917 | 181 | -3735 | -3735 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 6 | 6 | 3735 | 1 | AT: 189; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0230 |  | 9917 | 187 |  | 9917 | 181 | -3735 | -3735 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 6 | 6 | 3735 | 1 | AT: 189; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0330 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0430 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0530 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0630 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 0 | 25 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0730 |  | 9275 | 947 |  | 9275 | 931 | -2955 | -2955 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 2955 | 1 | AT: 182; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0830 |  | 9275 | 947 |  | 9275 | 931 | -2955 | -2955 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 2955 | 1 | AT: 182; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 0930 |  | 9497 | 763 |  | 9496 | 763 | -2332 | -2332 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2332 | 1 | AT: 378; AT: 118
20251224 | December | 1030 |  | 9497 | 763 |  | 9496 | 763 | -2332 | -2332 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2332 | 1 | AT: 378; AT: 118
20251224 | December | 1130 |  | 9497 | 763 |  | 9496 | 763 | -2332 | -2332 | 0 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 2332 | 1 | AT: 378; AT: 118
20251224 | December | 1230 |  | 9558 | 920 |  | 9558 | 908 | -3143 | -3143 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 12 | 12 | 3143 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1330 |  | 9558 | 920 |  | 9558 | 908 | -3143 | -3143 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 12 | 12 | 3143 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1430 |  | 9558 | 920 |  | 9558 | 908 | -3143 | -3143 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 12 | 12 | 3143 | 1 | AT: 217; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1530 |  | 9384 | 952 |  | 9384 | 936 | -1827 | -1827 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 1827 | 1 | AT: 215; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1630 |  | 9384 | 952 |  | 9384 | 936 | -1827 | -1827 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 1827 | 1 | AT: 215; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1730 |  | 9384 | 952 |  | 9384 | 936 | -1827 | -1827 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 1827 | 1 | AT: 215; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1830 |  | 9856 | 990 |  | 9856 | 968 | -3626 | -3626 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 22 | 22 | 3626 | 1 | AT: 222; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 1930 |  | 9856 | 990 |  | 9856 | 968 | -3626 | -3626 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 22 | 22 | 3626 | 1 | AT: 222; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 2030 |  | 9856 | 990 |  | 9856 | 968 | -3626 | -3626 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 22 | 22 | 3626 | 1 | AT: 222; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251224 | December | 2130 |  | 10556 | 131 |  | 10556 | 130 | -5421 | -5421 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 5421 | 1 | AT: 196; AT: 115
20251224 | December | 2230 |  | 10556 | 131 |  | 10556 | 130 | -5421 | -5421 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 5421 | 1 | AT: 196; AT: 115
20251224 | December | 2330 |  | 9751 | 206 |  | 9751 | 181 | -4602 | -4602 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 25 | 25 | 4602 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0030 |  | 9357 | 1138 |  | 9357 | 1102 | -5031 | -5031 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 36 | 36 | 5031 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0130 |  | 9357 | 1138 |  | 9357 | 1102 | -5031 | -5031 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 36 | 36 | 5031 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0230 |  | 9357 | 1138 |  | 9357 | 1102 | -5031 | -5031 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 36 | 36 | 5031 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0330 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0430 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0530 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0630 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 0 | 2 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0730 |  | 9341 | 1108 |  | 9341 | 1076 | -4909 | -4909 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 32 | 32 | 4909 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0830 |  | 9341 | 1108 |  | 9341 | 1076 | -4909 | -4909 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 32 | 32 | 4909 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 0930 |  | 9783 | 1071 |  | 9783 | 1045 | -5334 | -5334 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 26 | 26 | 5334 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1030 |  | 9783 | 1071 |  | 9783 | 1045 | -5334 | -5334 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 26 | 26 | 5334 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1130 |  | 9783 | 1071 |  | 9783 | 1045 | -5334 | -5334 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 26 | 26 | 5334 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1230 |  | 9782 | 1046 |  | 9782 | 1023 | -5511 | -5511 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 23 | 23 | 5511 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1330 |  | 9782 | 1046 |  | 9782 | 1023 | -5511 | -5511 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 23 | 23 | 5511 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1430 |  | 9782 | 1046 |  | 9782 | 1023 | -5511 | -5511 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 23 | 23 | 5511 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1530 |  | 9383 | 1120 |  | 9383 | 1086 | -4937 | -4937 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 34 | 34 | 4937 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1630 |  | 9383 | 1120 |  | 9383 | 1086 | -4937 | -4937 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 34 | 34 | 4937 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1730 |  | 9383 | 1120 |  | 9383 | 1086 | -4937 | -4937 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 34 | 34 | 4937 | 1 | AT: 186; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1830 |  | 9511 | 1169 |  | 9511 | 1128 | -5209 | -5209 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 41 | 41 | 5209 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 1930 |  | 9511 | 1169 |  | 9511 | 1128 | -5209 | -5209 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 41 | 41 | 5209 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 2030 |  | 9511 | 1169 |  | 9511 | 1128 | -5209 | -5209 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 41 | 41 | 5209 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 2130 |  | 9288 | 1132 |  | 9288 | 1097 | -3098 | -3098 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 3098 | 1 | AT: 185; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 2230 |  | 9288 | 1132 |  | 9288 | 1097 | -3098 | -3098 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 3098 | 1 | AT: 185; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251225 | December | 2330 |  | 9288 | 1132 |  | 9288 | 1097 | -3098 | -3098 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 3098 | 1 | AT: 185; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0030 |  | 10145 | 1126 |  | 10145 | 1091 | -5841 | -5841 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 5841 | 1 | AT: 199; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0130 |  | 10145 | 1126 |  | 10145 | 1091 | -5841 | -5841 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 5841 | 1 | AT: 199; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0230 |  | 10145 | 1126 |  | 10145 | 1091 | -5841 | -5841 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 35 | 35 | 5841 | 1 | AT: 199; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0330 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 20 | 20 | 5205 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0430 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 20 | 20 | 5205 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0530 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 20 | 20 | 5205 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0630 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 20 | 20 | 5205 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0730 |  | 9924 | 1016 |  | 9924 | 998 | -5833 | -5833 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 18 | 18 | 5833 | 1 | AT: 264; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0830 |  | 9924 | 1016 |  | 9924 | 998 | -5833 | -5833 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 18 | 18 | 5833 | 1 | AT: 264; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 0930 |  | 10060 | 1156 |  | 10060 | 1117 | -4726 | -4726 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 39 | 39 | 4726 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1030 |  | 10060 | 1156 |  | 10060 | 1117 | -4726 | -4726 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 39 | 39 | 4726 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1130 |  | 10060 | 1156 |  | 10060 | 1117 | -4726 | -4726 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 39 | 39 | 4726 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1230 |  | 8758 | 918 |  | 8758 | 915 | -4149 | -4149 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 3 | 3 | 4149 | 1 | AT: 176; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1330 |  | 8758 | 918 |  | 8758 | 915 | -4149 | -4149 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 3 | 3 | 4149 | 1 | AT: 176; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1430 |  | 8758 | 918 |  | 8758 | 915 | -4149 | -4149 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 3 | 3 | 4149 | 1 | AT: 176; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1530 |  | 10103 | 1040 |  | 10103 | 1018 | -7022 | -7022 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 22 | 22 | 7022 | 1 | AT: 198; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1630 |  | 10103 | 1040 |  | 10103 | 1018 | -7022 | -7022 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 22 | 22 | 7022 | 1 | AT: 198; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1730 |  | 10103 | 1040 |  | 10103 | 1018 | -7022 | -7022 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 22 | 22 | 7022 | 1 | AT: 198; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 1830 | 10459 |  |  | 10271 |  |  | -3287 | -3287 | -3099 | Critical Branch | Validation phase | 0 | 188 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9960; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251226 | December | 1930 | 10459 |  |  | 10271 |  |  | -3287 | -3287 | -3099 | Critical Branch | Validation phase | 0 | 188 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9960; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251226 | December | 2030 | 10459 |  |  | 10271 |  |  | -3287 | -3287 | -3099 | Critical Branch | Validation phase | 0 | 188 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9960; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251226 | December | 2130 |  | 10263 | 1101 |  | 10263 | 1070 | -6256 | -6256 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 31 | 31 | 6256 | 1 | AT: 201; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 2230 |  | 10263 | 1101 |  | 10263 | 1070 | -6256 | -6256 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 31 | 31 | 6256 | 1 | AT: 201; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251226 | December | 2330 |  | 10263 | 1101 |  | 10263 | 1070 | -6256 | -6256 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 31 | 31 | 6256 | 1 | AT: 201; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0030 |  | 10318 | 1346 |  | 10318 | 1278 | -6595 | -6595 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 68 | 68 | 6595 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0130 |  | 10318 | 1346 |  | 10318 | 1278 | -6595 | -6595 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 68 | 68 | 6595 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0230 |  | 10318 | 1346 |  | 10318 | 1278 | -6595 | -6595 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 68 | 68 | 6595 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0330 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 80 | 80 | 6255 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0430 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 80 | 80 | 6255 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0530 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 80 | 80 | 6255 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0630 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 80 | 80 | 6255 | 1 | AT: 202; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0730 |  | 10223 | 1228 |  | 10223 | 1174 | -6330 | -6330 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 54 | 54 | 6330 | 1 | AT: 198; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0830 |  | 10223 | 1228 |  | 10223 | 1174 | -6330 | -6330 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 54 | 54 | 6330 | 1 | AT: 198; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 0930 |  | 10130 | 1071 |  | 10130 | 1038 | -7719 | -7719 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 33 | 33 | 7719 | 1 | AT: 196; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1030 |  | 10130 | 1071 |  | 10130 | 1038 | -7719 | -7719 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 33 | 33 | 7719 | 1 | AT: 196; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1130 |  | 10130 | 1071 |  | 9866 | 1038 | -7719 | -7719 | 0 | Critical Branch | Critical Branch | 0 | NA | 264 | 33 | 297 | 7719 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1230 |  | 8411 | 904 |  | 8411 | 894 | -7093 | -7093 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 7093 | 1 | AT: 169; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1330 |  | 8411 | 904 |  | 8411 | 894 | -7093 | -7093 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 7093 | 1 | AT: 169; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1430 |  | 8411 | 904 |  | 8411 | 894 | -7093 | -7093 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 7093 | 1 | AT: 169; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1530 |  | 10334 | 1028 |  | 9843 | 1001 | -6928 | -6928 | 0 | Critical Branch | Critical Branch | 0 | NA | 491 | 27 | 518 | 6928 | 1 | AT: 189; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1630 |  | 10334 | 1028 |  | 10334 | 1001 | -6928 | -6928 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 27 | 27 | 6928 | 1 | AT: 199; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1730 |  | 10334 | 1028 |  | 10334 | 1001 | -6928 | -6928 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 27 | 27 | 6928 | 1 | AT: 199; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1830 |  | 10098 | 1071 |  | 10098 | 1038 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 33 | 33 | 7001 | 1 | AT: 196; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 1930 |  | 10098 | 1071 |  | 10098 | 1038 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 33 | 33 | 7001 | 1 | AT: 196; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 2030 |  | 10098 | 1071 |  | 10098 | 1038 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 33 | 33 | 7001 | 1 | AT: 196; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251227 | December | 2130 |  | 10516 | 975 |  | 10489 | 975 | -7941 | -7941 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 7941 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 112; AT: Reduction because NTC over thermal limit on border
20251227 | December | 2230 |  | 10516 | 975 |  | 10489 | 975 | -7941 | -7941 | 0 | Critical Branch | Critical Branch | 0 | NA | 27 | 0 | 27 | 7941 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 112; AT: Reduction because NTC over thermal limit on border
20251227 | December | 2330 |  | 9761 | 995 |  | 9735 | 995 | -7240 | -7240 | 0 | Critical Branch | Critical Branch | 0 | NA | 26 | 0 | 26 | 7240 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 156; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0030 |  | 9037 | 1193 |  | 9037 | 1148 | -5191 | -5191 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 45 | 45 | 5191 | 1 | AT: 181; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0130 |  | 9037 | 1193 |  | 9037 | 1148 | -5191 | -5191 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 45 | 45 | 5191 | 1 | AT: 181; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0230 |  | 9037 | 1193 |  | 9037 | 1148 | -5191 | -5191 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 45 | 45 | 5191 | 1 | AT: 181; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0330 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 49 | 49 | 5805 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0430 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 49 | 49 | 5805 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0530 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 49 | 49 | 5805 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0630 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 49 | 49 | 5805 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0730 |  | 10098 | 1224 |  | 10087 | 1175 | -5719 | -5719 | 0 | Critical Branch | Critical Branch | 0 | NA | 11 | 49 | 60 | 5719 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0830 |  | 10098 | 1224 |  | 8688 | 1175 | -5719 | -5719 | 0 | Critical Branch | Critical Branch | 0 | NA | 1410 | 49 | 1459 | 5719 | 1 | AT: 168; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 0930 |  | 7213 | 1352 |  | 7213 | 1284 | -3577 | -3577 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 68 | 68 | 3577 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1030 |  | 7213 | 1352 |  | 7213 | 1284 | -3577 | -3577 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 68 | 68 | 3577 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1130 |  | 7213 | 1352 |  | 7213 | 1284 | -3577 | -3577 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 68 | 68 | 3577 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1230 |  | 7067 | 948 |  | 7067 | 940 | -3831 | -3831 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 8 | 8 | 3831 | 1 | AT: 148; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1330 |  | 7067 | 948 |  | 7067 | 940 | -3831 | -3831 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 8 | 8 | 3831 | 1 | AT: 148; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1430 |  | 7067 | 948 |  | 7067 | 940 | -3831 | -3831 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 8 | 8 | 3831 | 1 | AT: 148; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1530 |  | 9190 | 1181 |  | 8506 | 1138 | -6334 | -6334 | 0 | Critical Branch | Critical Branch | 0 | NA | 684 | 43 | 727 | 6334 | 1 | AT: 168; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1630 |  | 9190 | 1181 |  | 9190 | 1138 | -6334 | -6334 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 43 | 43 | 6334 | 1 | AT: 183; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1730 |  | 9190 | 1181 |  | 9190 | 1138 | -6334 | -6334 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 43 | 43 | 6334 | 1 | AT: 183; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 1830 | 10508 |  |  | 9961 |  |  | -3451 | -3451 | -2903 | Critical Branch | Validation phase | 0 | 547 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9640; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251228 | December | 1930 | 10508 |  |  | 9961 |  |  | -3451 | -3451 | -2903 | Critical Branch | Validation phase | 0 | 547 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9640; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251228 | December | 2030 | 10508 |  |  | 9961 |  |  | -3451 | -3451 | -2903 | Critical Branch | Validation phase | 0 | 547 | NA | NA | NA | 0 | 1 | AT: 365; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border; CH: 9640; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251228 | December | 2130 |  | 9901 | 1334 |  | 9901 | 1268 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 66 | 66 | 7001 | 1 | AT: 195; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 2230 |  | 9901 | 1334 |  | 9901 | 1268 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 66 | 66 | 7001 | 1 | AT: 195; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251228 | December | 2330 |  | 9901 | 1334 |  | 9901 | 1268 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 66 | 66 | 7001 | 1 | AT: 195; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0030 |  | 7234 | 1052 |  | 7234 | 1029 | -274 | -274 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 23 | 23 | 274 | 1 | AT: 151; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0130 |  | 7234 | 1052 |  | 7234 | 1029 | -274 | -274 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 23 | 23 | 274 | 1 | AT: 151; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0230 |  | 7234 | 1052 |  | 7234 | 1029 | -274 | -274 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 23 | 23 | 274 | 1 | AT: 151; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0330 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 38 | 38 | 14 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0430 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 38 | 38 | 14 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0530 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 38 | 38 | 14 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0630 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 38 | 38 | 14 | 1 | AT: 150; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0730 |  | 9145 | 925 |  | 8538 | 912 | -6532 | -6532 | 0 | Critical Branch | Critical Branch | 0 | NA | 607 | 13 | 620 | 6532 | 1 | AT: 197; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0830 |  | 9145 | 925 |  | 9145 | 912 | -6532 | -6532 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 13 | 13 | 6532 | 1 | AT: 211; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 0930 |  | 7818 | 941 |  | 7818 | 926 | -49 | -49 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 15 | 15 | 49 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 1030 |  | 7818 | 941 |  | 7818 | 926 | -49 | -49 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 15 | 15 | 49 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 1130 |  | 7818 | 941 |  | 7818 | 926 | -49 | -49 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 15 | 15 | 49 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 1230 |  | 7818 | 736 |  | 7818 | 735 | -6861 | -6861 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6861 | 1 | AT: 190; AT: 106
20251229 | December | 1330 |  | 7818 | 736 |  | 7818 | 735 | -6861 | -6861 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6861 | 1 | AT: 190; AT: 106
20251229 | December | 1430 |  | 7818 | 736 |  | 7818 | 735 | -6861 | -6861 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 1 | 1 | 6861 | 1 | AT: 190; AT: 106
20251229 | December | 1530 |  | 9588 | 860 |  | 9230 | 833 | -2222 | -2222 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 358 | 27 | 385 | 2222 | 1 | AT: 180; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9859; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1630 |  | 9588 | 860 |  | 9276 | 833 | -2222 | -2222 | 0 | Critical Branch | Validation phase | 0 | NA | 312 | 27 | 339 | 2222 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9859; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1730 |  | 9588 | 860 |  | 9276 | 833 | -2222 | -2222 | 0 | Critical Branch | Validation phase | 0 | NA | 312 | 27 | 339 | 2222 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border; CH: 9859; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1830 |  | 9482 | 833 |  | 8985 | 790 | -2833 | -2833 | 0 | Critical Branch | Validation phase | 0 | NA | 497 | 43 | 540 | 2833 | 1 | AT: 219; AT: 119; CH: 9756; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1930 |  | 9482 | 833 |  | 8985 | 790 | -2833 | -2833 | 0 | Critical Branch | Validation phase | 0 | NA | 497 | 43 | 540 | 2833 | 1 | AT: 219; AT: 119; CH: 9756; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251229 | December | 2030 |  | 9482 | 833 |  | 8985 | 790 | -2833 | -2833 | 0 | Critical Branch | Validation phase | 0 | NA | 497 | 43 | 540 | 2833 | 1 | AT: 219; AT: 119; CH: 9756; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251229 | December | 2130 |  | 9324 | 909 |  | 9324 | 899 | -2466 | -2466 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 2466 | 1 | AT: 183; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 2230 |  | 9324 | 909 |  | 9324 | 899 | -2466 | -2466 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 10 | 10 | 2466 | 1 | AT: 183; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251229 | December | 2330 |  | 8576 | 1004 |  | 8576 | 988 | -1566 | -1566 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 16 | 16 | 1566 | 1 | AT: 173; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251230 | December | 0030 |  | 8950 | 1059 |  | 8950 | 1035 | -2643 | -2643 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 2643 | 1 | AT: 179; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251230 | December | 0130 |  | 8950 | 1059 |  | 8950 | 1035 | -2643 | -2643 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 2643 | 1 | AT: 179; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251230 | December | 0230 |  | 8950 | 1059 |  | 8950 | 1035 | -2643 | -2643 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 2643 | 1 | AT: 179; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251230 | December | 0330 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 0 | 433 | NA | NA | NA | 0 | 1 | AT: 356; AT: 165; CH: 8642; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0430 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 0 | 433 | NA | NA | NA | 0 | 1 | AT: 356; AT: 165; CH: 8642; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0530 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 0 | 433 | NA | NA | NA | 0 | 1 | AT: 356; AT: 165; CH: 8642; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0630 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 0 | 433 | NA | NA | NA | 0 | 1 | AT: 356; AT: 165; CH: 8642; CH: Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0730 |  | 9719 | 1044 |  | 9719 | 1015 | -6101 | -6101 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 29 | 29 | 6101 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 0830 |  | 9719 | 1044 |  | 9719 | 1015 | -6101 | -6101 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 29 | 29 | 6101 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 0930 |  | 9605 | 963 |  | 9605 | 945 | -2627 | -2627 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 18 | 18 | 2627 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1030 |  | 9605 | 963 |  | 9605 | 945 | -2627 | -2627 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 18 | 18 | 2627 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1130 |  | 9605 | 963 |  | 9605 | 945 | -2627 | -2627 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 18 | 18 | 2627 | 1 | AT: 188; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1230 |  | 9440 | 968 |  | 9440 | 949 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 19 | 19 | 3208 | 1 | AT: 185; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1330 |  | 9440 | 968 |  | 9440 | 949 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 19 | 19 | 3208 | 1 | AT: 185; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1430 |  | 9440 | 968 |  | 9440 | 949 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 19 | 19 | 3208 | 1 | AT: 185; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1530 |  | 9585 | 1028 |  | 9585 | 1001 | -2965 | -2965 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 27 | 27 | 2965 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1630 |  | 9585 | 1028 |  | 9585 | 1001 | -2965 | -2965 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 27 | 27 | 2965 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1730 |  | 9585 | 1028 |  | 9585 | 1001 | -2965 | -2965 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 27 | 27 | 2965 | 1 | AT: 187; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1830 |  | 9311 | 1006 |  | 9311 | 982 | -3132 | -3132 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 3132 | 1 | AT: 213; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 1930 |  | 9311 | 1006 |  | 9311 | 982 | -3132 | -3132 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 3132 | 1 | AT: 213; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 2030 |  | 9311 | 1006 |  | 9311 | 982 | -3132 | -3132 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 3132 | 1 | AT: 213; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 2130 |  | 8801 | 1006 |  | 8801 | 982 | -2427 | -2427 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 2427 | 1 | AT: 175; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 2230 |  | 8801 | 1006 |  | 8801 | 982 | -2427 | -2427 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 24 | 24 | 2427 | 1 | AT: 175; AT: Reduction because NTC over thermal limit on border; AT: 120; AT: Reduction because NTC over thermal limit on border
20251230 | December | 2330 |  | 8052 | 1101 |  | 8052 | 1070 | -1518 | -1518 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 31 | 31 | 1518 | 1 | AT: 164; AT: Reduction because NTC over thermal limit on border; AT: 165; AT: Reduction because NTC over thermal limit on border
20251231 | December | 0030 |  | 8116 | 1144 |  | 8116 | 1144 | -1770 | -1770 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1770 | 0
20251231 | December | 0130 |  | 8116 | 1144 |  | 8116 | 1144 | -1770 | -1770 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1770 | 0
20251231 | December | 0230 |  | 8116 | 1144 |  | 8116 | 1144 | -1770 | -1770 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1770 | 0
20251231 | December | 0330 |  | 9025 | 1187 |  | 9025 | 1187 | -2694 | -2694 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2694 | 0
20251231 | December | 0430 |  | 9025 | 1187 |  | 9025 | 1187 | -2694 | -2694 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2694 | 0
20251231 | December | 0530 |  | 9025 | 1187 |  | 9025 | 1187 | -2694 | -2694 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2694 | 0
20251231 | December | 0630 |  | 9025 | 1187 |  | 9025 | 1187 | -2694 | -2694 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2694 | 0
20251231 | December | 0730 |  | 9804 | 1039 |  | 9804 | 1039 | -6946 | -6946 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 6946 | 0
20251231 | December | 0830 |  | 9804 | 1039 |  | 9804 | 1039 | -6946 | -6946 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 6946 | 0
20251231 | December | 0930 |  | 9603 | 979 |  | 9603 | 979 | -4021 | -4021 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4021 | 0
20251231 | December | 1030 |  | 9603 | 979 |  | 9603 | 979 | -4021 | -4021 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4021 | 0
20251231 | December | 1130 |  | 9603 | 979 |  | 9603 | 979 | -4021 | -4021 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4021 | 0
20251231 | December | 1230 |  | 9732 | 958 |  | 9732 | 958 | -4378 | -4378 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 4378 | 0
20251231 | December | 1330 |  | 9732 | 958 |  | 9732 | 958 | -4378 | -4378 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 4378 | 0
20251231 | December | 1430 |  | 9732 | 958 |  | 9732 | 958 | -4378 | -4378 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 4378 | 0
20251231 | December | 1530 |  | 9626 | 1060 |  | 9626 | 1060 | -5135 | -5135 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 5135 | 0
20251231 | December | 1630 |  | 9626 | 1060 |  | 9626 | 1060 | -5135 | -5135 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 5135 | 0
20251231 | December | 1730 |  | 9626 | 1060 |  | 9626 | 1060 | -5135 | -5135 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 5135 | 0
20251231 | December | 1830 |  | 9655 | 1012 |  | 9655 | 1012 | -7515 | -7515 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 7515 | 0
20251231 | December | 1930 |  | 9655 | 1012 |  | 9655 | 1012 | -7515 | -7515 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 7515 | 0
20251231 | December | 2030 |  | 9655 | 1012 |  | 9655 | 1012 | -7515 | -7515 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 7515 | 0
20251231 | December | 2130 |  | 9457 | 974 |  | 9457 | 974 | -4768 | -4768 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4768 | 0
20251231 | December | 2230 |  | 9457 | 974 |  | 9457 | 974 | -4768 | -4768 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4768 | 0
20251231 | December | 2330 |  | 8709 | 1069 |  | 8709 | 1069 | -3914 | -3914 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3914 | 0

## DA 70% Reduction
DA 70% reduction results
|  |  | TTC Adjustment |  |  | ANTC |  | LimitedBy
BD | Month | TS | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | Adjustment | 70% reduction | % reduction | Category
20251001 | October | 1230 |  | 8645 | 779 | 550 | 450 | Minimum Margin | 100 | 18.18% | [500-1000] MW
20251001 | October | 1330 |  | 8645 | 779 | 550 | 450 | Minimum Margin | 100 | 18.18% | [500-1000] MW
20251001 | October | 1430 |  | 8645 | 779 | 550 | 450 | Minimum Margin | 100 | 18.18% | [500-1000] MW
20251002 | October | 1830 | 8016 |  |  | 735 | 0 | Critical Branch | 735 | 100% | [500-1000] MW
20251002 | October | 1930 | 8016 |  |  | 735 | 0 | Critical Branch | 735 | 100% | [500-1000] MW
20251002 | October | 2030 | 8016 |  |  | 735 | 0 | Critical Branch | 735 | 100% | [500-1000] MW
20251003 | October | 1830 |  | 7244 | 574 | 2826 | 0 | Critical Branch | 2826 | 100% | above 1000 MW
20251003 | October | 1930 |  | 7244 | 574 | 2826 | 0 | Critical Branch | 2826 | 100% | above 1000 MW
20251003 | October | 2030 |  | 7244 | 574 | 2826 | 0 | Critical Branch | 2826 | 100% | above 1000 MW
20251003 | October | 2130 | 9726 |  |  | 4926 | 208 | Minimum Margin | 4718 | 95.78% | above 1000 MW
20251003 | October | 2230 | 9708 |  |  | 4926 | 190 | Minimum Margin | 4736 | 96.14% | above 1000 MW
20251003 | October | 2330 | 9064 |  |  | 5068 | 156 | Minimum Margin | 4912 | 96.92% | above 1000 MW
20251006 | October | 0930 | 6250 |  |  | 3946 | 0 | TTC Selection - LTTC | 3946 | 100% | above 1000 MW
20251006 | October | 1030 | 6472 |  |  | 3946 | 222 | Minimum Margin | 3724 | 94.37% | above 1000 MW
20251006 | October | 1130 | 6461 |  |  | 3946 | 211 | Minimum Margin | 3735 | 94.65% | above 1000 MW
20251006 | October | 1230 | 6439 |  |  | 4444 | 189 | Minimum Margin | 4255 | 95.75% | above 1000 MW
20251006 | October | 1330 | 6439 |  |  | 4444 | 189 | Minimum Margin | 4255 | 95.75% | above 1000 MW
20251006 | October | 1430 | 6439 |  |  | 4444 | 189 | Minimum Margin | 4255 | 95.75% | above 1000 MW
20251006 | October | 1530 | 7389 |  |  | 2679 | 211 | Minimum Margin | 2468 | 92.12% | above 1000 MW
20251006 | October | 1630 | 7178 |  |  | 2679 | 0 | Critical Branch | 2679 | 100% | above 1000 MW
20251006 | October | 1730 | 7178 |  |  | 2679 | 0 | Critical Branch | 2679 | 100% | above 1000 MW
20251007 | October | 0730 | 7790 |  |  | 6687 | 0 | Critical Branch | 6687 | 100% | above 1000 MW
20251007 | October | 0830 | 7790 |  |  | 6687 | 0 | Critical Branch | 6687 | 100% | above 1000 MW
20251007 | October | 0930 | 7664 |  |  | 3667 | 0 | Critical Branch | 3667 | 100% | above 1000 MW
20251007 | October | 1030 | 7664 |  |  | 3667 | 0 | Critical Branch | 3667 | 100% | above 1000 MW
20251007 | October | 1130 | 7790 |  |  | 3667 | 126 | Minimum Margin | 3541 | 96.56% | above 1000 MW
20251008 | October | 0030 | 8488 |  |  | 2581 | 196 | Minimum Margin | 2385 | 92.41% | above 1000 MW
20251008 | October | 0130 | 8488 |  |  | 2581 | 196 | Minimum Margin | 2385 | 92.41% | above 1000 MW
20251008 | October | 0230 | 8488 |  |  | 2581 | 196 | Minimum Margin | 2385 | 92.41% | above 1000 MW
20251008 | October | 0330 | 8570 |  |  | 3101 | 200 | Minimum Margin | 2901 | 93.55% | above 1000 MW
20251008 | October | 0430 | 8570 |  |  | 3101 | 200 | Minimum Margin | 2901 | 93.55% | above 1000 MW
20251008 | October | 0530 | 8570 |  |  | 3101 | 200 | Minimum Margin | 2901 | 93.55% | above 1000 MW
20251008 | October | 0630 | 8570 |  |  | 3101 | 200 | Minimum Margin | 2901 | 93.55% | above 1000 MW
20251008 | October | 0930 |  | 5071 | 377 | 5465 | 2 | Minimum Margin | 5463 | 99.96% | above 1000 MW
20251008 | October | 1030 |  | 5142 | 384 | 5465 | 73 | Minimum Margin | 5392 | 98.66% | above 1000 MW
20251008 | October | 1130 |  | 5301 | 400 | 5465 | 233 | Minimum Margin | 5232 | 95.74% | above 1000 MW
20251008 | October | 1230 |  | 5265 | 529 | 5185 | 196 | Minimum Margin | 4989 | 96.22% | above 1000 MW
20251008 | October | 1330 |  | 5265 | 529 | 5185 | 196 | Minimum Margin | 4989 | 96.22% | above 1000 MW
20251008 | October | 1430 |  | 5265 | 529 | 5185 | 196 | Minimum Margin | 4989 | 96.22% | above 1000 MW
20251008 | October | 1530 |  | 7231 | 830 | 2750 | 187 | Minimum Margin | 2563 | 93.2% | above 1000 MW
20251008 | October | 1630 |  | 7141 | 819 | 2750 | 97 | Minimum Margin | 2653 | 96.47% | above 1000 MW
20251008 | October | 1730 |  | 7244 | 831 | 2750 | 200 | Minimum Margin | 2550 | 92.73% | above 1000 MW
20251009 | October | 0030 | 8374 |  |  | 1927 | 220 | Minimum Margin | 1707 | 88.58% | above 1000 MW
20251009 | October | 0130 | 8374 |  |  | 1927 | 220 | Minimum Margin | 1707 | 88.58% | above 1000 MW
20251009 | October | 0230 | 8374 |  |  | 1927 | 220 | Minimum Margin | 1707 | 88.58% | above 1000 MW
20251009 | October | 0330 | 6505 |  |  | 3305 | 236 | Minimum Margin | 3069 | 92.86% | above 1000 MW
20251009 | October | 0430 | 6505 |  |  | 3305 | 236 | Minimum Margin | 3069 | 92.86% | above 1000 MW
20251009 | October | 0530 | 6505 |  |  | 3305 | 236 | Minimum Margin | 3069 | 92.86% | above 1000 MW
20251009 | October | 0630 | 6505 |  |  | 3305 | 236 | Minimum Margin | 3069 | 92.86% | above 1000 MW
20251009 | October | 0930 | 5766 |  |  | 5231 | 116 | Minimum Margin | 5115 | 97.78% | above 1000 MW
20251009 | October | 1030 | 5887 |  |  | 5231 | 237 | Minimum Margin | 4994 | 95.47% | above 1000 MW
20251009 | October | 1130 | 5883 |  |  | 5231 | 233 | Minimum Margin | 4998 | 95.55% | above 1000 MW
20251009 | October | 1230 | 5890 |  |  | 2935 | 240 | Minimum Margin | 2695 | 91.82% | above 1000 MW
20251009 | October | 1330 | 5322 |  |  | 4623 | 272 | Minimum Margin | 4351 | 94.12% | above 1000 MW
20251009 | October | 1430 | 5322 |  |  | 4623 | 272 | Minimum Margin | 4351 | 94.12% | above 1000 MW
20251009 | October | 1530 |  | 6408 | 710 | 3713 | 254 | Minimum Margin | 3459 | 93.16% | above 1000 MW
20251009 | October | 1630 |  | 6408 | 710 | 3713 | 254 | Minimum Margin | 3459 | 93.16% | above 1000 MW
20251009 | October | 1730 |  | 6648 | 710 | 3613 | 254 | Minimum Margin | 3359 | 92.97% | above 1000 MW
20251011 | October | 0330 | 6973 |  |  | 4022 | 215 | Minimum Margin | 3807 | 94.65% | above 1000 MW
20251011 | October | 0430 | 6973 |  |  | 4022 | 215 | Minimum Margin | 3807 | 94.65% | above 1000 MW
20251011 | October | 0530 | 6973 |  |  | 4022 | 215 | Minimum Margin | 3807 | 94.65% | above 1000 MW
20251011 | October | 0630 | 6979 |  |  | 4022 | 221 | Minimum Margin | 3801 | 94.51% | above 1000 MW
20251011 | October | 0930 | 6950 |  |  | 1879 | 447 | Minimum Margin | 1432 | 76.21% | above 1000 MW
20251011 | October | 1030 | 6778 |  |  | 1879 | 275 | Minimum Margin | 1604 | 85.36% | above 1000 MW
20251011 | October | 1130 | 6950 |  |  | 1879 | 447 | Minimum Margin | 1432 | 76.21% | above 1000 MW
20251011 | October | 2330 | 6419 |  |  | 591 | 539 | Minimum Margin | 52 | 8.799% | [500-1000] MW
20251012 | October | 0930 | 7690 |  |  | 1235 | 218 | Minimum Margin | 1017 | 82.35% | above 1000 MW
20251012 | October | 1030 | 7688 |  |  | 1235 | 216 | Minimum Margin | 1019 | 82.51% | above 1000 MW
20251012 | October | 1130 | 7689 |  |  | 1235 | 217 | Minimum Margin | 1018 | 82.43% | above 1000 MW
20251012 | October | 1230 | 8075 |  |  | 1461 | 202 | Minimum Margin | 1259 | 86.17% | above 1000 MW
20251012 | October | 1330 | 8079 |  |  | 1461 | 206 | Minimum Margin | 1255 | 85.9% | above 1000 MW
20251012 | October | 1430 | 8075 |  |  | 1461 | 202 | Minimum Margin | 1259 | 86.17% | above 1000 MW
20251012 | October | 1530 | 6859 |  |  | 2236 | 218 | Minimum Margin | 2018 | 90.25% | above 1000 MW
20251012 | October | 1630 | 6859 |  |  | 2236 | 218 | Minimum Margin | 2018 | 90.25% | above 1000 MW
20251012 | October | 1730 | 6859 |  |  | 2236 | 218 | Minimum Margin | 2018 | 90.25% | above 1000 MW
20251013 | October | 1230 |  | 6077 | 519 | 3218 | 184 | Minimum Margin | 3034 | 94.28% | above 1000 MW
20251013 | October | 1330 |  | 6077 | 519 | 3218 | 184 | Minimum Margin | 3034 | 94.28% | above 1000 MW
20251013 | October | 1430 |  | 6077 | 519 | 3218 | 184 | Minimum Margin | 3034 | 94.28% | above 1000 MW
20251013 | October | 1530 |  | 6400 | 568 | 3150 | 181 | Minimum Margin | 2969 | 94.25% | above 1000 MW
20251013 | October | 1630 |  | 6400 | 568 | 3150 | 181 | Minimum Margin | 2969 | 94.25% | above 1000 MW
20251013 | October | 1730 |  | 6400 | 568 | 3150 | 181 | Minimum Margin | 2969 | 94.25% | above 1000 MW
20251014 | October | 1230 | 7575 |  |  | 4695 | 216 | Minimum Margin | 4479 | 95.4% | above 1000 MW
20251014 | October | 1330 | 7575 |  |  | 4695 | 216 | Minimum Margin | 4479 | 95.4% | above 1000 MW
20251014 | October | 1430 | 7575 |  |  | 4695 | 216 | Minimum Margin | 4479 | 95.4% | above 1000 MW
20251015 | October | 1230 |  | 5937 | 411 | 2566 | 191 | Minimum Margin | 2375 | 92.56% | above 1000 MW
20251015 | October | 1330 |  | 5937 | 411 | 2566 | 191 | Minimum Margin | 2375 | 92.56% | above 1000 MW
20251015 | October | 1430 |  | 5943 | 411 | 2566 | 197 | Minimum Margin | 2369 | 92.32% | above 1000 MW
20251015 | October | 1530 |  | 7205 | 654 | 3389 | 198 | Minimum Margin | 3191 | 94.16% | above 1000 MW
20251015 | October | 1630 |  | 7200 | 654 | 3389 | 193 | Minimum Margin | 3196 | 94.31% | above 1000 MW
20251015 | October | 1730 |  | 7209 | 655 | 3389 | 202 | Minimum Margin | 3187 | 94.04% | above 1000 MW
20251015 | October | 1830 |  | 7460 | 675 | 258 | 236 | Minimum Margin | 22 | 8.527% | below 500 MW
20251015 | October | 1930 |  | 7328 | 663 | 258 | 103 | Minimum Margin | 155 | 60.08% | below 500 MW
20251015 | October | 2030 |  | 7453 | 675 | 258 | 229 | Minimum Margin | 29 | 11.24% | below 500 MW
20251017 | October | 1230 | 6720 |  |  | 5289 | 230 | Minimum Margin | 5059 | 95.65% | above 1000 MW
20251017 | October | 1330 | 6720 |  |  | 5289 | 230 | Minimum Margin | 5059 | 95.65% | above 1000 MW
20251017 | October | 1430 | 6720 |  |  | 5289 | 230 | Minimum Margin | 5059 | 95.65% | above 1000 MW
20251017 | October | 1530 | 7108 |  |  | 4673 | 204 | Minimum Margin | 4469 | 95.63% | above 1000 MW
20251017 | October | 1630 | 7110 |  |  | 4673 | 206 | Minimum Margin | 4467 | 95.59% | above 1000 MW
20251017 | October | 1730 | 8006 |  |  | 3085 | 202 | Minimum Margin | 2883 | 93.45% | above 1000 MW
20251018 | October | 1230 | 8577 |  |  | 3055 | 153 | Minimum Margin | 2902 | 94.99% | above 1000 MW
20251018 | October | 1330 | 8577 |  |  | 3055 | 153 | Minimum Margin | 2902 | 94.99% | above 1000 MW
20251018 | October | 1430 | 8577 |  |  | 3055 | 153 | Minimum Margin | 2902 | 94.99% | above 1000 MW
20251024 | October | 1530 |  | 8384 | 740 | 2598 | 129 | Minimum Margin | 2469 | 95.03% | above 1000 MW
20251024 | October | 1630 |  | 8384 | 740 | 2598 | 129 | Minimum Margin | 2469 | 95.03% | above 1000 MW
20251024 | October | 1730 |  | 8384 | 740 | 2598 | 129 | Minimum Margin | 2469 | 95.03% | above 1000 MW
20251029 | October | 1530 |  | 7847 | 690 | 1258 | 235 | Minimum Margin | 1023 | 81.32% | above 1000 MW
20251029 | October | 1630 |  | 8706 | 680 | 181 | 96 | Minimum Margin | 85 | 46.96% | below 500 MW
20251030 | October | 1230 | 7108 |  |  | 4033 | 118 | Minimum Margin | 3915 | 97.07% | above 1000 MW
20251030 | October | 1330 | 7108 |  |  | 4033 | 118 | Minimum Margin | 3915 | 97.07% | above 1000 MW
20251030 | October | 1430 | 7108 |  |  | 4033 | 118 | Minimum Margin | 3915 | 97.07% | above 1000 MW
20251109 | November | 1230 |  | 7080 | 489 | 4168 | 25 | Minimum Margin | 4143 | 99.4% | above 1000 MW
20251109 | November | 1330 |  | 7204 | 499 | 4168 | 149 | Minimum Margin | 4019 | 96.43% | above 1000 MW
20251109 | November | 1430 |  | 7264 | 504 | 4168 | 210 | Minimum Margin | 3958 | 94.96% | above 1000 MW
20251120 | November | 0930 |  | 8054 | 143 | 5318 | 79 | Minimum Margin | 5239 | 98.51% | above 1000 MW
20251120 | November | 1030 |  | 8173 | 146 | 5318 | 198 | Minimum Margin | 5120 | 96.28% | above 1000 MW
20251120 | November | 1130 |  | 8108 | 145 | 5318 | 133 | Minimum Margin | 5185 | 97.5% | above 1000 MW
20251120 | November | 1230 |  | 7437 | 488 | 3523 | 86 | Minimum Margin | 3437 | 97.56% | above 1000 MW
20251120 | November | 1330 |  | 7433 | 488 | 3523 | 82 | Minimum Margin | 3441 | 97.67% | above 1000 MW
20251120 | November | 1430 |  | 7515 | 495 | 3523 | 165 | Minimum Margin | 3358 | 95.32% | above 1000 MW
20251121 | November | 0930 | 8334 |  |  | 5927 | 184 | Minimum Margin | 5743 | 96.9% | above 1000 MW
20251121 | November | 1030 | 8375 |  |  | 5927 | 225 | Minimum Margin | 5702 | 96.2% | above 1000 MW
20251121 | November | 1130 | 8356 |  |  | 5927 | 206 | Minimum Margin | 5721 | 96.52% | above 1000 MW
20251121 | November | 1230 |  | 7724 | 397 | 4570 | 199 | Minimum Margin | 4371 | 95.65% | above 1000 MW
20251121 | November | 1330 |  | 7534 | 383 | 4570 | 8 | Minimum Margin | 4562 | 99.82% | above 1000 MW
20251121 | November | 1430 |  | 7620 | 389 | 4570 | 95 | Minimum Margin | 4475 | 97.92% | above 1000 MW
20251121 | November | 1530 |  | 7426 | 478 | 6324 | 75 | Minimum Margin | 6249 | 98.81% | above 1000 MW
20251121 | November | 1630 |  | 7430 | 479 | 6324 | 79 | Minimum Margin | 6245 | 98.75% | above 1000 MW
20251121 | November | 1730 |  | 7426 | 478 | 6324 | 75 | Minimum Margin | 6249 | 98.81% | above 1000 MW
20251122 | November | 0030 | 7875 |  |  | 2761 | 195 | Minimum Margin | 2566 | 92.94% | above 1000 MW
20251122 | November | 0130 | 7818 |  |  | 2761 | 138 | Minimum Margin | 2623 | 95% | above 1000 MW
20251122 | November | 0230 | 7818 |  |  | 2761 | 138 | Minimum Margin | 2623 | 95% | above 1000 MW
20251122 | November | 0330 | 7852 |  |  | 2947 | 172 | Minimum Margin | 2775 | 94.16% | above 1000 MW
20251122 | November | 0430 | 7852 |  |  | 2947 | 172 | Minimum Margin | 2775 | 94.16% | above 1000 MW
20251122 | November | 0530 | 7852 |  |  | 2947 | 172 | Minimum Margin | 2775 | 94.16% | above 1000 MW
20251122 | November | 0630 | 7905 |  |  | 2947 | 225 | Minimum Margin | 2722 | 92.37% | above 1000 MW
20251122 | November | 1530 | 8627 |  |  | 3874 | 237 | Minimum Margin | 3637 | 93.88% | above 1000 MW
20251122 | November | 1630 | 8413 |  |  | 3874 | 23 | Minimum Margin | 3851 | 99.41% | above 1000 MW
20251122 | November | 1730 | 8390 |  |  | 3874 | 0 | TTC Selection - LTTC | 3874 | 100% | above 1000 MW
20251126 | November | 0930 | 8307 |  |  | 6778 | 177 | Minimum Margin | 6601 | 97.39% | above 1000 MW
20251126 | November | 1030 | 8327 |  |  | 6778 | 197 | Minimum Margin | 6581 | 97.09% | above 1000 MW
20251126 | November | 1130 | 8327 |  |  | 6778 | 197 | Minimum Margin | 6581 | 97.09% | above 1000 MW
20251126 | November | 1230 | 8325 |  |  | 5301 | 195 | Minimum Margin | 5106 | 96.32% | above 1000 MW
20251126 | November | 1330 | 8325 |  |  | 5301 | 195 | Minimum Margin | 5106 | 96.32% | above 1000 MW
20251126 | November | 1430 | 8361 |  |  | 5301 | 231 | Minimum Margin | 5070 | 95.64% | above 1000 MW
20251127 | November | 1230 | 8386 |  |  | 2693 | 196 | Minimum Margin | 2497 | 92.72% | above 1000 MW
20251127 | November | 1330 | 8386 |  |  | 2693 | 196 | Minimum Margin | 2497 | 92.72% | above 1000 MW
20251127 | November | 1430 | 8414 |  |  | 2693 | 224 | Minimum Margin | 2469 | 91.68% | above 1000 MW
20251202 | December | 1830 |  | 9669 | 902 | 3734 | 34 | Minimum Margin | 3700 | 99.09% | above 1000 MW
20251202 | December | 1930 |  | 9669 | 902 | 3734 | 34 | Minimum Margin | 3700 | 99.09% | above 1000 MW
20251202 | December | 2030 |  | 9669 | 902 | 3734 | 34 | Minimum Margin | 3700 | 99.09% | above 1000 MW
20251203 | December | 1530 |  | 9683 | 864 | 4105 | 150 | Minimum Margin | 3955 | 96.35% | above 1000 MW
20251203 | December | 1630 |  | 9683 | 864 | 4105 | 151 | Minimum Margin | 3954 | 96.32% | above 1000 MW
20251203 | December | 1730 |  | 9567 | 854 | 4105 | 35 | Minimum Margin | 4070 | 99.15% | above 1000 MW
20251203 | December | 1830 |  | 9090 | 794 | 4757 | 35 | Minimum Margin | 4722 | 99.26% | above 1000 MW
20251203 | December | 1930 |  | 9090 | 794 | 4757 | 35 | Minimum Margin | 4722 | 99.26% | above 1000 MW
20251203 | December | 2030 |  | 9090 | 794 | 4757 | 35 | Minimum Margin | 4722 | 99.26% | above 1000 MW
20251212 | December | 1530 |  | 7693 | 664 | 726 | 86 | Minimum Margin | 640 | 88.15% | [500-1000] MW
20251212 | December | 1630 |  | 7753 | 670 | 726 | 146 | Minimum Margin | 580 | 79.89% | [500-1000] MW
20251212 | December | 1730 |  | 7720 | 667 | 726 | 113 | Minimum Margin | 613 | 84.44% | [500-1000] MW

## DA TTC Validation
DA Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | ANTC |  |  | LimitedBy |  | TTC Validation Reduction |  |  | Reason for TTC Reduction |  | Reason for TTC Reduction AT |  | Reason for TTC Reduction CH |  | Reason for TTC Reduction FR |  | Reason for TTC Reduction IT |  | Reason for TTC Reduction SI
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | Smoothing | Reason | NTCBilateral | Reason | MNII | Reason | Bilateral | Reason | Bilateral | Reason | MNII | Reason
20251001 | October | 0030 | 10650 |  |  | 8758 |  |  | -3112 | -3112 | -1243 | Critical Branch | Validation phase | 1892 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8638 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0130 | 10650 |  |  | 8758 |  |  | -3112 | -3112 | -1243 | Critical Branch | Validation phase | 1892 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8638 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0230 | 10650 |  |  | 8758 |  |  | -3112 | -3112 | -1243 | Critical Branch | Validation phase | 1892 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8638 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0330 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 1460 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8603 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0430 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 1460 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8603 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0530 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 1460 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8603 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0630 | 10199 |  |  | 8739 |  |  | -5604 | -5604 | -4147 | Critical Branch | Validation phase | 1460 | NA | 0 |  |  | 375 | Reduction because NTC over thermal limit on border | 8603 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0730 |  | 9107 | 817 |  | 8201 | 763 | -5953 | -5953 | 0 | Critical Branch | Validation phase | NA | 960 | 5953 |  |  | 248 |  | 9220 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0830 |  | 7907 | 817 |  | 7054 | 762 | -4985 | -4985 | 0 | Critical Branch | Validation phase | NA | 908 | 4985 |  |  | 246 |  | 8020 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 0930 |  | 7716 | 701 |  | 7454 | 701 | -4583 | -4583 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 262 | 4583 |  |  | 359 |  |  |  | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1030 |  | 7716 | 701 |  | 7454 | 701 | -4583 | -4583 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 262 | 4583 |  |  | 359 |  |  |  | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1130 |  | 7716 | 701 |  | 7454 | 701 | -4583 | -4583 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 262 | 4583 |  |  | 359 |  |  |  | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1230 |  | 8645 | 779 |  | 7879 | 779 | 550 | 450 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 766 | -450 |  |  | 390 | Reduction because NTC over thermal limit on border |  |  | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1330 |  | 8645 | 779 |  | 7879 | 779 | 550 | 450 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 766 | -450 |  |  | 390 | Reduction because NTC over thermal limit on border |  |  | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1430 |  | 8645 | 779 |  | 7879 | 779 | 550 | 450 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 766 | -450 |  |  | 390 | Reduction because NTC over thermal limit on border |  |  | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1530 |  | 8642 | 740 |  | 7588 | 688 | -3912 | -3912 | 0 | Critical Branch | Validation phase | NA | 1106 | 3912 |  |  | 390 | Reduction because NTC over thermal limit on border | 8357 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1630 |  | 8843 | 740 |  | 7782 | 688 | -4153 | -4153 | 0 | Critical Branch | Validation phase | NA | 1113 | 4153 |  |  | 390 | Reduction because NTC over thermal limit on border | 8558 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1730 |  | 8843 | 740 |  | 7782 | 688 | -4153 | -4153 | 0 | Critical Branch | Validation phase | NA | 1113 | 4153 |  |  | 390 | Reduction because NTC over thermal limit on border | 8558 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1830 |  | 7232 | 732 |  | 7112 | 729 | -2967 | -2967 | 0 | Critical Branch | Validation phase | NA | 123 | 2967 |  |  | 253 |  | 7627 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 1930 |  | 7232 | 732 |  | 7112 | 729 | -2967 | -2967 | 0 | Critical Branch | Validation phase | NA | 123 | 2967 |  |  | 253 |  | 7627 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2030 |  | 7232 | 732 |  | 7112 | 729 | -2967 | -2967 | 0 | Critical Branch | Validation phase | NA | 123 | 2967 |  |  | 253 |  | 7627 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2130 |  | 8169 | 700 |  | 7662 | 682 | -3536 | -3536 | 0 | Critical Branch | Validation phase | NA | 525 | 3536 |  |  | 369 |  | 8212 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2230 |  | 8169 | 700 |  | 7662 | 682 | -3536 | -3536 | 0 | Critical Branch | Validation phase | NA | 525 | 3536 |  |  | 369 |  | 8212 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251001 | October | 2330 |  | 7615 | 720 |  | 7326 | 707 | -2964 | -2964 | 0 | Critical Branch | Validation phase | NA | 302 | 2964 |  |  | 352 |  | 7607 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 3600 | Outage - Bus bar 2.1 GENISSIAT
20251002 | October | 0030 | 8392 |  |  | 7382 |  |  | -1595 | -1595 | -585 | Critical Branch | Validation phase | 1010 | NA | 0 |  |  |  |  | 7052 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0130 | 8392 |  |  | 7382 |  |  | -1595 | -1595 | -585 | Critical Branch | Validation phase | 1010 | NA | 0 |  |  |  |  | 7052 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0230 | 8392 |  |  | 7382 |  |  | -1595 | -1595 | -585 | Critical Branch | Validation phase | 1010 | NA | 0 |  |  |  |  | 7052 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0330 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 1172 | NA | 0 |  |  |  |  | 6917 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0430 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 1172 | NA | 0 |  |  |  |  | 6917 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0530 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 1172 | NA | 0 |  |  |  |  | 6917 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0630 | 8419 |  |  | 7247 |  |  | -4829 | -4829 | -3657 | Critical Branch | Validation phase | 1172 | NA | 0 |  |  |  |  | 6917 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0730 |  | 7687 | 629 |  | 7631 | 624 | -3645 | -3645 | 0 | Critical Branch | Validation phase | NA | 61 | 3645 |  |  |  |  | 7709 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 0830 |  | 7687 | 629 |  | 7631 | 624 | -3645 | -3645 | 0 | Critical Branch | Validation phase | NA | 61 | 3645 |  |  |  |  | 7709 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251002 | October | 1130 | 7719 |  |  | 7544 |  |  | -4548 | -4548 | -4372 | Critical Branch | Smoothing ramp | 175 | NA | 0 | Smoothing | Smoothing ramp
20251002 | October | 1230 | 8306 |  |  | 6044 |  |  | -2102 | -2102 | 160 | Critical Branch | Validation phase | 2262 | NA | 2422 |  |  |  |  | 5709 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1330 | 8306 |  |  | 6044 |  |  | -2102 | -2102 | 160 | Critical Branch | Validation phase | 2262 | NA | 2422 |  |  |  |  | 5709 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1430 | 8306 |  |  | 6044 |  |  | -2102 | -2102 | 160 | Critical Branch | Validation phase | 2262 | NA | 2422 |  |  |  |  | 5709 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1530 | 7651 |  |  | 6541 |  |  | -4184 | -4184 | -3074 | Critical Branch | Validation phase | 1110 | NA | 0 |  |  |  |  | 6206 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1630 | 8511 |  |  | 7401 |  |  | -5077 | -5077 | -3967 | Critical Branch | Validation phase | 1110 | NA | 0 |  |  |  |  | 7066 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1730 | 8511 |  |  | 7401 |  |  | -5077 | -5077 | -3967 | Critical Branch | Validation phase | 1110 | NA | 0 |  |  |  |  | 7066 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251002 | October | 1830 | 8016 |  |  | 7089 |  |  | 735 | 0 | 1662 | Critical Branch | Validation phase | 927 | NA | 3324 |  |  |  |  | 6754 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 1930 | 8016 |  |  | 7089 |  |  | 735 | 0 | 1662 | Critical Branch | Validation phase | 927 | NA | 3324 |  |  |  |  | 6754 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2030 | 8016 |  |  | 7089 |  |  | 735 | 0 | 1662 | Critical Branch | Validation phase | 927 | NA | 3324 |  |  |  |  | 6754 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2130 | 8985 |  |  | 7791 |  |  | -2573 | -2573 | -1379 | Critical Branch | Validation phase | 1194 | NA | 0 |  |  |  |  | 7456 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2230 | 8985 |  |  | 7791 |  |  | -2573 | -2573 | -1379 | Critical Branch | Validation phase | 1194 | NA | 0 |  |  |  |  | 7456 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251002 | October | 2330 | 8375 |  |  | 7181 |  |  | -1949 | -1949 | -755 | Critical Branch | Validation phase | 1194 | NA | 0 |  |  |  |  | 6851 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251003 | October | 0030 | 9044 |  |  | 8293 |  |  | -2397 | -2397 | -1646 | Critical Branch | Validation phase | 751 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7963 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0130 | 9044 |  |  | 8293 |  |  | -2397 | -2397 | -1646 | Critical Branch | Validation phase | 751 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7963 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0230 | 9044 |  |  | 8293 |  |  | -2397 | -2397 | -1646 | Critical Branch | Validation phase | 751 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7963 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0330 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 701 | NA | 0 |  |  | 432 |  | 7860 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0430 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 701 | NA | 0 |  |  | 432 |  | 7860 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0530 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 701 | NA | 0 |  |  | 432 |  | 7860 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0630 | 8891 |  |  | 8190 |  |  | -2440 | -2440 | -1739 | Critical Branch | Validation phase | 701 | NA | 0 |  |  | 432 |  | 7860 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0730 | 9415 |  |  | 8844 |  |  | -2644 | -2644 | -2073 | Critical Branch | Validation phase | 571 | NA | 0 |  |  | 444 |  | 8509 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0830 | 9415 |  |  | 8844 |  |  | -2644 | -2644 | -2073 | Critical Branch | Validation phase | 571 | NA | 0 |  |  | 444 |  | 8509 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 0930 | 8600 |  |  | 8599 |  |  | -2137 | -2137 | -2136 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 410
20251003 | October | 1030 | 8600 |  |  | 8599 |  |  | -2137 | -2137 | -2136 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 410
20251003 | October | 1130 | 8600 |  |  | 8599 |  |  | -2137 | -2137 | -2136 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 410
20251003 | October | 1230 |  | 8604 | 835 |  | 8402 | 835 | -1443 | -1443 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 202 | 1443 |  |  | 442 |  |  |  | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1330 |  | 8604 | 835 |  | 8402 | 835 | -1443 | -1443 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 202 | 1443 |  |  | 442 |  |  |  | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1430 |  | 8604 | 835 |  | 8402 | 835 | -1443 | -1443 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 202 | 1443 |  |  | 442 |  |  |  | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1530 | 9182 |  |  | 9077 |  |  | -2694 | -2694 | -2596 | Critical Branch | TTC Validation phase - bilateral reduction | 105 | NA | 0 |  |  | 434 |  |  |  | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1630 | 9182 |  |  | 9077 |  |  | -2694 | -2694 | -2596 | Critical Branch | TTC Validation phase - bilateral reduction | 105 | NA | 0 |  |  | 434 |  |  |  | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1730 | 9182 |  |  | 9077 |  |  | -2694 | -2694 | -2596 | Critical Branch | TTC Validation phase - bilateral reduction | 105 | NA | 0 |  |  | 434 |  |  |  | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 1830 |  | 7244 | 574 |  | 7244 | 574 | 2826 | 0 | 0 | Critical Branch | Critical Branch | NA | 0 | 0 |  |  | 382
20251003 | October | 1930 |  | 7244 | 574 |  | 7244 | 574 | 2826 | 0 | 0 | Critical Branch | Critical Branch | NA | 0 | 0 |  |  | 382
20251003 | October | 2030 |  | 7244 | 574 |  | 7244 | 574 | 2826 | 0 | 0 | Critical Branch | Critical Branch | NA | 0 | 0 |  |  | 382
20251003 | October | 2130 | 9726 |  |  | 9080 |  |  | 4926 | 208 | 5475 | Minimum Margin | Validation phase | 646 | NA | 10742 |  |  | 445 |  | 8851 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 2230 | 9708 |  |  | 9080 |  |  | 4926 | 190 | 5475 | Minimum Margin | Validation phase | 628 | NA | 10760 |  |  | 450 | Reduction because NTC over thermal limit on border | 8851 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251003 | October | 2330 | 9064 |  |  | 8576 |  |  | 5068 | 156 | 5400 | Minimum Margin | Validation phase | 488 | NA | 10644 |  |  | 435 | Reduction because NTC over thermal limit on border | 8246 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Retrait Barre Genissiat 400kV
20251004 | October | 0030 | 9051 |  |  | 8673 |  |  | -2440 | -2440 | -2063 | Critical Branch | Validation phase | 378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8346 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0130 | 9051 |  |  | 8673 |  |  | -2440 | -2440 | -2063 | Critical Branch | Validation phase | 378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8346 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0230 | 9051 |  |  | 8673 |  |  | -2440 | -2440 | -2063 | Critical Branch | Validation phase | 378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8346 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0330 | 8896 |  |  | 8731 |  |  | -2356 | -2356 | -2195 | Critical Branch | Validation phase | 165 | NA | 0 |  |  | 432 |  | 8459 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0430 | 8896 |  |  | 8731 |  |  | -2356 | -2356 | -2195 | Critical Branch | Validation phase | 165 | NA | 0 |  |  | 432 |  | 8459 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0530 | 8896 |  |  | 8731 |  |  | -2356 | -2356 | -2195 | Critical Branch | Validation phase | 165 | NA | 0 |  |  | 432 |  | 8459 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0630 | 8696 |  |  | 8533 |  |  | -2133 | -2133 | -1974 | Critical Branch | Validation phase | 163 | NA | 0 |  |  | 432 |  | 8259 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0730 | 8869 |  |  | 8697 |  |  | -2465 | -2465 | -2293 | Critical Branch | Validation phase | 172 | NA | 0 |  |  | 429 |  | 8362 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0830 | 8869 |  |  | 8697 |  |  | -2465 | -2465 | -2293 | Critical Branch | Validation phase | 172 | NA | 0 |  |  | 429 |  | 8362 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 0930 | 8886 |  |  | 8686 |  |  | -1548 | -1548 | -1348 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 430 |  | 8351 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1030 | 8886 |  |  | 8686 |  |  | -1548 | -1548 | -1348 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 430 |  | 8351 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1130 | 8886 |  |  | 8686 |  |  | -1548 | -1548 | -1348 | Critical Branch | Validation phase | 200 | NA | 0 |  |  | 430 |  | 8351 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1230 | 8193 |  |  | 8163 |  |  | -2313 | -2313 | -2283 | Critical Branch | Validation phase | 30 | NA | 0 |  |  | 401 |  | 7828 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 1330 | 8193 |  |  | 8163 |  |  | -2313 | -2313 | -2283 | Critical Branch | Validation phase | 30 | NA | 0 |  |  | 401 |  | 7828 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 1430 | 8193 |  |  | 8163 |  |  | -2313 | -2313 | -2283 | Critical Branch | Validation phase | 30 | NA | 0 |  |  | 401 |  | 7828 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 1530 |  | 8156 | 978 |  | 7836 | 961 | -958 | -958 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 337 | 958 |  |  | 241 | Reduction because NTC over thermal limit on border |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1630 |  | 8156 | 978 |  | 7836 | 961 | -958 | -958 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 337 | 958 |  |  | 241 | Reduction because NTC over thermal limit on border |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1730 |  | 8156 | 978 |  | 7836 | 961 | -958 | -958 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 337 | 958 |  |  | 241 | Reduction because NTC over thermal limit on border |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251004 | October | 1830 |  | 7923 | 654 |  | 7922 | 654 | -5636 | -5636 | 0 | Critical Branch | Critical Branch | NA | 1 | 5636 |  |  | 412
20251004 | October | 1930 |  | 7923 | 654 |  | 7922 | 654 | -5636 | -5636 | 0 | Critical Branch | Critical Branch | NA | 1 | 5636 |  |  | 412
20251004 | October | 2030 |  | 7923 | 654 |  | 7922 | 654 | -5636 | -5636 | 0 | Critical Branch | Critical Branch | NA | 1 | 5636 |  |  | 412
20251004 | October | 2130 | 8829 |  |  | 8737 |  |  | -2409 | -2409 | -2317 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 420 |  | 8402 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 2230 | 8829 |  |  | 8737 |  |  | -2409 | -2409 | -2317 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 420 |  | 8402 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251004 | October | 2330 | 8219 |  |  | 8127 |  |  | -1790 | -1790 | -1698 | Critical Branch | Validation phase | 92 | NA | 0 |  |  | 403 |  | 7797 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251005 | October | 0030 | 8418 |  |  | 8063 |  |  | -557 | -557 | -202 | Critical Branch | Validation phase | 355 | NA | 0 |  |  | 412 |  | 7733 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251005 | October | 0130 | 8418 |  |  | 8063 |  |  | -557 | -557 | -202 | Critical Branch | Validation phase | 355 | NA | 0 |  |  | 412 |  | 7733 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251005 | October | 0230 | 8418 |  |  | 8063 |  |  | -557 | -557 | -202 | Critical Branch | Validation phase | 355 | NA | 0 |  |  | 412 |  | 7733 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251005 | October | 0330 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 22 | 1086 |  |  | 425 |  |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0430 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 22 | 1086 |  |  | 425 |  |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0530 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 22 | 1086 |  |  | 425 |  |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0630 |  | 8054 | 795 |  | 8032 | 795 | -1086 | -1086 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 22 | 1086 |  |  | 425 |  |  |  | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0730 |  | 8110 | 751 |  | 7935 | 736 | -1097 | -1097 | 0 | Critical Branch | Validation phase | NA | 190 | 1097 |  |  | 427 |  | 8120 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0830 |  | 7810 | 751 |  | 7633 | 735 | -710 | -710 | 0 | Critical Branch | Validation phase | NA | 193 | 710 |  |  | 424 |  | 7820 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 0930 |  | 5972 | 519 |  | 5971 | 519 | -3294 | -3294 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 1 | 3294 |  |  | 339
20251005 | October | 1030 |  | 5972 | 519 |  | 5971 | 519 | -3294 | -3294 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 1 | 3294 |  |  | 339
20251005 | October | 1130 |  | 5972 | 519 |  | 5971 | 519 | -3294 | -3294 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | NA | 1 | 3294 |  |  | 339
20251005 | October | 1230 |  | 5972 | 417 |  | 5971 | 417 | -3016 | -3016 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | NA | 1 | 3016 |  |  | 339
20251005 | October | 1330 |  | 5972 | 417 |  | 5971 | 417 | -3016 | -3016 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | NA | 1 | 3016 |  |  | 339
20251005 | October | 1430 |  | 5972 | 417 |  | 5971 | 417 | -3016 | -3016 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | NA | 1 | 3016 |  |  | 339
20251005 | October | 1530 |  | 8406 | 782 |  | 7453 | 698 | 171 | 171 | 0 | Adjustment reached | Validation phase | NA | 1037 | -171 |  |  | 417 |  | 7719 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1630 |  | 8536 | 767 |  | 7755 | 698 | -212 | -212 | 0 | Critical Branch | Validation phase | NA | 850 | 212 |  |  | 435 | Reduction because NTC over thermal limit on border | 8019 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1730 |  | 8536 | 767 |  | 7755 | 698 | -212 | -212 | 0 | Critical Branch | Validation phase | NA | 850 | 212 |  |  | 435 | Reduction because NTC over thermal limit on border | 8019 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1830 |  | 8461 | 795 |  | 7755 | 733 | -3076 | -3076 | 0 | Critical Branch | Validation phase | NA | 768 | 3076 |  |  | 435 | Reduction because NTC over thermal limit on border | 8485 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 1930 |  | 8461 | 795 |  | 7755 | 733 | -3076 | -3076 | 0 | Critical Branch | Validation phase | NA | 768 | 3076 |  |  | 435 | Reduction because NTC over thermal limit on border | 8485 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2030 |  | 8461 | 795 |  | 7755 | 733 | -3076 | -3076 | 0 | Critical Branch | Validation phase | NA | 768 | 3076 |  |  | 435 | Reduction because NTC over thermal limit on border | 8485 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2130 |  | 8389 | 806 |  | 8137 | 797 | -1227 | -1227 | 0 | Critical Branch | Validation phase | NA | 261 | 1227 |  |  | 435 | Reduction because NTC over thermal limit on border | 8410 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2230 |  | 8389 | 806 |  | 8137 | 797 | -1227 | -1227 | 0 | Critical Branch | Validation phase | NA | 261 | 1227 |  |  | 435 | Reduction because NTC over thermal limit on border | 8410 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251005 | October | 2330 |  | 8389 | 806 |  | 8137 | 797 | -1227 | -1227 | 0 | Critical Branch | Validation phase | NA | 261 | 1227 |  |  | 435 | Reduction because NTC over thermal limit on border | 8410 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 4000 | Overload - Planned Outage Busbar 1.2 Genissiat
20251006 | October | 0030 | 8421 |  |  | 8063 |  |  | -2116 | -2116 | -1758 | Critical Branch | Validation phase | 358 | NA | 0 |  |  | 412 |  | 7733 | Values from previous day, cause of missing data
20251006 | October | 0130 | 8421 |  |  | 8063 |  |  | -2116 | -2116 | -1758 | Critical Branch | Validation phase | 358 | NA | 0 |  |  | 412 |  | 7733 | Values from previous day, cause of missing data
20251006 | October | 0230 | 8421 |  |  | 8063 |  |  | -2116 | -2116 | -1758 | Critical Branch | Validation phase | 358 | NA | 0 |  |  | 412 |  | 7733 | Values from previous day, cause of missing data
20251006 | October | 0330 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 402
20251006 | October | 0430 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 402
20251006 | October | 0530 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 402
20251006 | October | 0630 | 8178 |  |  | 8178 |  |  | -748 | -748 | -748 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 402
20251006 | October | 0730 | 8802 |  |  | 7693 |  |  | -2114 | -2114 | -1047 | Critical Branch | Validation phase | 1109 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 7638 | Values from previous day, cause of missing data | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 0830 | 8562 |  |  | 7430 |  |  | -1893 | -1893 | -798 | Critical Branch | Validation phase | 1132 | NA | 0 |  |  | 210 |  | 7338 | Values from previous day, cause of missing data | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 0930 | 6250 |  |  | 6250 |  |  | 3946 | 0 | 3946 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | NA | 3946 |  |  | 210
20251006 | October | 1030 | 6472 |  |  | 6472 |  |  | 3946 | 222 | 3724 | Minimum Margin | Minimum Margin | 0 | NA | 7226 |  |  | 210
20251006 | October | 1130 | 6461 |  |  | 6461 |  |  | 3946 | 211 | 3735 | Minimum Margin | Minimum Margin | 0 | NA | 7259 |  |  | 210
20251006 | October | 1230 | 6439 |  |  | 6439 |  |  | 4444 | 189 | 4255 | Minimum Margin | Minimum Margin | 0 | NA | 8321 |  |  | 210
20251006 | October | 1330 | 6439 |  |  | 6439 |  |  | 4444 | 189 | 4255 | Minimum Margin | Minimum Margin | 0 | NA | 8321 |  |  | 210
20251006 | October | 1430 | 6439 |  |  | 6439 |  |  | 4444 | 189 | 4255 | Minimum Margin | Minimum Margin | 0 | NA | 8321 |  |  | 210
20251006 | October | 1530 | 7389 |  |  | 7276 |  |  | 2679 | 211 | 2706 | Minimum Margin | TTC Validation phase - bilateral reduction | 113 | NA | 5201 |  |  | 210 |  |  |  | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 1630 | 7178 |  |  | 7178 |  |  | 2679 | 0 | 2679 | Critical Branch | Critical Branch | 0 | NA | 2679 |  |  | 210
20251006 | October | 1730 | 7178 |  |  | 7178 |  |  | 2679 | 0 | 2679 | Critical Branch | Critical Branch | 0 | NA | 2679 |  |  | 210
20251006 | October | 1830 | 8767 |  |  | 7495 |  |  | -2804 | -2804 | -1581 | Critical Branch | Validation phase | 1272 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7458 | Values from previous day, cause of missing data | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 1930 | 8767 |  |  | 7495 |  |  | -2804 | -2804 | -1581 | Critical Branch | Validation phase | 1272 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7458 | Values from previous day, cause of missing data | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2030 | 8767 |  |  | 7495 |  |  | -2804 | -2804 | -1581 | Critical Branch | Validation phase | 1272 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border | 7458 | Values from previous day, cause of missing data | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2130 | 8218 |  |  | 7725 |  |  | -1914 | -1914 | -1494 | Critical Branch | TTC Validation phase - bilateral reduction | 493 | NA | 0 |  |  | 210 |  |  |  | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2230 | 8218 |  |  | 7725 |  |  | -1914 | -1914 | -1494 | Critical Branch | TTC Validation phase - bilateral reduction | 493 | NA | 0 |  |  | 210 |  |  |  | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251006 | October | 2330 | 7623 |  |  | 7281 |  |  | -1302 | -1302 | -1009 | Critical Branch | TTC Validation phase - bilateral reduction | 342 | NA | 0 |  |  | 210 |  |  |  | 3000 | Outage - CHAFFARD - GRANDE ILE 1
20251007 | October | 0030 | 7776 |  |  | 7361 |  |  | -4682 | -4682 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 415 | NA | 0 |  |  | 209 |  |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0130 | 7776 |  |  | 7361 |  |  | -4682 | -4682 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 415 | NA | 0 |  |  | 209 |  |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0230 | 7776 |  |  | 7361 |  |  | -4682 | -4682 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 415 | NA | 0 |  |  | 209 |  |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0330 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 505 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0430 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 505 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0530 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 505 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0630 | 7962 |  |  | 7457 |  |  | -4449 | -4449 | -3964 | Critical Branch | TTC Validation phase - bilateral reduction | 505 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0730 | 7790 |  |  | 7393 |  |  | 6687 | 0 | 7318 | Critical Branch | Validation phase | 397 | NA | 14636 |  |  | 199 |  | 7270 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0830 | 7790 |  |  | 7393 |  |  | 6687 | 0 | 7318 | Critical Branch | Validation phase | 397 | NA | 14636 |  |  | 199 |  | 7270 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 0930 | 7664 |  |  | 7424 |  |  | 3667 | 0 | 4172 | Critical Branch | TTC Validation phase - bilateral reduction | 240 | NA | 8344 |  |  | 197 |  |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1030 | 7664 |  |  | 7424 |  |  | 3667 | 0 | 4172 | Critical Branch | TTC Validation phase - bilateral reduction | 240 | NA | 8344 |  |  | 197 |  |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1130 | 7790 |  |  | 7492 |  |  | 3667 | 126 | 4167 | Minimum Margin | TTC Validation phase - bilateral reduction | 298 | NA | 8208 |  |  | 199 |  |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1230 | 8420 |  |  | 7218 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1202 | NA | 0 |  |  | 210 |  | 7329 | Calculation not possible, values manuell adapted | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1 |  |  | 6947 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251007 | October | 1330 | 8420 |  |  | 7218 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1202 | NA | 0 |  |  | 210 |  | 7329 | Calculation not possible, values manuell adapted | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1 |  |  | 6947 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251007 | October | 1430 | 8420 |  |  | 7218 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1202 | NA | 0 |  |  | 210 |  | 7329 | Calculation not possible, values manuell adapted | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1 |  |  | 6947 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251007 | October | 1530 | 8420 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 995 | NA | 0 |  |  | 210 |  | 7329 | Calculation not possible, values manuell adapted | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1630 | 8420 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 995 | NA | 0 |  |  | 210 |  | 7329 | Calculation not possible, values manuell adapted | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1730 | 8420 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 995 | NA | 0 |  |  | 210 |  | 7329 | Calculation not possible, values manuell adapted | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 1830 | 7226 |  |  | 7225 |  |  | -1953 | -1953 | -1953 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 190
20251007 | October | 1930 | 7226 |  |  | 7225 |  |  | -1953 | -1953 | -1953 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 190
20251007 | October | 2030 | 7226 |  |  | 7225 |  |  | -1953 | -1953 | -1953 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 190
20251007 | October | 2130 | 8572 |  |  | 7915 |  |  | -2739 | -2739 | -2183 | Critical Branch | TTC Validation phase - bilateral reduction | 657 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 2230 | 8572 |  |  | 7915 |  |  | -2739 | -2739 | -2183 | Critical Branch | TTC Validation phase - bilateral reduction | 657 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251007 | October | 2330 | 7977 |  |  | 7464 |  |  | -2128 | -2128 | -1692 | Critical Branch | TTC Validation phase - bilateral reduction | 513 | NA | 0 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Planed outage on CHAFFARD - GDE ILE 1
20251008 | October | 0030 | 8488 |  |  | 7387 |  |  | 2581 | 196 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1101 | NA | -196 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0130 | 8488 |  |  | 7387 |  |  | 2581 | 196 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1101 | NA | -196 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0230 | 8488 |  |  | 7387 |  |  | 2581 | 196 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1101 | NA | -196 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0330 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1183 | NA | -200 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0430 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1183 | NA | -200 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0530 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1183 | NA | -200 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0630 | 8570 |  |  | 7387 |  |  | 3101 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1183 | NA | -200 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage Chaffard - Gd ILE 1
20251008 | October | 0730 | 7983 |  |  | 7235 |  |  | -5170 | -5170 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 748 | NA | 5170 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 0830 | 7983 |  |  | 7151 |  |  | -5170 | -5170 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 832 | NA | 5170 |  |  | 190 |  |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 0930 |  | 5071 | 377 | 5651 |  |  | 5465 | 2 | 6208 | Minimum Margin | Minimum Margin | NA | NA | 12414 |  |  | 147
20251008 | October | 1030 |  | 5142 | 384 | 5727 |  |  | 5465 | 73 | 6133 | Minimum Margin | Minimum Margin | NA | NA | 12193 |  |  | 150
20251008 | October | 1130 |  | 5301 | 400 | 5898 |  |  | 5465 | 233 | 5962 | Minimum Margin | Minimum Margin | NA | NA | 11691 |  |  | 155
20251008 | October | 1230 |  | 5265 | 529 | 5868 |  |  | 5185 | 196 | 5578 | Minimum Margin | Minimum Margin | NA | NA | 10960 |  |  | 154
20251008 | October | 1330 |  | 5265 | 529 | 5868 |  |  | 5185 | 196 | 5578 | Minimum Margin | Minimum Margin | NA | NA | 10960 |  |  | 154
20251008 | October | 1430 |  | 5265 | 529 | 5868 |  |  | 5185 | 196 | 5578 | Minimum Margin | Minimum Margin | NA | NA | 10960 |  |  | 154
20251008 | October | 1530 |  | 7231 | 830 | 7144 |  |  | 2750 | 187 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | -187 |  |  | 119 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1630 |  | 7141 | 819 | 7100 |  |  | 2750 | 97 | 4796 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 9495 |  |  | 128 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1730 |  | 7244 | 831 | 7153 |  |  | 2750 | 200 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | -200 |  |  | 128 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1830 |  | 6965 | 852 | 6940 |  |  | -5142 | -5142 | -4628 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | 100 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 1930 |  | 6965 | 852 | 6940 |  |  | -5142 | -5142 | -4628 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | 100 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 2030 |  | 6965 | 852 | 6940 |  |  | -5142 | -5142 | -4628 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | 100 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 2130 |  | 8091 | 917 | 7235 |  |  | -2595 | -2595 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 2595 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 2230 |  | 8091 | 917 | 7235 |  |  | -2595 | -2595 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 2595 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251008 | October | 2330 |  | 7559 | 937 | 6787 |  |  | -1945 | -1945 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 1945 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1
20251009 | October | 0030 | 8374 |  |  | 7423 |  |  | 1927 | 220 | 3803 | Minimum Margin | TTC Validation phase - bilateral reduction | 951 | NA | 7386 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0130 | 8374 |  |  | 7423 |  |  | 1927 | 220 | 3803 | Minimum Margin | TTC Validation phase - bilateral reduction | 951 | NA | 7386 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0230 | 8374 |  |  | 7423 |  |  | 1927 | 220 | 3803 | Minimum Margin | TTC Validation phase - bilateral reduction | 951 | NA | 7386 |  |  | 210 | Reduction because NTC over thermal limit on border |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0330 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 131 | NA | 6490 |  |  | 195 |  |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0430 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 131 | NA | 6490 |  |  | 195 |  |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0530 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 131 | NA | 6490 |  |  | 195 |  |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0630 | 6505 |  |  | 6374 |  |  | 3305 | 236 | 3363 | Minimum Margin | TTC Validation phase - bilateral reduction | 131 | NA | 6490 |  |  | 195 |  |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0730 | 7401 |  |  | 6988 |  |  | -2202 | -2202 | -1791 | Critical Branch | TTC Validation phase - bilateral reduction | 413 | NA | 0 |  |  | 202 |  |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0830 | 7401 |  |  | 6984 |  |  | -2202 | -2202 | -1789 | Critical Branch | TTC Validation phase - bilateral reduction | 417 | NA | 0 |  |  | 198 |  |  |  | 2400 | Outage - RDCR FIL Link 1
20251009 | October | 0930 | 5766 |  |  | 5765 |  |  | 5231 | 116 | 5115 | Minimum Margin | Minimum Margin | 1 | NA | 10114 |  |  | 174
20251009 | October | 1030 | 5887 |  |  | 5886 |  |  | 5231 | 237 | 4994 | Minimum Margin | Minimum Margin | 1 | NA | 9751 |  |  | 176
20251009 | October | 1130 | 5883 |  |  | 5882 |  |  | 5231 | 233 | 4998 | Minimum Margin | Minimum Margin | 1 | NA | 9763 |  |  | 176
20251009 | October | 1230 | 5890 |  |  | 5501 |  |  | 2935 | 240 | 3598 | Minimum Margin | TTC Validation phase - bilateral reduction | 389 | NA | 6956 |  |  | 176 |  |  |  | 1800 | Outage - RDCR FIL Link 1 & 2
20251009 | October | 1330 | 5322 |  |  | 5322 |  |  | 4623 | 272 | 4351 | Minimum Margin | Minimum Margin | 0 | NA | 8430 |  |  | 174
20251009 | October | 1430 | 5322 |  |  | 5322 |  |  | 4623 | 272 | 4351 | Minimum Margin | Minimum Margin | 0 | NA | 8430 |  |  | 174
20251009 | October | 1530 |  | 6408 | 710 |  | 5819 | 710 | 3713 | 254 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 589 | -254 |  |  | 205 |  |  |  | 1800 | Outage - RDCR FIL Link 1 & 2
20251009 | October | 1630 |  | 6408 | 710 |  | 5823 | 710 | 3713 | 254 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 585 | -254 |  |  | 209 |  |  |  | 1800 | Outage - RDCR FIL Link 1 & 2
20251009 | October | 1730 |  | 6648 | 710 |  | 6055 | 710 | 3613 | 254 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 593 | -254 |  |  | 440 |  |  |  | 1800 | Outage - RDCR FIL Link 1 & 2
20251009 | October | 1830 |  | 8561 | 795 |  | 7598 | 795 | -4451 | -4451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 963 | 4451 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - RO CHAFFARD G.ILE 1
20251009 | October | 1930 |  | 8561 | 795 |  | 7598 | 795 | -4451 | -4451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 963 | 4451 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2030 |  | 8561 | 795 |  | 7598 | 795 | -4451 | -4451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 963 | 4451 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2130 | 9155 |  |  | 8324 |  |  | -2823 | -2823 | -2066 | Critical Branch | Validation phase | 831 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 8813 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2230 | 9155 |  |  | 8324 |  |  | -2823 | -2823 | -2066 | Critical Branch | Validation phase | 831 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 8813 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - RO CHAFFARD G.ILE 1
20251009 | October | 2330 | 8545 |  |  | 7852 |  |  | -2208 | -2208 | -1575 | Critical Branch | Validation phase | 693 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8208 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - RO CHAFFARD G.ILE 1
20251010 | October | 0930 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2325 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1030 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2325 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1130 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2325 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1230 | 8660 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2325 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1330 | 8260 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1925 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1430 | 8260 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1925 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251010 | October | 1530 | 8660 |  |  | 7385 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1275 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1630 | 8660 |  |  | 7385 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1275 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1730 | 8660 |  |  | 7385 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1275 | NA | 0 |  |  |  |  | 7084 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1830 | 7707 |  |  | 7545 |  |  | -2971 | -2971 | -2810 | Critical Branch | TTC Validation phase - bilateral reduction | 162 | NA | 0 | [6 empty] | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 1930 | 7707 |  |  | 7545 |  |  | -2971 | -2971 | -2810 | Critical Branch | TTC Validation phase - bilateral reduction | 162 | NA | 0 | [6 empty] | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2030 | 7707 |  |  | 7545 |  |  | -2971 | -2971 | -2810 | Critical Branch | TTC Validation phase - bilateral reduction | 162 | NA | 0 | [6 empty] | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2130 | 8660 |  |  | 7736 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 924 | NA | 0 |  |  |  |  | 7715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2230 | 8660 |  |  | 7736 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 924 | NA | 0 |  |  |  |  | 7715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251010 | October | 2330 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0330 | 6973 |  |  | 6874 |  |  | 4022 | 215 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 99 | NA | 7809 | [6 empty] | 2843 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0430 | 6973 |  |  | 6874 |  |  | 4022 | 215 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 99 | NA | 7809 | [6 empty] | 2843 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0530 | 6973 |  |  | 6874 |  |  | 4022 | 215 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 99 | NA | 7809 | [6 empty] | 2843 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0630 | 6979 |  |  | 6877 |  |  | 4022 | 221 | 4012 | Minimum Margin | TTC Validation phase - bilateral reduction | 102 | NA | 7803 | [6 empty] | 2843 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 0930 | 6950 |  |  | 6750 |  |  | 1879 | 447 | 1701 | Minimum Margin | TTC Validation phase - bilateral reduction | 200 | NA | 2955 | [6 empty] | 2626 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 1030 | 6778 |  |  | 6655 |  |  | 1879 | 275 | 1770 | Minimum Margin | TTC Validation phase - bilateral reduction | 123 | NA | 3265 | [6 empty] | 2626 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 1130 | 6950 |  |  | 6750 |  |  | 1879 | 447 | 1701 | Minimum Margin | TTC Validation phase - bilateral reduction | 200 | NA | 2955 | [6 empty] | 2626 | Outage - Outage Chaffard - Gd ILE 1
20251011 | October | 1830 | 6490 |  |  | 6202 |  |  | -1151 | -1151 | -863 | TTC Selection - LTTC | Validation phase | 288 | NA | 0 |  |  |  |  | 5867 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251011 | October | 1930 | 6490 |  |  | 6202 |  |  | -1151 | -1151 | -863 | TTC Selection - LTTC | Validation phase | 288 | NA | 0 |  |  |  |  | 5867 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251011 | October | 2030 | 6490 |  |  | 6202 |  |  | -1151 | -1151 | -863 | TTC Selection - LTTC | Validation phase | 288 | NA | 0 |  |  |  |  | 5867 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251011 | October | 2330 | 6419 |  |  | 6170 |  |  | 591 | 539 | 310 | Minimum Margin | TTC Validation phase - bilateral reduction | 249 | NA | 81 | [6 empty] | 2438 | Outage - Outage Chaffard - Gd ILE 1
20251012 | October | 0030 | 8550 |  |  | 7858 |  |  | -1648 | -1648 | -1073 | Critical Branch | TTC Validation phase - bilateral reduction | 692 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0130 | 8550 |  |  | 7858 |  |  | -1648 | -1648 | -1073 | Critical Branch | TTC Validation phase - bilateral reduction | 692 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0230 | 8550 |  |  | 7858 |  |  | -1648 | -1648 | -1073 | Critical Branch | TTC Validation phase - bilateral reduction | 692 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0330 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 754 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0430 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 754 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0530 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 754 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0630 | 8672 |  |  | 7918 |  |  | -1765 | -1765 | -1125 | Critical Branch | TTC Validation phase - bilateral reduction | 754 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0730 | 8543 |  |  | 7855 |  |  | -1910 | -1910 | -1337 | Critical Branch | TTC Validation phase - bilateral reduction | 688 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0830 | 8543 |  |  | 7855 |  |  | -1910 | -1910 | -1337 | Critical Branch | TTC Validation phase - bilateral reduction | 688 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 0930 | 7690 |  |  | 7417 |  |  | 1235 | 218 | 1579 | Minimum Margin | TTC Validation phase - bilateral reduction | 273 | NA | 2940 |  |  | 417 |  |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1030 | 7688 |  |  | 7416 |  |  | 1235 | 216 | 1579 | Minimum Margin | TTC Validation phase - bilateral reduction | 272 | NA | 2942 |  |  | 417 |  |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1130 | 7689 |  |  | 7416 |  |  | 1235 | 217 | 1579 | Minimum Margin | TTC Validation phase - bilateral reduction | 273 | NA | 2941 |  |  | 417 |  |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1230 | 8075 |  |  | 7624 |  |  | 1461 | 202 | 2190 | Minimum Margin | TTC Validation phase - bilateral reduction | 451 | NA | 4178 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1330 | 8079 |  |  | 7626 |  |  | 1461 | 206 | 2190 | Minimum Margin | TTC Validation phase - bilateral reduction | 453 | NA | 4174 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1430 | 8075 |  |  | 7624 |  |  | 1461 | 202 | 2190 | Minimum Margin | TTC Validation phase - bilateral reduction | 451 | NA | 4178 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1530 | 6859 |  |  | 6859 |  |  | 2236 | 218 | 2018 | Minimum Margin | Minimum Margin | 0 | NA | 3818 |  |  | 378
20251012 | October | 1630 | 6859 |  |  | 6859 |  |  | 2236 | 218 | 2018 | Minimum Margin | Minimum Margin | 0 | NA | 3818 |  |  | 378
20251012 | October | 1730 | 6859 |  |  | 6859 |  |  | 2236 | 218 | 2018 | Minimum Margin | Minimum Margin | 0 | NA | 3818 |  |  | 378
20251012 | October | 1830 | 8681 |  |  | 7923 |  |  | -3132 | -3132 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 758 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 1930 | 8681 |  |  | 7923 |  |  | -3132 | -3132 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 758 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2030 | 8681 |  |  | 7923 |  |  | -3132 | -3132 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 758 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2130 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2230 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251012 | October | 2330 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - Outage CHAFFARD - GD ILE 1
20251013 | October | 0030 | 8343 |  |  | 7756 |  |  | -4851 | -4851 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 587 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0130 | 8343 |  |  | 7756 |  |  | -4851 | -4851 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 587 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0230 | 8343 |  |  | 7756 |  |  | -4851 | -4851 | -4279 | Critical Branch | TTC Validation phase - bilateral reduction | 587 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0330 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 449 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0430 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 449 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0530 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 449 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0630 | 8071 |  |  | 7622 |  |  | -4383 | -4383 | -3948 | Critical Branch | TTC Validation phase - bilateral reduction | 449 | NA | 0 |  |  | 435 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0730 | 9001 |  |  | 8249 |  |  | -3247 | -3247 | -2598 | Critical Branch | TTC Validation phase - bilateral reduction | 752 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0830 | 9001 |  |  | 8249 |  |  | -3247 | -3247 | -2598 | Critical Branch | TTC Validation phase - bilateral reduction | 752 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 0930 | 8306 |  |  | 7877 |  |  | -4187 | -4187 | -3771 | Critical Branch | TTC Validation phase - bilateral reduction | 429 | NA | 0 |  |  | 433 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1030 | 8306 |  |  | 7877 |  |  | -4187 | -4187 | -3771 | Critical Branch | TTC Validation phase - bilateral reduction | 429 | NA | 0 |  |  | 433 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1130 | 8306 |  |  | 7870 |  |  | -4187 | -4187 | -3764 | Critical Branch | TTC Validation phase - bilateral reduction | 436 | NA | 0 |  |  | 426 |  |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1230 |  | 6077 | 519 |  | 6077 | 519 | 3218 | 184 | 0 | Minimum Margin | Minimum Margin | NA | 0 | -184 |  |  | 361
20251013 | October | 1330 |  | 6077 | 519 |  | 6077 | 519 | 3218 | 184 | 0 | Minimum Margin | Minimum Margin | NA | 0 | -184 |  |  | 361
20251013 | October | 1430 |  | 6077 | 519 |  | 6077 | 519 | 3218 | 184 | 0 | Minimum Margin | Minimum Margin | NA | 0 | -184 |  |  | 361
20251013 | October | 1530 |  | 6400 | 568 |  | 6400 | 568 | 3150 | 181 | 0 | Minimum Margin | Minimum Margin | NA | 0 | -181 |  |  | 377
20251013 | October | 1630 |  | 6400 | 568 |  | 6400 | 396 | 3150 | 181 | 0 | Minimum Margin | Minimum Margin | NA | 172 | -181 |  |  | 377
20251013 | October | 1730 |  | 6400 | 568 |  | 6400 | 221 | 3150 | 181 | 0 | Minimum Margin | Minimum Margin | NA | 347 | -181 |  |  | 377
20251013 | October | 1830 |  | 7882 | 721 |  | 7285 | 47 | -5008 | -5008 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1271 | 5008 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 1930 |  | 7882 | 721 |  | 7285 | 47 | -5008 | -5008 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1271 | 5008 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 2030 |  | 7882 | 721 |  | 7285 | 47 | -5008 | -5008 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1271 | 5008 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 2130 | 9128 |  |  | 7888 |  |  | -3380 | -3380 | -2197 | Critical Branch | Validation phase | 1240 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 7989 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 2230 | 9128 |  |  | 7888 |  |  | -3380 | -3380 | -2197 | Critical Branch | Validation phase | 1240 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 7989 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251013 | October | 2330 | 8518 |  |  | 7431 |  |  | -2758 | -2758 | -1707 | Critical Branch | Validation phase | 1087 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7384 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | 3000 | Outage - maintenance work on bus bar 2.1 GENISSIAT
20251014 | October | 0030 | 8323 |  |  | 7745 |  |  | -4524 | -4524 | -3961 | Critical Branch | TTC Validation phase - bilateral reduction | 578 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0130 | 8323 |  |  | 7745 |  |  | -4524 | -4524 | -3961 | Critical Branch | TTC Validation phase - bilateral reduction | 578 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0230 | 8323 |  |  | 7745 |  |  | -4524 | -4524 | -3961 | Critical Branch | TTC Validation phase - bilateral reduction | 578 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0330 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 706 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0430 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 706 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0530 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 706 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0630 | 8572 |  |  | 7866 |  |  | -3667 | -3667 | -2764 | Critical Branch | TTC Validation phase - bilateral reduction | 706 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0730 |  | 7604 | 693 |  | 7143 | 693 | -2676 | -2676 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 461 | 2676 |  |  | 434 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0830 |  | 7604 | 693 |  | 7143 | 693 | -2676 | -2676 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 461 | 2676 |  |  | 434 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 0930 | 8437 |  |  | 7949 |  |  | -3188 | -3188 | -2753 | Critical Branch | TTC Validation phase - bilateral reduction | 488 | NA | 0 |  |  | 437 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1030 | 8437 |  |  | 7949 |  |  | -3188 | -3188 | -2753 | Critical Branch | TTC Validation phase - bilateral reduction | 488 | NA | 0 |  |  | 437 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1130 | 8437 |  |  | 7949 |  |  | -3188 | -3188 | -2753 | Critical Branch | TTC Validation phase - bilateral reduction | 488 | NA | 0 |  |  | 437 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1230 | 7575 |  |  | 7467 |  |  | 4695 | 216 | 4713 | Minimum Margin | TTC Validation phase - bilateral reduction | 108 | NA | 9210 |  |  | 390 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1330 | 7575 |  |  | 7467 |  |  | 4695 | 216 | 4713 | Minimum Margin | TTC Validation phase - bilateral reduction | 108 | NA | 9210 |  |  | 390 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1430 | 7575 |  |  | 7467 |  |  | 4695 | 216 | 4713 | Minimum Margin | TTC Validation phase - bilateral reduction | 108 | NA | 9210 |  |  | 390 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1530 |  | 7744 | 710 |  | 7215 | 693 | -4139 | -4139 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 546 | 4139 |  |  | 442 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1630 |  | 7744 | 710 |  | 7215 | 477 | -4139 | -4139 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 762 | 4139 |  |  | 442 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1730 |  | 7744 | 710 |  | 7215 | 262 | -4139 | -4139 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 977 | 4139 |  |  | 442 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1830 |  | 7264 | 888 |  | 6740 | 74 | -2593 | -2593 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1338 | 2593 |  |  | 203 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 1930 |  | 7264 | 888 |  | 6740 | 74 | -2593 | -2593 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1338 | 2593 |  |  | 203 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 2030 |  | 7264 | 888 |  | 6740 | 74 | -2593 | -2593 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1338 | 2593 |  |  | 203 |  |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 2130 |  | 8120 | 765 |  | 7394 | 280 | -3838 | -3838 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1211 | 3838 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 2230 |  | 8120 | 765 |  | 7394 | 513 | -3838 | -3838 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 978 | 3838 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251014 | October | 2330 |  | 7569 | 785 |  | 7018 | 722 | -3200 | -3200 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 614 | 3200 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - Bus bar 2.1 GENISSIAT
20251015 | October | 0030 | 8743 |  |  | 7953 |  |  | -3072 | -3072 | -2365 | Critical Branch | TTC Validation phase - bilateral reduction | 790 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0130 | 8743 |  |  | 7953 |  |  | -3072 | -3072 | -2365 | Critical Branch | TTC Validation phase - bilateral reduction | 790 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0230 | 8743 |  |  | 7953 |  |  | -3072 | -3072 | -2365 | Critical Branch | TTC Validation phase - bilateral reduction | 790 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0330 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0430 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0530 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0630 | 8639 |  |  | 7902 |  |  | -4810 | -4810 | -4094 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0730 |  | 7169 | 791 |  | 6701 | 790 | -4931 | -4931 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 469 | 4931 |  |  | 139 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0830 |  | 7169 | 791 |  | 6701 | 790 | -4931 | -4931 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 469 | 4931 |  |  | 139 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 0930 | 8209 |  |  | 7759 |  |  | -3643 | -3643 | -3219 | Critical Branch | TTC Validation phase - bilateral reduction | 450 | NA | 0 |  |  | 291 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1030 | 8209 |  |  | 7759 |  |  | -3643 | -3643 | -3219 | Critical Branch | TTC Validation phase - bilateral reduction | 450 | NA | 0 |  |  | 291 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1130 | 8209 |  |  | 7753 |  |  | -3643 | -3643 | -3216 | Critical Branch | TTC Validation phase - bilateral reduction | 456 | NA | 0 |  |  | 285 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1230 |  | 5937 | 411 |  | 5936 | 411 | 2566 | 191 | 0 | Minimum Margin | Validation phase | NA | 1 | -191 |  |  | 246 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251015 | October | 1330 |  | 5937 | 411 |  | 5936 | 411 | 2566 | 191 | 0 | Minimum Margin | Validation phase | NA | 1 | -191 |  |  | 246 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251015 | October | 1430 |  | 5943 | 411 |  | 5943 | 411 | 2566 | 197 | 0 | Minimum Margin | Validation phase | NA | 0 | -197 |  |  | 247 | [7 empty] | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251015 | October | 1530 |  | 7205 | 654 |  | 6871 | 652 | 3389 | 198 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 336 | -198 |  |  | 284 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1630 |  | 7200 | 654 |  | 6869 | 450 | 3389 | 193 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 535 | -193 |  |  | 284 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1730 |  | 7209 | 655 |  | 6873 | 249 | 3389 | 202 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 742 | -202 |  |  | 284 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1830 |  | 7460 | 675 |  | 7071 | 47 | 258 | 236 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 1017 | -236 |  |  | 430 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 1930 |  | 7328 | 663 |  | 7003 | 47 | 258 | 103 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 941 | -103 |  |  | 423 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 2030 |  | 7453 | 675 |  | 7067 | 47 | 258 | 229 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 1014 | -229 |  |  | 429 |  |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 2130 |  | 8776 | 817 |  | 7697 | 297 | -3641 | -3641 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1599 | 3641 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 2230 |  | 8776 | 817 |  | 7697 | 547 | -3641 | -3641 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1349 | 3641 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251015 | October | 2330 |  | 8228 | 837 |  | 7311 | 769 | -2975 | -2975 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 985 | 2975 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  | 3000 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
20251016 | October | 0030 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0130 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0230 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0330 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0430 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0530 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0630 | 8050 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0730 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0830 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 0930 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1030 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1130 | 8510 |  |  | 7835 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 675 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1230 | 8510 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2175 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251016 | October | 1330 | 8510 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2175 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251016 | October | 1430 | 8510 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2175 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1 |  |  | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251016 | October | 1530 | 8510 |  |  | 7835 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 675 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1630 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1730 | 8510 |  |  | 7925 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1830 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 1930 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 2030 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 2130 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 2230 | 8810 |  |  | 8225 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 585 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251016 | October | 2330 | 8200 |  |  | 7762 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 438 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0030 | 7348 |  |  | 7233 |  |  | -3434 | -3434 | -3322 | Critical Branch | TTC Validation phase - bilateral reduction | 115 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0130 | 7348 |  |  | 7233 |  |  | -3434 | -3434 | -3322 | Critical Branch | TTC Validation phase - bilateral reduction | 115 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0230 | 7348 |  |  | 7233 |  |  | -3434 | -3434 | -3322 | Critical Branch | TTC Validation phase - bilateral reduction | 115 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0730 | 8350 |  |  | 7903 |  |  | -3035 | -3035 | -2636 | Critical Branch | TTC Validation phase - bilateral reduction | 447 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0830 | 8350 |  |  | 7903 |  |  | -3035 | -3035 | -2636 | Critical Branch | TTC Validation phase - bilateral reduction | 447 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 0930 | 8107 |  |  | 7768 |  |  | -4555 | -4555 | -4221 | Critical Branch | TTC Validation phase - bilateral reduction | 339 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 1030 | 8107 |  |  | 7768 |  |  | -4555 | -4555 | -4221 | Critical Branch | TTC Validation phase - bilateral reduction | 339 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 1130 | 8107 |  |  | 7768 |  |  | -4555 | -4555 | -4221 | Critical Branch | TTC Validation phase - bilateral reduction | 339 | NA | 0 | [6 empty] | 3000 | Outage - CHAFFARD GRANDE ILE 1
20251017 | October | 2130 | 9511 |  |  | 9125 |  |  | -3256 | -3256 | -2870 | Critical Branch | Validation phase | 386 | NA | 0 |  |  |  |  | 8790 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251017 | October | 2230 | 9511 |  |  | 9125 |  |  | -3256 | -3256 | -2870 | Critical Branch | Validation phase | 386 | NA | 0 |  |  |  |  | 8790 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251017 | October | 2330 | 8901 |  |  | 8515 |  |  | -2633 | -2633 | -2247 | Critical Branch | Validation phase | 386 | NA | 0 |  |  |  |  | 8185 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251018 | October | 0030 | 9458 |  |  | 8912 |  |  | -2774 | -2774 | -2233 | Critical Branch | Validation phase | 546 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 0130 | 9458 |  |  | 8912 |  |  | -2774 | -2774 | -2233 | Critical Branch | Validation phase | 546 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 0230 | 9458 |  |  | 8912 |  |  | -2774 | -2774 | -2233 | Critical Branch | Validation phase | 546 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 0330 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 419 |  | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0430 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 419 |  | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0530 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 419 |  | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0630 | 8589 |  |  | 8588 |  |  | -5075 | -5075 | -5074 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 419 |  | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0730 | 8637 |  |  | 8637 |  |  | -4884 | -4884 | -4883 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 412 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0830 | 8637 |  |  | 8637 |  |  | -4884 | -4884 | -4883 | Critical Branch | Validation phase | 0 | NA | 0 |  |  | 412 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 0930 | 8197 |  |  | 8196 |  |  | -4400 | -4400 | -4399 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 394 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1030 | 8197 |  |  | 8196 |  |  | -4400 | -4400 | -4399 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 394 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1130 | 8197 |  |  | 8196 |  |  | -4400 | -4400 | -4399 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 394 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1230 | 8577 |  |  | 8577 |  |  | 3055 | 153 | 2902 | Minimum Margin | Validation phase | 0 | NA | 5651 |  |  | 410 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1330 | 8577 |  |  | 8577 |  |  | 3055 | 153 | 2902 | Minimum Margin | Validation phase | 0 | NA | 5651 |  |  | 410 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1430 | 8577 |  |  | 8577 |  |  | 3055 | 153 | 2902 | Minimum Margin | Validation phase | 0 | NA | 5651 |  |  | 410 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 1530 |  | 8845 | 780 |  | 8580 | 774 | -2449 | -2449 | 0 | Critical Branch | Validation phase | NA | 271 | 2449 |  |  | 450 | Reduction because NTC over thermal limit on border | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1630 |  | 8845 | 780 |  | 8580 | 774 | -2449 | -2449 | 0 | Critical Branch | Validation phase | NA | 271 | 2449 |  |  | 450 | Reduction because NTC over thermal limit on border | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1730 |  | 8845 | 780 |  | 8580 | 774 | -2449 | -2449 | 0 | Critical Branch | Validation phase | NA | 271 | 2449 |  |  | 450 | Reduction because NTC over thermal limit on border | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1830 |  | 8497 | 720 |  | 8452 | 720 | -3209 | -3209 | 0 | Critical Branch | Validation phase | NA | 45 | 3209 |  |  | 438 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 1930 |  | 8497 | 720 |  | 8452 | 720 | -3209 | -3209 | 0 | Critical Branch | Validation phase | NA | 45 | 3209 |  |  | 438 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 2030 |  | 8497 | 720 |  | 8452 | 720 | -3209 | -3209 | 0 | Critical Branch | Validation phase | NA | 45 | 3209 |  |  | 438 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - Busbar 2.1 GENISSIAT
20251018 | October | 2130 | 8403 |  |  | 8402 |  |  | -4539 | -4539 | -4538 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 402 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 2230 | 8403 |  |  | 8402 |  |  | -4539 | -4539 | -4538 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 402 |  | 9225 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251018 | October | 2330 | 7793 |  |  | 7792 |  |  | -3929 | -3929 | -3928 | Critical Branch | Validation phase | 1 | NA | 0 |  |  | 385 |  | 8620 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251019 | October | 0030 | 9011 |  |  | 8225 |  |  | -5652 | -5652 | -4866 | Critical Branch | Validation phase | 786 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7895 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0130 | 9011 |  |  | 8225 |  |  | -5652 | -5652 | -4866 | Critical Branch | Validation phase | 786 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7895 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0230 | 9011 |  |  | 8225 |  |  | -5652 | -5652 | -4866 | Critical Branch | Validation phase | 786 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7895 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0330 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 408
20251019 | October | 0430 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 408
20251019 | October | 0530 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 408
20251019 | October | 0630 | 8330 |  |  | 8329 |  |  | -4549 | -4549 | -4548 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 408
20251019 | October | 0730 | 8664 |  |  | 8387 |  |  | -4959 | -4959 | -4682 | Critical Branch | Validation phase | 277 | NA | 0 |  |  | 422 |  | 8057 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0830 | 8664 |  |  | 8387 |  |  | -4959 | -4959 | -4682 | Critical Branch | Validation phase | 277 | NA | 0 |  |  | 422 |  | 8057 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 0930 | 8285 |  |  | 7266 |  |  | -1769 | -1769 | -750 | Critical Branch | Validation phase | 1019 | NA | 0 |  |  | 406 |  | 6936 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251019 | October | 1030 | 8285 |  |  | 7266 |  |  | -1769 | -1769 | -750 | Critical Branch | Validation phase | 1019 | NA | 0 |  |  | 406 |  | 6936 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251019 | October | 1130 | 8285 |  |  | 7266 |  |  | -1769 | -1769 | -750 | Critical Branch | Validation phase | 1019 | NA | 0 |  |  | 406 |  | 6936 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251019 | October | 1230 | 6936 |  |  | 6935 |  |  | -2858 | -2858 | -2858 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 349
20251019 | October | 1330 | 6936 |  |  | 6935 |  |  | -2858 | -2858 | -2858 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 349
20251019 | October | 1430 | 6936 |  |  | 6935 |  |  | -2858 | -2858 | -2858 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 349
20251019 | October | 1530 |  | 8298 | 778 |  | 8003 | 752 | -1788 | -1788 | 0 | Critical Branch | Validation phase | NA | 321 | 1788 |  |  | 425 |  | 8249 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 1630 |  | 8298 | 778 |  | 8003 | 752 | -1788 | -1788 | 0 | Critical Branch | Validation phase | NA | 321 | 1788 |  |  | 435 | Reduction because NTC over thermal limit on border | 8249 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 1730 |  | 8298 | 778 |  | 8003 | 752 | -1788 | -1788 | 0 | Critical Branch | Validation phase | NA | 321 | 1788 |  |  | 435 | Reduction because NTC over thermal limit on border | 8249 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251019 | October | 1830 |  | 8445 | 767 |  | 8246 | 755 | -3088 | -3088 | 0 | Critical Branch | Validation phase | NA | 211 | 3088 |  |  | 435 | Reduction because NTC over thermal limit on border | 8468 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 4100 | Outage - Busbar 2.1 GENISSIAT
20251019 | October | 1930 |  | 8445 | 767 |  | 8246 | 755 | -3088 | -3088 | 0 | Critical Branch | Validation phase | NA | 211 | 3088 |  |  | 435 | Reduction because NTC over thermal limit on border | 8468 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 4100 | Outage - Busbar 2.1 GENISSIAT
20251019 | October | 2030 |  | 8445 | 767 |  | 8246 | 755 | -3088 | -3088 | 0 | Critical Branch | Validation phase | NA | 211 | 3088 |  |  | 435 | Reduction because NTC over thermal limit on border | 8468 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | 4100 | Outage - Busbar 2.1 GENISSIAT
20251019 | October | 2130 | 8023 |  |  | 8022 |  |  | -4491 | -4491 | -4490 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 395
20251019 | October | 2230 | 8023 |  |  | 8022 |  |  | -4491 | -4491 | -4490 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 395
20251019 | October | 2330 | 8023 |  |  | 8022 |  |  | -4491 | -4491 | -4490 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 395
20251020 | October | 0730 |  | 8034 | 685 |  | 7613 | 651 | -2778 | -2778 | 0 | Critical Branch | Validation phase | NA | 455 | 2778 |  |  |  |  | 7891 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251020 | October | 0830 |  | 8034 | 685 |  | 7613 | 651 | -2778 | -2778 | 0 | Critical Branch | Validation phase | NA | 455 | 2778 |  |  |  |  | 7891 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251020 | October | 1130 | 7698 |  |  | 7698 |  |  | -3552 | -3552 | -3552 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 7363 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1230 | 8250 |  |  | 7801 |  |  | -4127 | -4127 | -3678 | Critical Branch | Validation phase | 449 | NA | 0 |  |  |  |  | 7466 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1330 | 8250 |  |  | 7801 |  |  | -4127 | -4127 | -3678 | Critical Branch | Validation phase | 449 | NA | 0 |  |  |  |  | 7466 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1430 | 8250 |  |  | 7801 |  |  | -4127 | -4127 | -3678 | Critical Branch | Validation phase | 449 | NA | 0 |  |  |  |  | 7466 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1530 |  | 8157 | 690 |  | 7759 | 658 | -2479 | -2479 | 0 | Critical Branch | Validation phase | NA | 430 | 2479 |  |  |  |  | 8197 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1630 |  | 8157 | 690 |  | 7759 | 658 | -2479 | -2479 | 0 | Critical Branch | Validation phase | NA | 430 | 2479 |  |  |  |  | 8197 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 1730 |  | 8157 | 690 |  | 7759 | 658 | -2479 | -2479 | 0 | Critical Branch | Validation phase | NA | 430 | 2479 |  |  |  |  | 8197 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 2130 | 8514 |  |  | 7801 |  |  | -2429 | -2429 | -1716 | Critical Branch | Validation phase | 713 | NA | 0 |  |  |  |  | 7466 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 2230 | 8514 |  |  | 7801 |  |  | -2429 | -2429 | -1716 | Critical Branch | Validation phase | 713 | NA | 0 |  |  |  |  | 7466 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251020 | October | 2330 | 7904 |  |  | 7801 |  |  | -1806 | -1806 | -1703 | Critical Branch | Validation phase | 103 | NA | 0 |  |  |  |  | 7471 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251021 | October | 0030 | 7643 |  |  | 6760 |  |  | -3823 | -3823 | -2940 | Critical Branch | Validation phase | 883 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0130 | 7643 |  |  | 6760 |  |  | -3823 | -3823 | -2940 | Critical Branch | Validation phase | 883 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0230 | 7643 |  |  | 6760 |  |  | -3823 | -3823 | -2940 | Critical Branch | Validation phase | 883 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0330 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 462 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0430 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 462 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0530 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 462 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0630 | 7222 |  |  | 6760 |  |  | -3147 | -3147 | -2685 | Critical Branch | Validation phase | 462 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0730 |  | 7734 | 675 |  | 6891 | 675 | -2534 | -2534 | 0 | Critical Branch | Validation phase | NA | 843 | 2534 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0830 |  | 7734 | 675 |  | 6891 | 675 | -2534 | -2534 | 0 | Critical Branch | Validation phase | NA | 843 | 2534 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 0930 | 8357 |  |  | 7248 |  |  | -2167 | -2167 | -1058 | Critical Branch | Validation phase | 1109 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1030 | 8357 |  |  | 7248 |  |  | -2167 | -2167 | -1058 | Critical Branch | Validation phase | 1109 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1130 | 8357 |  |  | 7248 |  |  | -2167 | -2167 | -1058 | Critical Branch | Validation phase | 1109 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1230 | 8550 |  |  | 7248 |  |  | -2173 | -2173 | -871 | Critical Branch | Validation phase | 1302 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1330 | 8550 |  |  | 7248 |  |  | -2173 | -2173 | -871 | Critical Branch | Validation phase | 1302 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1430 | 8550 |  |  | 7248 |  |  | -2173 | -2173 | -871 | Critical Branch | Validation phase | 1302 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1530 | 8512 |  |  | 7248 |  |  | -2428 | -2428 | -1164 | Critical Branch | Validation phase | 1264 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1630 | 8512 |  |  | 7248 |  |  | -2428 | -2428 | -1164 | Critical Branch | Validation phase | 1264 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1730 | 8512 |  |  | 7248 |  |  | -2428 | -2428 | -1164 | Critical Branch | Validation phase | 1264 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1830 |  | 7896 | 649 |  | 6884 | 649 | -2730 | -2730 | 0 | Critical Branch | Validation phase | NA | 1012 | 2730 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 1930 |  | 7896 | 649 |  | 6884 | 649 | -2730 | -2730 | 0 | Critical Branch | Validation phase | NA | 1012 | 2730 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2030 |  | 7896 | 649 |  | 6884 | 649 | -2730 | -2730 | 0 | Critical Branch | Validation phase | NA | 1012 | 2730 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2130 | 8388 |  |  | 7248 |  |  | -2345 | -2345 | -1205 | Critical Branch | Validation phase | 1140 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2230 | 8388 |  |  | 7248 |  |  | -2345 | -2345 | -1205 | Critical Branch | Validation phase | 1140 | NA | 0 |  |  |  |  | 6913 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251021 | October | 2330 | 7778 |  |  | 6760 |  |  | -1719 | -1719 | -701 | Critical Branch | Validation phase | 1018 | NA | 0 |  |  |  |  | 6430 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251022 | October | 0030 | 9347 |  |  | 6730 |  |  | -5159 | -5159 | -2542 | Critical Branch | Validation phase | 2617 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0130 | 9347 |  |  | 6730 |  |  | -5159 | -5159 | -2542 | Critical Branch | Validation phase | 2617 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0230 | 9347 |  |  | 6730 |  |  | -5159 | -5159 | -2542 | Critical Branch | Validation phase | 2617 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0330 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 2240 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0430 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 2240 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0530 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 2240 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0630 | 8970 |  |  | 6730 |  |  | -4706 | -4706 | -2466 | Critical Branch | Validation phase | 2240 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0730 |  | 9437 | 800 | 7100 |  |  | -3724 | -3724 | -809 | Critical Branch | Validation phase | NA | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0830 |  | 9437 | 800 | 7100 |  |  | -3724 | -3724 | -809 | Critical Branch | Validation phase | NA | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 0930 | 9561 |  |  | 7100 |  |  | -3407 | -3407 | -946 | Critical Branch | Validation phase | 2461 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1030 | 9561 |  |  | 7100 |  |  | -3407 | -3407 | -946 | Critical Branch | Validation phase | 2461 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1130 | 9561 |  |  | 7100 |  |  | -3407 | -3407 | -946 | Critical Branch | Validation phase | 2461 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1230 | 8099 |  |  | 7100 |  |  | -3737 | -3737 | -2738 | Critical Branch | Validation phase | 999 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1330 | 8099 |  |  | 7100 |  |  | -3737 | -3737 | -2738 | Critical Branch | Validation phase | 999 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1430 | 8099 |  |  | 7100 |  |  | -3737 | -3737 | -2738 | Critical Branch | Validation phase | 999 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1530 |  | 8950 | 760 | 7100 |  |  | -3725 | -3725 | -1209 | Critical Branch | Validation phase | NA | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1630 |  | 8950 | 760 | 7100 |  |  | -3725 | -3725 | -1209 | Critical Branch | Validation phase | NA | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1730 |  | 8950 | 760 | 7100 |  |  | -3725 | -3725 | -1209 | Critical Branch | Validation phase | NA | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1830 |  | 9374 | 775 | 7100 |  |  | -2662 | -2662 | 365 | Critical Branch | Validation phase | NA | NA | 3392 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 1930 |  | 9374 | 775 | 7100 |  |  | -2662 | -2662 | 365 | Critical Branch | Validation phase | NA | NA | 3392 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2030 |  | 9374 | 775 | 7100 |  |  | -2662 | -2662 | 365 | Critical Branch | Validation phase | NA | NA | 3392 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2130 | 9453 |  |  | 7100 |  |  | -5128 | -5128 | -2775 | Critical Branch | Validation phase | 2353 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2230 | 9453 |  |  | 7100 |  |  | -5128 | -5128 | -2775 | Critical Branch | Validation phase | 2353 | NA | 0 |  |  |  |  | 6765 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251022 | October | 2330 | 8843 |  |  | 6730 |  |  | -4520 | -4520 | -2407 | Critical Branch | Validation phase | 2113 | NA | 0 |  |  |  |  | 6400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4100 | Outage - RO S2.1 GENISSIAT 400
20251023 | October | 0330 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 951 | NA | 0 |  |  |  |  | 7691 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0430 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 951 | NA | 0 |  |  |  |  | 7691 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0530 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 951 | NA | 0 |  |  |  |  | 7691 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0630 | 8892 |  |  | 7941 |  |  | -2887 | -2887 | -1936 | Critical Branch | Validation phase | 951 | NA | 0 |  |  |  |  | 7691 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0730 |  | 9189 | 655 |  | 8478 | 605 | -4041 | -4041 | 0 | Critical Branch | Validation phase | NA | 761 | 4041 |  |  |  |  | 8944 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0830 |  | 9189 | 655 |  | 8478 | 605 | -4041 | -4041 | 0 | Critical Branch | Validation phase | NA | 761 | 4041 |  |  |  |  | 8944 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 0930 | 9200 |  |  | 8535 |  |  | -3221 | -3221 | -2556 | Critical Branch | Validation phase | 665 | NA | 0 |  |  |  |  | 8285 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1030 | 9200 |  |  | 8535 |  |  | -3221 | -3221 | -2556 | Critical Branch | Validation phase | 665 | NA | 0 |  |  |  |  | 8285 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1130 | 9200 |  |  | 8535 |  |  | -3221 | -3221 | -2556 | Critical Branch | Validation phase | 665 | NA | 0 |  |  |  |  | 8285 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1230 | 8809 |  |  | 8102 |  |  | -4564 | -4564 | -3857 | Critical Branch | Validation phase | 707 | NA | 0 |  |  |  |  | 7852 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1330 | 8809 |  |  | 8102 |  |  | -4564 | -4564 | -3857 | Critical Branch | Validation phase | 707 | NA | 0 |  |  |  |  | 7852 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1430 | 8809 |  |  | 8102 |  |  | -4564 | -4564 | -3857 | Critical Branch | Validation phase | 707 | NA | 0 |  |  |  |  | 7852 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1530 |  | 9196 | 708 |  | 8290 | 644 | -3468 | -3468 | 0 | Critical Branch | Validation phase | NA | 970 | 3468 |  |  |  |  | 9323 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1630 |  | 9196 | 708 |  | 8290 | 644 | -3468 | -3468 | 0 | Critical Branch | Validation phase | NA | 970 | 3468 |  |  |  |  | 9323 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1730 |  | 9196 | 708 |  | 8290 | 644 | -3468 | -3468 | 0 | Critical Branch | Validation phase | NA | 970 | 3468 |  |  |  |  | 9323 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1830 |  | 9019 | 682 |  | 8290 | 630 | -3613 | -3613 | 0 | Critical Branch | Validation phase | NA | 781 | 3613 |  |  |  |  | 9139 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 1930 |  | 9019 | 682 |  | 8290 | 630 | -3613 | -3613 | 0 | Critical Branch | Validation phase | NA | 781 | 3613 |  |  |  |  | 9139 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2030 |  | 9019 | 682 |  | 8290 | 630 | -3613 | -3613 | 0 | Critical Branch | Validation phase | NA | 781 | 3613 |  |  |  |  | 9139 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2130 | 9261 |  |  | 8327 |  |  | -2808 | -2808 | -1874 | Critical Branch | Validation phase | 934 | NA | 0 |  |  |  |  | 8077 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2230 | 9261 |  |  | 8327 |  |  | -2808 | -2808 | -1874 | Critical Branch | Validation phase | 934 | NA | 0 |  |  |  |  | 8077 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251023 | October | 2330 | 8451 |  |  | 7517 |  |  | -1986 | -1986 | -1052 | Critical Branch | Validation phase | 934 | NA | 0 |  |  |  |  | 7267 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251024 | October | 0930 | 8430 |  |  | 8143 |  |  | -2516 | -2516 | -2229 | Critical Branch | Validation phase | 287 | NA | 0 |  |  |  |  | 7893 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1030 | 8430 |  |  | 8143 |  |  | -2516 | -2516 | -2229 | Critical Branch | Validation phase | 287 | NA | 0 |  |  |  |  | 7893 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1130 | 8430 |  |  | 8143 |  |  | -2516 | -2516 | -2229 | Critical Branch | Validation phase | 287 | NA | 0 |  |  |  |  | 7893 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1230 | 8726 |  |  | 8143 |  |  | -2524 | -2524 | -1941 | Critical Branch | Validation phase | 583 | NA | 0 |  |  |  |  | 7893 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1330 | 8726 |  |  | 8143 |  |  | -2524 | -2524 | -1941 | Critical Branch | Validation phase | 583 | NA | 0 |  |  |  |  | 7893 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1430 | 8726 |  |  | 8143 |  |  | -2524 | -2524 | -1941 | Critical Branch | Validation phase | 583 | NA | 0 |  |  |  |  | 7893 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 1530 |  | 8384 | 740 |  | 8316 | 740 | 2598 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 68 | -129 | [6 empty] | 4050 | Process fail during TSO validation phase
20251024 | October | 1630 |  | 8384 | 740 |  | 8316 | 740 | 2598 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 68 | -129 | [6 empty] | 4050 | Process fail during TSO validation phase
20251024 | October | 1730 |  | 8384 | 740 |  | 8316 | 740 | 2598 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 68 | -129 | [6 empty] | 4050 | Process fail during TSO validation phase
20251024 | October | 2130 | 8995 |  |  | 8546 |  |  | -2349 | -2349 | -1900 | Critical Branch | Validation phase | 449 | NA | 0 |  |  |  |  | 8296 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 2230 | 8995 |  |  | 8546 |  |  | -2349 | -2349 | -1900 | Critical Branch | Validation phase | 449 | NA | 0 |  |  |  |  | 8296 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251024 | October | 2330 | 8385 |  |  | 7936 |  |  | -1739 | -1739 | -1290 | Critical Branch | Validation phase | 449 | NA | 0 |  |  |  |  | 7686 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251025 | October | 0030 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0130 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0230 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0330 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0430 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0530 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0630 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0730 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0830 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 0930 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1030 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1130 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1230 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1330 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1430 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1530 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1630 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1730 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1830 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 1930 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 2030 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 2130 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 2230 | 9560 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1860 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251025 | October | 2330 | 8950 |  |  | 7700 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1250 | NA | 0 |  |  |  |  | 7450 | manual values cause of to high BackUP values
20251026 | October | 0030 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 423
20251026 | October | 0130 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 423
20251026 | October | 0230 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 423
20251026 | October | 0230 | 8720 |  |  | 8720 |  |  | -1669 | -1669 | -1669 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 423
20251026 | October | 0330 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251026 | October | 0430 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251026 | October | 0530 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251026 | October | 0630 | 8875 |  |  | 8875 |  |  | -2141 | -2141 | -2141 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251026 | October | 0730 | 8090 |  |  | 8089 |  |  | -4004 | -4004 | -4003 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 390
20251026 | October | 0830 | 8090 |  |  | 8089 |  |  | -4004 | -4004 | -4003 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 390
20251026 | October | 0930 | 8098 |  |  | 8098 |  |  | -4413 | -4413 | -4413 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20251026 | October | 1030 | 8098 |  |  | 8098 |  |  | -4413 | -4413 | -4413 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20251026 | October | 1130 | 8098 |  |  | 8098 |  |  | -4413 | -4413 | -4413 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20251026 | October | 1230 | 8423 |  |  | 8422 |  |  | -1603 | -1603 | -1602 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 407
20251026 | October | 1330 | 8423 |  |  | 8422 |  |  | -1603 | -1603 | -1602 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 407
20251026 | October | 1430 | 8423 |  |  | 8422 |  |  | -1603 | -1603 | -1602 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 407
20251026 | October | 1530 |  | 8311 | 958 |  | 8311 | 949 | -2825 | -2825 | 0 | Critical Branch | Critical Branch | NA | 9 | 2825 |  |  | 271 | Reduction because NTC over thermal limit on border
20251026 | October | 1630 |  | 8311 | 958 |  | 8311 | 949 | -2825 | -2825 | 0 | Critical Branch | Critical Branch | NA | 9 | 2825 |  |  | 271 | Reduction because NTC over thermal limit on border
20251026 | October | 1730 |  | 8311 | 958 |  | 8311 | 949 | -2825 | -2825 | 0 | Critical Branch | Critical Branch | NA | 9 | 2825 |  |  | 271 | Reduction because NTC over thermal limit on border
20251026 | October | 1830 | 9076 |  |  | 9070 |  |  | -2420 | -2420 | -2414 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251026 | October | 1930 | 9076 |  |  | 9070 |  |  | -2420 | -2420 | -2414 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251026 | October | 2030 | 9076 |  |  | 9070 |  |  | -2420 | -2420 | -2414 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251026 | October | 2130 | 8678 |  |  | 8677 |  |  | -1655 | -1655 | -1654 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 420
20251026 | October | 2230 | 8678 |  |  | 8677 |  |  | -1655 | -1655 | -1654 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 420
20251026 | October | 2330 | 8678 |  |  | 8677 |  |  | -1655 | -1655 | -1654 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 420
20251027 | October | 0030 | 7900 |  |  | 7899 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251027 | October | 0130 | 7900 |  |  | 7899 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251027 | October | 0230 | 7900 |  |  | 7899 |  |  | -1169 | -1169 | -1168 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251027 | October | 0330 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20251027 | October | 0430 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20251027 | October | 0530 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20251027 | October | 0630 | 7824 |  |  | 7824 |  |  | -1309 | -1309 | -1309 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 377
20251027 | October | 0730 | 9047 |  |  | 9047 |  |  | -3235 | -3235 | -3235 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 434
20251027 | October | 0830 | 9047 |  |  | 9047 |  |  | -3235 | -3235 | -3235 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 434
20251027 | October | 0930 | 8990 |  |  | 8990 |  |  | -2287 | -2287 | -2287 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251027 | October | 1030 | 8990 |  |  | 8990 |  |  | -2287 | -2287 | -2287 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251027 | October | 1130 | 8990 |  |  | 8990 |  |  | -2287 | -2287 | -2287 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251027 | October | 1230 | 8435 |  |  | 8435 |  |  | -5107 | -5107 | -5107 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 403
20251027 | October | 1330 | 8435 |  |  | 8435 |  |  | -5107 | -5107 | -5107 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 403
20251027 | October | 1430 | 8435 |  |  | 8435 |  |  | -5107 | -5107 | -5107 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 403
20251027 | October | 1530 |  | 8005 | 741 |  | 8004 | 741 | -1947 | -1947 | 0 | Critical Branch | Critical Branch | NA | 1 | 1947 |  |  | 418
20251027 | October | 1630 |  | 8005 | 741 |  | 8004 | 741 | -1947 | -1947 | 0 | Critical Branch | Critical Branch | NA | 1 | 1947 |  |  | 418
20251027 | October | 1730 |  | 8005 | 741 |  | 8004 | 741 | -1947 | -1947 | 0 | Critical Branch | Critical Branch | NA | 1 | 1947 |  |  | 418
20251027 | October | 1830 |  | 8918 | 832 |  | 8898 | 832 | -3308 | -3308 | 0 | Critical Branch | Critical Branch | NA | 20 | 3308 |  |  | 450 | Reduction because NTC over thermal limit on border
20251027 | October | 1930 |  | 8918 | 832 |  | 8898 | 832 | -3308 | -3308 | 0 | Critical Branch | Critical Branch | NA | 20 | 3308 |  |  | 450 | Reduction because NTC over thermal limit on border
20251027 | October | 2030 |  | 8918 | 832 |  | 8584 | 832 | -3308 | -3308 | 0 | Critical Branch | Critical Branch | NA | 334 | 3308 |  |  | 450 | Reduction because NTC over thermal limit on border
20251027 | October | 2130 | 7489 |  |  | 7488 |  |  | -3692 | -3692 | -3691 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 354
20251027 | October | 2230 | 7489 |  |  | 7488 |  |  | -3692 | -3692 | -3691 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 354
20251027 | October | 2330 | 6879 |  |  | 6879 |  |  | -3085 | -3085 | -3085 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 336
20251029 | October | 1130 | 9257 |  |  | 8886 |  |  | -1780 | -1780 | -1409 | Critical Branch | Smoothing ramp | 371 | NA | 0 | Smoothing | Smoothing ramp
20251030 | October | 0030 | 9842 |  |  | 9838 |  |  | -3172 | -3172 | -3169 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251030 | October | 0130 | 9842 |  |  | 9838 |  |  | -3172 | -3172 | -3169 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251030 | October | 0230 | 9842 |  |  | 9838 |  |  | -3172 | -3172 | -3169 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251030 | October | 0330 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 406
20251030 | October | 0430 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 406
20251030 | October | 0530 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 406
20251030 | October | 0630 | 9135 |  |  | 9135 |  |  | -5249 | -5249 | -5249 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 406
20251030 | October | 0730 | 9681 |  |  | 9680 |  |  | -2572 | -2572 | -2571 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 410
20251030 | October | 0830 | 8281 |  |  | 8281 |  |  | -1038 | -1038 | -1037 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 404
20251030 | October | 0930 | 7958 |  |  | 7957 |  |  | -4064 | -4064 | -4064 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20251030 | October | 1030 | 7958 |  |  | 7957 |  |  | -4064 | -4064 | -4064 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20251030 | October | 1130 | 7958 |  |  | 7957 |  |  | -4064 | -4064 | -4064 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20251030 | October | 1230 | 7108 |  |  | 7108 |  |  | 4033 | 118 | 3915 | Minimum Margin | Minimum Margin | 0 | NA | 7712 |  |  | 343
20251030 | October | 1330 | 7108 |  |  | 7108 |  |  | 4033 | 118 | 3915 | Minimum Margin | Minimum Margin | 0 | NA | 7712 |  |  | 343
20251030 | October | 1430 | 7108 |  |  | 7108 |  |  | 4033 | 118 | 3915 | Minimum Margin | Minimum Margin | 0 | NA | 7712 |  |  | 343
20251030 | October | 1530 | 8512 |  |  | 8512 |  |  | -414 | -414 | -414 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 416
20251030 | October | 1630 | 8512 |  |  | 8512 |  |  | -414 | -414 | -414 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 416
20251030 | October | 1730 | 8512 |  |  | 8512 |  |  | -414 | -414 | -414 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 416
20251030 | October | 1830 | 8302 |  |  | 8302 |  |  | -2771 | -2771 | -2770 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 405
20251030 | October | 1930 | 8302 |  |  | 8302 |  |  | -2771 | -2771 | -2770 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 405
20251030 | October | 2030 | 8302 |  |  | 8302 |  |  | -2771 | -2771 | -2770 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 405
20251030 | October | 2130 | 8339 |  |  | 8339 |  |  | -1950 | -1950 | -1950 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 407
20251030 | October | 2230 | 8339 |  |  | 8339 |  |  | -1950 | -1950 | -1950 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 407
20251030 | October | 2330 | 7729 |  |  | 7728 |  |  | -1313 | -1313 | -1313 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 390
20251031 | October | 0030 | 7894 |  |  | 7893 |  |  | -4095 | -4095 | -4094 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 399
20251031 | October | 0130 | 7894 |  |  | 7893 |  |  | -4095 | -4095 | -4094 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 399
20251031 | October | 0230 | 7894 |  |  | 7893 |  |  | -4095 | -4095 | -4094 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 399
20251031 | October | 0330 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 120 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8551 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0430 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 120 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8551 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0530 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 120 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8551 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0630 | 8907 |  |  | 8787 |  |  | -1916 | -1916 | -1797 | Critical Branch | Validation phase | 120 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8551 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251031 | October | 0730 | 9175 |  |  | 8982 |  |  | -2490 | -2490 | -2297 | Critical Branch | Critical Branch | 193 | NA | 0 |  |  | 450
20251031 | October | 0830 | 9175 |  |  | 7482 |  |  | -2490 | -2490 | -949 | Critical Branch | TTC Validation phase - bilateral reduction | 1693 | NA | 0 |  |  | 450 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 0930 | 8463 |  |  | 7122 |  |  | -1323 | -1323 | -172 | Critical Branch | TTC Validation phase - bilateral reduction | 1341 | NA | 0 |  |  | 413 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 1030 | 8463 |  |  | 7122 |  |  | -1323 | -1323 | -172 | Critical Branch | TTC Validation phase - bilateral reduction | 1341 | NA | 0 |  |  | 413 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 1130 | 8463 |  |  | 7122 |  |  | -1323 | -1323 | -172 | Critical Branch | TTC Validation phase - bilateral reduction | 1341 | NA | 0 |  |  | 413 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 1230 | 8839 |  |  | 7313 |  |  | -1950 | -1950 | -605 | Critical Branch | TTC Validation phase - bilateral reduction | 1526 | NA | 0 |  |  | 433 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 1330 | 8839 |  |  | 7313 |  |  | -1950 | -1950 | -605 | Critical Branch | TTC Validation phase - bilateral reduction | 1526 | NA | 0 |  |  | 433 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 1430 | 8839 |  |  | 7313 |  |  | -1950 | -1950 | -605 | Critical Branch | TTC Validation phase - bilateral reduction | 1526 | NA | 0 |  |  | 433 | [5 empty] | 3600 | forecasted security violation
20251031 | October | 1530 | 9227 |  |  | 7305 |  |  | -2438 | -2438 | -820 | Critical Branch | TTC Validation phase - bilateral reduction | 1922 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3300 | forecasted security violation
20251031 | October | 1630 | 9227 |  |  | 7305 |  |  | -2438 | -2438 | -820 | Critical Branch | TTC Validation phase - bilateral reduction | 1922 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3300 | forecasted security violation
20251031 | October | 1730 | 9227 |  |  | 6909 |  |  | -2438 | -2438 | -396 | Critical Branch | TTC Validation phase - bilateral reduction | 2318 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3000 | forecasted security violation
20251031 | October | 1830 | 8406 |  |  | 6297 |  |  | -1198 | -1198 | 642 | Critical Branch | TTC Validation phase - bilateral reduction | 2109 | NA | 2482 |  |  | 410 | [5 empty] | 2700 | forecasted security violation
20251031 | October | 1930 | 8406 |  |  | 6297 |  |  | -1198 | -1198 | 642 | Critical Branch | TTC Validation phase - bilateral reduction | 2109 | NA | 2482 |  |  | 410 | [5 empty] | 2700 | forecasted security violation
20251031 | October | 2030 | 8406 |  |  | 6297 |  |  | -1198 | -1198 | 642 | Critical Branch | TTC Validation phase - bilateral reduction | 2109 | NA | 2482 |  |  | 410 | [5 empty] | 2700 | forecasted security violation
20251031 | October | 2130 | 9117 |  |  | 6396 |  |  | -2062 | -2062 | 467 | Critical Branch | TTC Validation phase - bilateral reduction | 2721 | NA | 2996 |  |  | 447 | [5 empty] | 2700 | forecasted security violation
20251031 | October | 2230 | 9117 |  |  | 6896 |  |  | -2062 | -2062 | -84 | Critical Branch | TTC Validation phase - bilateral reduction | 2221 | NA | 0 |  |  | 447 | [5 empty] | 3000 | forecasted security violation
20251031 | October | 2330 | 8507 |  |  | 6790 |  |  | -1423 | -1423 | 64 | Critical Branch | TTC Validation phase - bilateral reduction | 1717 | NA | 1551 |  |  | 432 | [5 empty] | 3500 | forecasted security violation
20251101 | November | 0030 | 7679 |  |  | 7678 |  |  | -4645 | -4645 | -4644 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20251101 | November | 0130 | 7679 |  |  | 7678 |  |  | -4645 | -4645 | -4644 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20251101 | November | 0230 | 7679 |  |  | 7678 |  |  | -4645 | -4645 | -4644 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 387
20251101 | November | 0330 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251101 | November | 0430 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251101 | November | 0530 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251101 | November | 0630 | 8933 |  |  | 8912 |  |  | -2030 | -2030 | -2011 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251101 | November | 0730 | 8025 |  |  | 8024 |  |  | -4699 | -4699 | -4698 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 406
20251101 | November | 0830 | 8025 |  |  | 8024 |  |  | -4699 | -4699 | -4698 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 406
20251101 | November | 0930 | 7951 |  |  | 7950 |  |  | -633 | -633 | -632 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 402
20251101 | November | 1030 | 7951 |  |  | 7950 |  |  | -633 | -633 | -632 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 402
20251101 | November | 1130 | 7951 |  |  | 7950 |  |  | -633 | -633 | -632 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 402
20251101 | November | 1230 | 8272 |  |  | 8271 |  |  | -1580 | -1580 | -1579 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 419
20251101 | November | 1330 | 8272 |  |  | 8271 |  |  | -1580 | -1580 | -1579 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 419
20251101 | November | 1430 | 8272 |  |  | 8271 |  |  | -1580 | -1580 | -1579 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 419
20251101 | November | 1530 | 7446 |  |  | 7446 |  |  | -4287 | -4287 | -4287 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 375
20251101 | November | 1630 | 7446 |  |  | 7446 |  |  | -4287 | -4287 | -4287 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 375
20251101 | November | 1730 | 7446 |  |  | 7446 |  |  | -4287 | -4287 | -4287 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 375
20251101 | November | 1830 | 8865 |  |  | 7501 |  |  | -1830 | -1830 | -425 | Critical Branch | TTC Validation phase - bilateral reduction | 1364 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2400 | forecasted security violation
20251101 | November | 1930 | 8865 |  |  | 7501 |  |  | -1830 | -1830 | -425 | Critical Branch | TTC Validation phase - bilateral reduction | 1364 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2400 | forecasted security violation
20251101 | November | 2030 | 8865 |  |  | 7501 |  |  | -1830 | -1830 | -425 | Critical Branch | TTC Validation phase - bilateral reduction | 1364 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2400 | forecasted security violation
20251101 | November | 2130 | 9115 |  |  | 7521 |  |  | -1907 | -1907 | -274 | Critical Branch | TTC Validation phase - bilateral reduction | 1594 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2400 | forecasted security violation
20251101 | November | 2230 | 9115 |  |  | 7521 |  |  | -1907 | -1907 | -274 | Critical Branch | TTC Validation phase - bilateral reduction | 1594 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2400 | forecasted security violation
20251101 | November | 2330 | 9115 |  |  | 8021 |  |  | -1907 | -1907 | -786 | Critical Branch | TTC Validation phase - bilateral reduction | 1094 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2600 | forecasted security violation
20251102 | November | 0030 | 9073 |  |  | 7179 |  |  | -2119 | -2119 | -225 | Critical Branch | Validation phase | 1894 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6929 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0130 | 9073 |  |  | 7179 |  |  | -2119 | -2119 | -225 | Critical Branch | Validation phase | 1894 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6929 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0230 | 9073 |  |  | 7179 |  |  | -2119 | -2119 | -225 | Critical Branch | Validation phase | 1894 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6929 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0330 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 1065 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0430 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 1065 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0530 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 1065 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0630 | 9115 |  |  | 8050 |  |  | -2004 | -2004 | -939 | Critical Branch | Validation phase | 1065 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0730 | 7669 |  |  | 7525 |  |  | -4190 | -4190 | -4046 | Critical Branch | Validation phase | 144 | NA | 0 |  |  | 397 |  | 7275 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0830 | 7669 |  |  | 7525 |  |  | -4190 | -4190 | -4046 | Critical Branch | Validation phase | 144 | NA | 0 |  |  | 397 |  | 7275 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 0930 | 9063 |  |  | 7451 |  |  | -1765 | -1765 | -153 | Critical Branch | Validation phase | 1612 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7201 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1030 | 9063 |  |  | 7451 |  |  | -1765 | -1765 | -153 | Critical Branch | Validation phase | 1612 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7201 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1130 | 9063 |  |  | 7451 |  |  | -1765 | -1765 | -153 | Critical Branch | Validation phase | 1612 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7201 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1230 | 8920 |  |  | 7772 |  |  | -2033 | -2033 | -885 | Critical Branch | Validation phase | 1148 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7522 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1330 | 8920 |  |  | 7772 |  |  | -2033 | -2033 | -885 | Critical Branch | Validation phase | 1148 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7522 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1430 | 8920 |  |  | 7772 |  |  | -2033 | -2033 | -885 | Critical Branch | Validation phase | 1148 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7522 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1530 | 7969 |  |  | 6946 |  |  | -4507 | -4507 | -3484 | Critical Branch | Validation phase | 1023 | NA | 0 |  |  | 413 |  | 6696 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20251102 | November | 1630 | 7969 |  |  | 6946 |  |  | -4507 | -4507 | -3484 | Critical Branch | Validation phase | 1023 | NA | 0 |  |  | 413 |  | 6696 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2500 | forecasted security violation
20251102 | November | 1730 | 7969 |  |  | 6946 |  |  | -4507 | -4507 | -3484 | Critical Branch | Validation phase | 1023 | NA | 0 |  |  | 413 |  | 6696 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251102 | November | 1830 | 8211 |  |  | 7307 |  |  | -4647 | -4647 | -3745 | Critical Branch | Validation phase | 904 | NA | 0 |  |  | 427 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251102 | November | 1930 | 8211 |  |  | 7307 |  |  | -4647 | -4647 | -3745 | Critical Branch | Validation phase | 904 | NA | 0 |  |  | 427 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251102 | November | 2030 | 8211 |  |  | 7307 |  |  | -4647 | -4647 | -3745 | Critical Branch | Validation phase | 904 | NA | 0 |  |  | 427 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251102 | November | 2130 | 8525 |  |  | 7307 |  |  | -5497 | -5497 | -4281 | Critical Branch | Validation phase | 1218 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251102 | November | 2230 | 8525 |  |  | 7307 |  |  | -5497 | -5497 | -4281 | Critical Branch | Validation phase | 1218 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251102 | November | 2330 | 8725 |  |  | 7809 |  |  | -5703 | -5703 | -4776 | Critical Branch | Validation phase | 916 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 7800 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2500 | forecasted security violation
20251103 | November | 0030 | 7844 |  |  | 7115 |  |  | -3118 | -3118 | -2376 | Critical Branch | Validation phase | 729 | NA | 0 |  |  | 396 |  | 7094 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0130 | 7844 |  |  | 7115 |  |  | -3118 | -3118 | -2376 | Critical Branch | Validation phase | 729 | NA | 0 |  |  | 396 |  | 7094 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0230 | 7844 |  |  | 7115 |  |  | -3118 | -3118 | -2376 | Critical Branch | Validation phase | 729 | NA | 0 |  |  | 396 |  | 7094 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0330 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 500 | NA | 0 |  |  | 374 |  | 6682 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0430 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 500 | NA | 0 |  |  | 374 |  | 6682 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0530 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 500 | NA | 0 |  |  | 374 |  | 6682 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0630 | 7432 |  |  | 6932 |  |  | -2771 | -2771 | -2271 | Critical Branch | Validation phase | 500 | NA | 0 |  |  | 374 |  | 6682 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251103 | November | 0730 | 8523 |  |  | 7176 |  |  | -3779 | -3779 | -2405 | Critical Branch | Validation phase | 1347 | NA | 0 |  |  | 416 |  | 7275 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2400 | forecasted security violation
20251103 | November | 0830 | 8523 |  |  | 7525 |  |  | -3779 | -3779 | -2781 | Critical Branch | Validation phase | 998 | NA | 0 |  |  | 416 |  | 7275 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 0930 | 8222 |  |  | 7451 |  |  | -3618 | -3618 | -2847 | Critical Branch | Validation phase | 771 | NA | 0 |  |  | 401 |  | 7201 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 1030 | 8222 |  |  | 7451 |  |  | -3618 | -3618 | -2847 | Critical Branch | Validation phase | 771 | NA | 0 |  |  | 401 |  | 7201 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 1130 | 8222 |  |  | 7451 |  |  | -3618 | -3618 | -2847 | Critical Branch | Validation phase | 771 | NA | 0 |  |  | 401 |  | 7201 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 1230 | 8884 |  |  | 7610 |  |  | -2192 | -2192 | -916 | Critical Branch | Validation phase | 1274 | NA | 0 |  |  | 435 |  | 7522 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 1330 | 8884 |  |  | 7610 |  |  | -2192 | -2192 | -916 | Critical Branch | Validation phase | 1274 | NA | 0 |  |  | 435 |  | 7522 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 1430 | 8884 |  |  | 7610 |  |  | -2192 | -2192 | -916 | Critical Branch | Validation phase | 1274 | NA | 0 |  |  | 435 |  | 7522 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2600 | forecasted security violation
20251103 | November | 1530 |  | 8676 | 832 |  | 6402 | 832 | -2878 | -2878 | 0 | Critical Branch | Validation phase | NA | 2274 | 2878 |  |  | 450 | Reduction because NTC over thermal limit on border | 6696 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2400 | forecasted security violation
20251103 | November | 1630 |  | 8676 | 832 |  | 6402 | 832 | -2878 | -2878 | 0 | Critical Branch | Validation phase | NA | 2274 | 2878 |  |  | 450 | Reduction because NTC over thermal limit on border | 6696 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2400 | forecasted security violation
20251103 | November | 1730 |  | 8676 | 832 |  | 6002 | 832 | -2878 | -2878 | 0 | Critical Branch | Validation phase | NA | 2674 | 2878 |  |  | 450 | Reduction because NTC over thermal limit on border | 6696 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2200 | forecasted security violation
20251103 | November | 1830 | 8771 |  |  | 6221 |  |  | -1945 | -1945 | 643 | Critical Branch | Validation phase | 2550 | NA | 3231 |  |  | 429 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2000 | forecasted security violation
20251103 | November | 1930 | 8771 |  |  | 6221 |  |  | -1945 | -1945 | 643 | Critical Branch | Validation phase | 2550 | NA | 3231 |  |  | 429 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2000 | forecasted security violation
20251103 | November | 2030 | 8771 |  |  | 6221 |  |  | -1945 | -1945 | 643 | Critical Branch | Validation phase | 2550 | NA | 3231 |  |  | 429 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2000 | forecasted security violation
20251103 | November | 2130 | 8745 |  |  | 6221 |  |  | -2089 | -2089 | 477 | Critical Branch | Validation phase | 2524 | NA | 3043 |  |  | 428 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2000 | forecasted security violation
20251103 | November | 2230 | 8745 |  |  | 6621 |  |  | -2089 | -2089 | 54 | Critical Branch | Validation phase | 2124 | NA | 2197 |  |  | 428 |  | 7600 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2200 | forecasted security violation
20251103 | November | 2330 | 8135 |  |  | 7154 |  |  | -1450 | -1450 | -450 | Critical Branch | Validation phase | 981 | NA | 0 |  |  | 412 |  | 7385 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  |  | 2300 | forecasted security violation
20251104 | November | 0030 | 9311 |  |  | 7332 |  |  | -2343 | -2343 | -305 | Critical Branch | Validation phase | 1979 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 9007 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2300 | forecasted security violation
20251104 | November | 0130 | 9311 |  |  | 7332 |  |  | -2343 | -2343 | -305 | Critical Branch | Validation phase | 1979 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 9007 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2300 | forecasted security violation
20251104 | November | 0230 | 9311 |  |  | 7332 |  |  | -2343 | -2343 | -305 | Critical Branch | Validation phase | 1979 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 9007 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2300 | forecasted security violation
20251104 | November | 0330 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 1714 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2300 | forecasted security violation
20251104 | November | 0430 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 1714 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2300 | forecasted security violation
20251104 | November | 0530 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 1714 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2300 | forecasted security violation
20251104 | November | 0630 | 9028 |  |  | 7314 |  |  | -2271 | -2271 | -503 | Critical Branch | TTC Validation phase - bilateral reduction | 1714 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2300 | forecasted security violation
20251104 | November | 0730 | 9323 |  |  | 7417 |  |  | -4846 | -4846 | -2825 | Critical Branch | TTC Validation phase - bilateral reduction | 1906 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2400 | forecasted security violation
20251104 | November | 0830 | 9323 |  |  | 7817 |  |  | -4846 | -4846 | -3235 | Critical Branch | TTC Validation phase - bilateral reduction | 1506 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2600 | forecasted security violation
20251104 | November | 0930 | 9131 |  |  | 7793 |  |  | -2287 | -2287 | -919 | Critical Branch | Validation phase | 1338 | NA | 0 |  |  | 448 |  | 8840 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia |  |  | 2600 | forecasted security violation
20251104 | November | 1030 | 9131 |  |  | 7793 |  |  | -2287 | -2287 | -919 | Critical Branch | Validation phase | 1338 | NA | 0 |  |  | 448 |  | 8840 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia |  |  | 2600 | forecasted security violation
20251104 | November | 1130 | 9131 |  |  | 7793 |  |  | -2287 | -2287 | -919 | Critical Branch | Validation phase | 1338 | NA | 0 |  |  | 448 |  | 8840 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia |  |  | 2600 | forecasted security violation
20251104 | November | 1230 | 9381 |  |  | 7774 |  |  | -2626 | -2626 | -988 | Critical Branch | Validation phase | 1607 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 8702 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA |  |  | 2600 | forecasted security violation
20251104 | November | 1330 | 9381 |  |  | 7774 |  |  | -2626 | -2626 | -988 | Critical Branch | Validation phase | 1607 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 8702 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA |  |  | 2600 | forecasted security violation
20251104 | November | 1430 | 9381 |  |  | 7774 |  |  | -2626 | -2626 | -988 | Critical Branch | Validation phase | 1607 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border | 8702 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA |  |  | 2600 | forecasted security violation
20251104 | November | 1530 | 9171 |  |  | 7255 |  |  | -4314 | -4314 | -2279 | Critical Branch | Validation phase | 1916 | NA | 0 |  |  | 450 |  | 8563 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2400 | forecasted security violation
20251104 | November | 1630 | 9171 |  |  | 7255 |  |  | -4314 | -4314 | -2279 | Critical Branch | Validation phase | 1916 | NA | 0 |  |  | 450 |  | 8563 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2400 | forecasted security violation
20251104 | November | 1730 | 9171 |  |  | 6855 |  |  | -4314 | -4314 | -1868 | Critical Branch | Validation phase | 2316 | NA | 0 |  |  | 450 |  | 8563 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2200 | forecasted security violation
20251104 | November | 1830 | 9376 |  |  | 6422 |  |  | -2992 | -2992 | 31 | Critical Branch | TTC Validation phase - bilateral reduction | 2954 | NA | 3054 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2000 | forecasted security violation
20251104 | November | 1930 | 9376 |  |  | 6422 |  |  | -2992 | -2992 | 31 | Critical Branch | TTC Validation phase - bilateral reduction | 2954 | NA | 3054 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2000 | forecasted security violation
20251104 | November | 2030 | 9376 |  |  | 6422 |  |  | -2992 | -2992 | 31 | Critical Branch | TTC Validation phase - bilateral reduction | 2954 | NA | 3054 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2000 | forecasted security violation
20251104 | November | 2130 | 9366 |  |  | 6421 |  |  | -2224 | -2224 | 801 | Critical Branch | TTC Validation phase - bilateral reduction | 2945 | NA | 3826 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2000 | forecasted security violation
20251104 | November | 2230 | 9366 |  |  | 6821 |  |  | -2224 | -2224 | 375 | Critical Branch | TTC Validation phase - bilateral reduction | 2545 | NA | 2974 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 2200 | forecasted security violation
20251104 | November | 2330 | 8756 |  |  | 7292 |  |  | -1574 | -1574 | -66 | Critical Branch | TTC Validation phase - bilateral reduction | 1464 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border |  |  |  |  | 2300 | forecasted security violation
20251105 | November | 0030 | 8922 |  |  | 7502 |  |  | -2082 | -2082 | -620 | Critical Branch | Validation phase | 1420 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8624 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia |  |  | 2400 | forecasted security violation
20251105 | November | 0130 | 8922 |  |  | 7502 |  |  | -2082 | -2082 | -620 | Critical Branch | Validation phase | 1420 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8624 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia |  |  | 2400 | forecasted security violation
20251105 | November | 0230 | 8922 |  |  | 7502 |  |  | -2082 | -2082 | -620 | Critical Branch | Validation phase | 1420 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8624 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia |  |  | 2400 | forecasted security violation
20251105 | November | 0330 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 1290 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8024 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2400 | forecasted security violation
20251105 | November | 0430 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 1290 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8024 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2400 | forecasted security violation
20251105 | November | 0530 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 1290 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8024 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2400 | forecasted security violation
20251105 | November | 0630 | 8729 |  |  | 7439 |  |  | -2042 | -2042 | -728 | Critical Branch | Validation phase | 1290 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8024 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2400 | forecasted security violation
20251105 | November | 0730 | 8105 |  |  | 7456 |  |  | -1415 | -1415 | -788 | Critical Branch | TTC Validation phase - bilateral reduction | 649 | NA | 0 |  |  | 395 | [5 empty] | 2400 | forecasted security violation
20251105 | November | 0830 | 8105 |  |  | 7756 |  |  | -1415 | -1415 | -1065 | Critical Branch | TTC Validation phase - bilateral reduction | 349 | NA | 0 |  |  | 395 | [5 empty] | 2600 | forecasted security violation
20251105 | November | 0930 | 8666 |  |  | 7827 |  |  | -3689 | -3689 | -2798 | Critical Branch | Validation phase | 839 | NA | 0 |  |  | 424 |  | 8364 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2600 | forecasted security violation
20251105 | November | 1030 | 8666 |  |  | 7827 |  |  | -3689 | -3689 | -2798 | Critical Branch | Validation phase | 839 | NA | 0 |  |  | 424 |  | 8364 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2600 | forecasted security violation
20251105 | November | 1130 | 8666 |  |  | 7827 |  |  | -3689 | -3689 | -2798 | Critical Branch | Validation phase | 839 | NA | 0 |  |  | 424 |  | 8364 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2600 | forecasted security violation
20251105 | November | 1230 | 8858 |  |  | 7810 |  |  | -2533 | -2533 | -1447 | Critical Branch | Validation phase | 1048 | NA | 0 |  |  | 434 |  | 8243 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2600 | forecasted security violation
20251105 | November | 1330 | 8858 |  |  | 7810 |  |  | -2533 | -2533 | -1447 | Critical Branch | Validation phase | 1048 | NA | 0 |  |  | 434 |  | 8243 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2600 | forecasted security violation
20251105 | November | 1430 | 8858 |  |  | 7810 |  |  | -2533 | -2533 | -1447 | Critical Branch | Validation phase | 1048 | NA | 0 |  |  | 434 |  | 8243 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2600 | forecasted security violation
20251105 | November | 1530 | 8435 |  |  | 7602 |  |  | -3551 | -3551 | -2748 | Critical Branch | TTC Validation phase - bilateral reduction | 833 | NA | 0 |  |  | 412 | [5 empty] | 2400 | forecasted security violation
20251105 | November | 1630 | 8435 |  |  | 7302 |  |  | -3551 | -3551 | -2355 | Critical Branch | TTC Validation phase - bilateral reduction | 1133 | NA | 0 |  |  | 412 | [5 empty] | 2400 | forecasted security violation
20251105 | November | 1730 | 9835 |  |  | 6657 |  |  | -4787 | -4787 | -1618 | Critical Branch | Validation phase | 3178 | NA | 0 |  |  | 417 |  | 8250 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano |  |  | 2500 | forecasted security violation
20251105 | November | 1830 | 10465 |  |  | 6721 |  |  | -2887 | -2887 | 904 | Critical Branch | Validation phase | 3744 | NA | 4695 |  |  | 445 |  | 8786 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2700 | forecasted security violation
20251105 | November | 1930 | 10465 |  |  | 6721 |  |  | -2887 | -2887 | 904 | Critical Branch | Validation phase | 3744 | NA | 4695 |  |  | 445 |  | 8786 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2700 | forecasted security violation
20251105 | November | 2030 | 10465 |  |  | 6721 |  |  | -2887 | -2887 | 904 | Critical Branch | Validation phase | 3744 | NA | 4695 |  |  | 441 |  | 8786 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 2700 | forecasted security violation
20251105 | November | 2130 | 8864 |  |  | 6700 |  |  | -3958 | -3958 | -1685 | Critical Branch | TTC Validation phase - bilateral reduction | 2164 | NA | 0 |  |  | 374 | [5 empty] | 2700 | forecasted security violation
20251105 | November | 2230 | 8864 |  |  | 7300 |  |  | -3958 | -3958 | -2303 | Critical Branch | TTC Validation phase - bilateral reduction | 1564 | NA | 0 |  |  | 374 | [5 empty] | 2900 | forecasted security violation
20251105 | November | 2330 | 8054 |  |  | 7178 |  |  | -3149 | -3149 | -2212 | Critical Branch | TTC Validation phase - bilateral reduction | 876 | NA | 0 |  |  | 355 | [5 empty] | 2700 | forecasted security violation
20251106 | November | 0030 | 9379 |  |  | 7432 |  |  | -4635 | -4635 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 1947 | NA | 0 |  |  | 417 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0130 | 9379 |  |  | 7432 |  |  | -4635 | -4635 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 1947 | NA | 0 |  |  | 417 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0230 | 9379 |  |  | 7432 |  |  | -4635 | -4635 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 1947 | NA | 0 |  |  | 417 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0330 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 1643 | NA | 0 |  |  | 401 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0430 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 1643 | NA | 0 |  |  | 401 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0530 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 1643 | NA | 0 |  |  | 401 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0630 | 9036 |  |  | 7393 |  |  | -2606 | -2606 | -878 | Critical Branch | TTC Validation phase - bilateral reduction | 1643 | NA | 0 |  |  | 401 | Reduction because NTC over thermal limit on border |  |  |  |  | 2900 | forecasted security violation
20251106 | November | 0730 | 9620 |  |  | 7490 |  |  | -1636 | -1636 | 620 | Critical Branch | TTC Validation phase - bilateral reduction | 2130 | NA | 2876 |  |  | 407 | [5 empty] | 2900 | forecasted security violation
20251106 | November | 0830 | 9620 |  |  | 7790 |  |  | -1636 | -1636 | 252 | Critical Branch | TTC Validation phase - bilateral reduction | 1830 | NA | 2140 |  |  | 407 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 0930 | 9301 |  |  | 7752 |  |  | -4813 | -4813 | -3185 | Critical Branch | TTC Validation phase - bilateral reduction | 1549 | NA | 0 |  |  | 393 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 1030 | 9301 |  |  | 7752 |  |  | -4813 | -4813 | -3185 | Critical Branch | TTC Validation phase - bilateral reduction | 1549 | NA | 0 |  |  | 393 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 1130 | 9301 |  |  | 7752 |  |  | -4813 | -4813 | -3185 | Critical Branch | TTC Validation phase - bilateral reduction | 1549 | NA | 0 |  |  | 393 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 1230 | 10282 |  |  | 7869 |  |  | -5061 | -5061 | -2533 | Critical Branch | TTC Validation phase - bilateral reduction | 2413 | NA | 0 |  |  | 437 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 1330 | 10282 |  |  | 7869 |  |  | -5061 | -5061 | -2533 | Critical Branch | TTC Validation phase - bilateral reduction | 2413 | NA | 0 |  |  | 437 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 1430 | 10282 |  |  | 7869 |  |  | -5061 | -5061 | -2533 | Critical Branch | TTC Validation phase - bilateral reduction | 2413 | NA | 0 |  |  | 437 | [5 empty] | 3200 | forecasted security violation
20251106 | November | 1530 | 9837 |  |  | 7792 |  |  | -2915 | -2915 | -806 | Critical Branch | Validation phase | 2045 | NA | 0 |  |  | 417 |  | 9378 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 3200 | forecasted security violation
20251106 | November | 1630 | 9837 |  |  | 7392 |  |  | -2915 | -2915 | -394 | Critical Branch | Validation phase | 2445 | NA | 0 |  |  | 417 |  | 9378 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano |  |  | 3000 | forecasted security violation
20251106 | November | 1730 | 9837 |  |  | 8892 |  |  | -2915 | -2915 | -1970 | Critical Branch | Smoothing ramp | 945 | NA | 0 | Smoothing | Smoothing ramp | 417 |  | 9378 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano
20251106 | November | 1830 | 10049 |  |  | 9762 |  |  | -3084 | -3084 | -2797 | Critical Branch | Validation phase | 287 | NA | 0 |  |  | 427 |  | 9512 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251106 | November | 1930 | 10049 |  |  | 9762 |  |  | -3084 | -3084 | -2797 | Critical Branch | Validation phase | 287 | NA | 0 |  |  | 427 |  | 9512 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2030 | 10049 |  |  | 9762 |  |  | -3084 | -3084 | -2797 | Critical Branch | Validation phase | 287 | NA | 0 |  |  | 427 |  | 9512 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2130 | 9940 |  |  | 9562 |  |  | -4009 | -4009 | -3631 | Critical Branch | Validation phase | 378 | NA | 0 |  |  | 422 |  | 9312 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2230 | 9940 |  |  | 9562 |  |  | -4009 | -4009 | -3631 | Critical Branch | Validation phase | 378 | NA | 0 |  |  | 422 |  | 9312 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251106 | November | 2330 | 9130 |  |  | 8752 |  |  | -3195 | -3195 | -2817 | Critical Branch | Validation phase | 378 | NA | 0 |  |  | 405 |  | 8502 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0030 | 9681 |  |  | 8904 |  |  | -4320 | -4320 | -3543 | Critical Branch | Validation phase | 777 | NA | 0 |  |  | 431 |  | 8654 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0130 | 9681 |  |  | 8904 |  |  | -4320 | -4320 | -3543 | Critical Branch | Validation phase | 777 | NA | 0 |  |  | 431 |  | 8654 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0230 | 9681 |  |  | 8904 |  |  | -4320 | -4320 | -3543 | Critical Branch | Validation phase | 777 | NA | 0 |  |  | 431 |  | 8654 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0330 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 844 | NA | 0 |  |  | 433 |  | 8623 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0430 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 844 | NA | 0 |  |  | 433 |  | 8623 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0530 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 844 | NA | 0 |  |  | 433 |  | 8623 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0630 | 9717 |  |  | 8873 |  |  | -4373 | -4373 | -3529 | Critical Branch | Validation phase | 844 | NA | 0 |  |  | 433 |  | 8623 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0730 | 9949 |  |  | 8400 |  |  | -2896 | -2896 | -1347 | Critical Branch | Validation phase | 1549 | NA | 0 |  |  | 422 |  | 8150 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0830 | 9949 |  |  | 8400 |  |  | -2896 | -2896 | -1347 | Critical Branch | Validation phase | 1549 | NA | 0 |  |  | 422 |  | 8150 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251107 | November | 0930 | 9670 |  |  | 8269 |  |  | -2567 | -2567 | -1166 | Critical Branch | Validation phase | 1401 | NA | 0 |  |  | 410 |  | 8019 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1030 | 9670 |  |  | 8269 |  |  | -2567 | -2567 | -1166 | Critical Branch | Validation phase | 1401 | NA | 0 |  |  | 410 |  | 8019 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1130 | 9670 |  |  | 8269 |  |  | -2567 | -2567 | -1166 | Critical Branch | Validation phase | 1401 | NA | 0 |  |  | 410 |  | 8019 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1230 | 8814 |  |  | 7941 |  |  | -2686 | -2686 | -1813 | Critical Branch | Validation phase | 873 | NA | 0 |  |  | 371 |  | 7691 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1330 | 8814 |  |  | 7941 |  |  | -2686 | -2686 | -1813 | Critical Branch | Validation phase | 873 | NA | 0 |  |  | 371 |  | 7691 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1430 | 8814 |  |  | 7941 |  |  | -2686 | -2686 | -1813 | Critical Branch | Validation phase | 873 | NA | 0 |  |  | 371 |  | 7691 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 1530 |  | 9970 | 766 |  | 9049 | 727 | -2911 | -2911 | 0 | Critical Branch | Validation phase | NA | 960 | 2911 |  |  | 450 | Reduction because NTC over thermal limit on border | 9949 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251107 | November | 1630 |  | 9970 | 766 |  | 9423 | 727 | -2911 | -2911 | 0 | Critical Branch | Validation phase | NA | 586 | 2911 |  |  | 450 | Reduction because NTC over thermal limit on border | 9949 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251107 | November | 1730 |  | 9970 | 766 |  | 9423 | 727 | -2911 | -2911 | 0 | Critical Branch | Validation phase | NA | 586 | 2911 |  |  | 450 | Reduction because NTC over thermal limit on border | 9949 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251107 | November | 1830 |  | 10205 | 801 |  | 9943 | 783 | -5645 | -5645 | 0 | Critical Branch | Validation phase | NA | 280 | 5645 |  |  | 450 | Reduction because NTC over thermal limit on border | 10371 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251107 | November | 1930 |  | 10205 | 801 |  | 9943 | 783 | -5645 | -5645 | 0 | Critical Branch | Validation phase | NA | 280 | 5645 |  |  | 450 | Reduction because NTC over thermal limit on border | 10371 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251107 | November | 2030 |  | 10205 | 801 |  | 9321 | 783 | -5645 | -5645 | 0 | Critical Branch | Validation phase | NA | 902 | 5645 |  |  | 450 | Reduction because NTC over thermal limit on border | 10371 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251107 | November | 2130 | 10336 |  |  | 8212 |  |  | -2945 | -2945 | -821 | Critical Branch | Validation phase | 2124 | NA | 0 |  |  | 439 |  | 7962 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 2230 | 10336 |  |  | 8212 |  |  | -2945 | -2945 | -821 | Critical Branch | Validation phase | 2124 | NA | 0 |  |  | 439 |  | 7962 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251107 | November | 2330 | 9526 |  |  | 7402 |  |  | -2120 | -2120 | 4 | Critical Branch | Validation phase | 2124 | NA | 2128 |  |  | 424 |  | 7152 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0030 | 10754 |  |  | 8914 |  |  | -5430 | -5430 | -3590 | Critical Branch | Validation phase | 1840 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8664 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0130 | 10754 |  |  | 8914 |  |  | -5430 | -5430 | -3590 | Critical Branch | Validation phase | 1840 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8664 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0230 | 10754 |  |  | 8669 |  |  | -5430 | -5430 | -3345 | Critical Branch | Validation phase | 2085 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 8664 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0330 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 3378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6919 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0430 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 3378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6919 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0530 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 3378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6919 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0630 | 10547 |  |  | 7169 |  |  | -5365 | -5365 | -1987 | Critical Branch | Validation phase | 3378 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border | 6919 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251108 | November | 0730 | 10563 |  |  | 8669 |  |  | -2881 | -2881 | -987 | Critical Branch | Smoothing ramp | 1894 | NA | 0 | Smoothing | Smoothing ramp | 450 |  | 9737 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0830 | 10563 |  |  | 9987 |  |  | -2881 | -2881 | -2305 | Critical Branch | Validation phase | 576 | NA | 0 |  |  | 450 |  | 9737 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251108 | November | 0930 | 9265 |  |  | 9104 |  |  | -3944 | -3944 | -3783 | Critical Branch | Validation phase | 161 | NA | 0 |  |  | 392 |  | 8854 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1030 | 9265 |  |  | 9104 |  |  | -3944 | -3944 | -3783 | Critical Branch | Validation phase | 161 | NA | 0 |  |  | 392 |  | 8854 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1130 | 9265 |  |  | 9104 |  |  | -3944 | -3944 | -3783 | Critical Branch | Validation phase | 161 | NA | 0 |  |  | 392 |  | 8854 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1230 | 9532 |  |  | 8899 |  |  | -3952 | -3952 | -3319 | Critical Branch | Validation phase | 633 | NA | 0 |  |  | 404 |  | 8649 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1330 | 9532 |  |  | 8899 |  |  | -3952 | -3952 | -3319 | Critical Branch | Validation phase | 633 | NA | 0 |  |  | 404 |  | 8649 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1430 | 9532 |  |  | 8899 |  |  | -3952 | -3952 | -3319 | Critical Branch | Validation phase | 633 | NA | 0 |  |  | 404 |  | 8649 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251108 | November | 1530 |  | 10286 | 815 |  | 9990 | 815 | -5861 | -5861 | 0 | Critical Branch | Critical Branch | NA | 296 | 5861 |  |  | 450 | Reduction because NTC over thermal limit on border
20251108 | November | 1630 |  | 10286 | 815 |  | 10261 | 815 | -5861 | -5861 | 0 | Critical Branch | Critical Branch | NA | 25 | 5861 |  |  | 450 | Reduction because NTC over thermal limit on border
20251108 | November | 1730 |  | 10286 | 815 |  | 10261 | 815 | -5861 | -5861 | 0 | Critical Branch | Critical Branch | NA | 25 | 5861 |  |  | 450 | Reduction because NTC over thermal limit on border
20251108 | November | 1830 | 10279 |  |  | 9756 |  |  | -2820 | -2820 | -2297 | Critical Branch | Validation phase | 523 | NA | 0 |  |  | 437 |  | 9506 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251108 | November | 1930 | 10279 |  |  | 9756 |  |  | -2820 | -2820 | -2297 | Critical Branch | Validation phase | 523 | NA | 0 |  |  | 437 |  | 9506 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251108 | November | 2030 | 10279 |  |  | 9756 |  |  | -2820 | -2820 | -2297 | Critical Branch | Validation phase | 523 | NA | 0 |  |  | 437 |  | 9506 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251108 | November | 2130 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  | 450 |  | 8298 | D2CC failed. Correction of BackUp-values.
20251108 | November | 2230 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  | 450 |  | 8298 | D2CC failed. Correction of BackUp-values.
20251108 | November | 2330 | 9750 |  |  | 7738 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  | 435 |  | 7488 | D2CC failed. Correction of BackUp-values.
20251109 | November | 0030 | 10534 |  |  | 10497 |  |  | -5174 | -5174 | -5142 | Critical Branch | Critical Branch | 37 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0130 | 10534 |  |  | 10497 |  |  | -5174 | -5174 | -5142 | Critical Branch | Critical Branch | 37 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0230 | 10534 |  |  | 10497 |  |  | -5174 | -5174 | -5142 | Critical Branch | Critical Branch | 37 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0330 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | NA | 7 | 1190 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0430 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | NA | 7 | 1190 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0530 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | NA | 7 | 1190 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0630 |  | 9218 | 902 |  | 9211 | 902 | -1190 | -1190 | 0 | Critical Branch | Critical Branch | NA | 7 | 1190 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0730 | 10325 |  |  | 10298 |  |  | -5501 | -5501 | -5481 | Critical Branch | Critical Branch | 27 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0830 | 10325 |  |  | 10298 |  |  | -5501 | -5501 | -5481 | Critical Branch | Critical Branch | 27 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 0930 |  | 9395 | 783 |  | 9379 | 783 | -4175 | -4175 | 0 | Critical Branch | Critical Branch | NA | 16 | 4175 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 1030 |  | 9395 | 783 |  | 9379 | 783 | -4175 | -4175 | 0 | Critical Branch | Critical Branch | NA | 16 | 4175 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 1130 |  | 9395 | 783 |  | 8758 | 783 | -4175 | -4175 | 0 | Critical Branch | Critical Branch | NA | 637 | 4175 |  |  | 419
20251109 | November | 1230 |  | 7080 | 489 |  | 7066 | 489 | 4168 | 25 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 14 | -25 |  |  | 334 |  |  |  | 3166 | Process fail during TSO validation phase
20251109 | November | 1330 |  | 7204 | 499 |  | 7131 | 499 | 4168 | 149 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 73 | -149 |  |  | 340 |  |  |  | 3166 | Process fail during TSO validation phase
20251109 | November | 1430 |  | 7264 | 504 |  | 7163 | 504 | 4168 | 210 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 101 | -210 |  |  | 343 |  |  |  | 3167 | Process fail during TSO validation phase
20251109 | November | 1530 |  | 9918 | 1083 |  | 8649 | 1048 | -5551 | -5551 | 0 | Critical Branch | Critical Branch | NA | 1304 | 5551 |  |  | 206 | Reduction because NTC over thermal limit on border
20251109 | November | 1630 |  | 9918 | 1083 |  | 9918 | 1048 | -5551 | -5551 | 0 | Critical Branch | Critical Branch | NA | 35 | 5551 |  |  | 236 | Reduction because NTC over thermal limit on border
20251109 | November | 1730 |  | 9918 | 1083 |  | 9918 | 1048 | -5551 | -5551 | 0 | Critical Branch | Critical Branch | NA | 35 | 5551 |  |  | 236 | Reduction because NTC over thermal limit on border
20251109 | November | 1830 |  | 10046 | 793 |  | 9997 | 793 | -2747 | -2747 | 0 | Critical Branch | Critical Branch | NA | 49 | 2747 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 1930 |  | 10046 | 793 |  | 9997 | 793 | -2747 | -2747 | 0 | Critical Branch | Critical Branch | NA | 49 | 2747 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 2030 |  | 10046 | 793 |  | 9997 | 793 | -2747 | -2747 | 0 | Critical Branch | Critical Branch | NA | 49 | 2747 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 2130 | 10796 |  |  | 10747 |  |  | -5842 | -5842 | -5797 | Critical Branch | Critical Branch | 49 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 2230 | 10796 |  |  | 10747 |  |  | -5842 | -5842 | -5797 | Critical Branch | Critical Branch | 49 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251109 | November | 2330 | 10796 |  |  | 10747 |  |  | -5842 | -5842 | -5797 | Critical Branch | Critical Branch | 49 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251110 | November | 0030 | 10099 |  |  | 10083 |  |  | -3038 | -3038 | -3027 | Critical Branch | Critical Branch | 16 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251110 | November | 0130 | 10099 |  |  | 10083 |  |  | -3038 | -3038 | -3027 | Critical Branch | Critical Branch | 16 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251110 | November | 0230 | 10099 |  |  | 10083 |  |  | -3038 | -3038 | -3027 | Critical Branch | Critical Branch | 16 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251110 | November | 0330 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20251110 | November | 0430 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20251110 | November | 0530 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20251110 | November | 0630 | 9454 |  |  | 9454 |  |  | -3678 | -3678 | -3677 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 421
20251110 | November | 0730 |  | 9798 | 1009 |  | 9798 | 984 | -3269 | -3269 | 0 | Critical Branch | Critical Branch | NA | 25 | 3269 |  |  | 227 | Reduction because NTC over thermal limit on border
20251110 | November | 0830 |  | 9798 | 1009 |  | 9798 | 984 | -3269 | -3269 | 0 | Critical Branch | Critical Branch | NA | 25 | 3269 |  |  | 227 | Reduction because NTC over thermal limit on border
20251110 | November | 0930 |  | 10212 | 782 |  | 10180 | 782 | -3373 | -3373 | 0 | Critical Branch | Critical Branch | NA | 32 | 3373 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1030 |  | 10212 | 782 |  | 10180 | 782 | -3373 | -3373 | 0 | Critical Branch | Critical Branch | NA | 32 | 3373 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1130 |  | 10212 | 782 |  | 10180 | 782 | -3373 | -3373 | 0 | Critical Branch | Critical Branch | NA | 32 | 3373 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1230 |  | 10107 | 732 |  | 10080 | 732 | -3927 | -3927 | 0 | Critical Branch | Critical Branch | NA | 27 | 3927 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1330 |  | 10107 | 732 |  | 10080 | 732 | -3927 | -3927 | 0 | Critical Branch | Critical Branch | NA | 27 | 3927 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1430 |  | 10107 | 732 |  | 10080 | 732 | -3927 | -3927 | 0 | Critical Branch | Critical Branch | NA | 27 | 3927 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1530 | 10441 |  |  | 10437 |  |  | -3096 | -3096 | -3092 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1630 | 10441 |  |  | 10437 |  |  | -3096 | -3096 | -3092 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1730 | 10641 |  |  | 10637 |  |  | -3327 | -3327 | -3324 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border
20251110 | November | 1830 |  | 9783 | 704 |  | 9782 | 704 | -3447 | -3447 | 0 | Critical Branch | Critical Branch | NA | 1 | 3447 |  |  | 450
20251110 | November | 1930 |  | 9783 | 704 |  | 9782 | 704 | -3447 | -3447 | 0 | Critical Branch | Critical Branch | NA | 1 | 3447 |  |  | 450
20251110 | November | 2030 |  | 9783 | 704 |  | 9782 | 704 | -3447 | -3447 | 0 | Critical Branch | Critical Branch | NA | 1 | 3447 |  |  | 450
20251110 | November | 2130 | 9684 |  |  | 9683 |  |  | -2410 | -2410 | -2409 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 410
20251110 | November | 2230 | 9684 |  |  | 9683 |  |  | -2410 | -2410 | -2409 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 410
20251110 | November | 2330 | 8874 |  |  | 8873 |  |  | -1715 | -1715 | -1715 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 393
20251111 | November | 0030 | 10160 |  |  | 10141 |  |  | -3505 | -3505 | -3485 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251111 | November | 0130 | 10160 |  |  | 10141 |  |  | -3505 | -3505 | -3485 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251111 | November | 0230 | 10160 |  |  | 10141 |  |  | -3505 | -3505 | -3485 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251111 | November | 0330 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 434
20251111 | November | 0430 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 434
20251111 | November | 0530 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 434
20251111 | November | 0630 | 9737 |  |  | 9737 |  |  | -3898 | -3898 | -3898 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 434
20251111 | November | 0730 |  | 9278 | 678 |  | 9277 | 678 | -2624 | -2624 | 0 | Critical Branch | Critical Branch | NA | 1 | 2624 |  |  | 435
20251111 | November | 0830 |  | 9278 | 678 |  | 9277 | 678 | -2624 | -2624 | 0 | Critical Branch | Critical Branch | NA | 1 | 2624 |  |  | 435
20251111 | November | 0930 | 9710 |  |  | 9710 |  |  | -2844 | -2844 | -2844 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20251111 | November | 1030 | 9710 |  |  | 9710 |  |  | -2844 | -2844 | -2844 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20251111 | November | 1130 | 9710 |  |  | 9710 |  |  | -2844 | -2844 | -2844 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20251111 | November | 1230 |  | 9948 | 727 |  | 9929 | 727 | -3802 | -3802 | 0 | Critical Branch | Critical Branch | NA | 19 | 3802 |  |  | 450 | Reduction because NTC over thermal limit on border
20251111 | November | 1330 |  | 9948 | 727 |  | 9929 | 727 | -3802 | -3802 | 0 | Critical Branch | Critical Branch | NA | 19 | 3802 |  |  | 450 | Reduction because NTC over thermal limit on border
20251111 | November | 1430 |  | 9948 | 727 |  | 9929 | 727 | -3802 | -3802 | 0 | Critical Branch | Critical Branch | NA | 19 | 3802 |  |  | 450 | Reduction because NTC over thermal limit on border
20251111 | November | 1530 | 9836 |  |  | 9836 |  |  | -3696 | -3696 | -3695 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 426
20251111 | November | 1630 | 9836 |  |  | 9836 |  |  | -3696 | -3696 | -3695 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 426
20251111 | November | 1730 | 10036 |  |  | 10035 |  |  | -3911 | -3911 | -3911 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 426
20251111 | November | 1830 |  | 9307 | 660 |  | 9306 | 660 | -2990 | -2990 | 0 | Critical Branch | Critical Branch | NA | 1 | 2990 |  |  | 427
20251111 | November | 1930 |  | 9307 | 660 |  | 9306 | 660 | -2990 | -2990 | 0 | Critical Branch | Critical Branch | NA | 1 | 2990 |  |  | 427
20251111 | November | 2030 |  | 9307 | 660 |  | 9306 | 660 | -2990 | -2990 | 0 | Critical Branch | Critical Branch | NA | 1 | 2990 |  |  | 427
20251111 | November | 2130 | 9627 |  |  | 9627 |  |  | -3000 | -3000 | -2999 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20251111 | November | 2230 | 9627 |  |  | 9627 |  |  | -3000 | -3000 | -2999 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 408
20251111 | November | 2330 | 8817 |  |  | 8817 |  |  | -2160 | -2160 | -2160 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391
20251112 | November | 0030 | 9873 |  |  | 9867 |  |  | -2427 | -2427 | -2423 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251112 | November | 0130 | 9873 |  |  | 9867 |  |  | -2427 | -2427 | -2423 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251112 | November | 0230 | 9873 |  |  | 9867 |  |  | -2427 | -2427 | -2423 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251112 | November | 0330 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251112 | November | 0430 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251112 | November | 0530 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251112 | November | 0630 | 9696 |  |  | 9696 |  |  | -3997 | -3997 | -3997 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251112 | November | 0730 |  | 8609 | 632 |  | 8608 | 632 | -2139 | -2139 | 0 | Critical Branch | Critical Branch | NA | 1 | 2139 |  |  | 402
20251112 | November | 0830 |  | 8010 | 632 |  | 8010 | 632 | -1299 | -1299 | 0 | Critical Branch | Critical Branch | NA | 0 | 1299 |  |  | 399
20251112 | November | 0930 | 8389 |  |  | 8389 |  |  | -55 | -55 | -55 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 334
20251112 | November | 1030 | 8389 |  |  | 8389 |  |  | -55 | -55 | -55 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 334
20251112 | November | 1130 | 8389 |  |  | 8389 |  |  | -55 | -55 | -55 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 334
20251112 | November | 1230 | 9119 |  |  | 9118 |  |  | -2447 | -2447 | -2446 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 418
20251112 | November | 1330 | 9119 |  |  | 9118 |  |  | -2447 | -2447 | -2446 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 418
20251112 | November | 1430 | 9119 |  |  | 9118 |  |  | -2447 | -2447 | -2446 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 418
20251112 | November | 1530 |  | 8694 | 673 |  | 8693 | 673 | -3884 | -3884 | 0 | Critical Branch | Critical Branch | NA | 1 | 3884 |  |  | 435
20251112 | November | 1630 |  | 9294 | 673 |  | 9294 | 673 | -4454 | -4454 | 0 | Critical Branch | Critical Branch | NA | 0 | 4454 |  |  | 436
20251112 | November | 1730 |  | 9494 | 673 |  | 9493 | 673 | -4675 | -4675 | 0 | Critical Branch | Critical Branch | NA | 1 | 4675 |  |  | 436
20251112 | November | 1830 |  | 8739 | 637 |  | 8739 | 637 | -1851 | -1851 | 0 | Critical Branch | Critical Branch | NA | 0 | 1851 |  |  | 400
20251112 | November | 1930 |  | 8739 | 637 |  | 8739 | 637 | -1851 | -1851 | 0 | Critical Branch | Critical Branch | NA | 0 | 1851 |  |  | 400
20251112 | November | 2030 |  | 8739 | 637 |  | 8739 | 637 | -1851 | -1851 | 0 | Critical Branch | Critical Branch | NA | 0 | 1851 |  |  | 400
20251112 | November | 2130 | 10243 |  |  | 10242 |  |  | -3553 | -3553 | -3552 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 435
20251112 | November | 2230 | 10243 |  |  | 10242 |  |  | -3553 | -3553 | -3552 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 435
20251112 | November | 2330 | 9433 |  |  | 9433 |  |  | -2755 | -2755 | -2755 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 420
20251114 | November | 0030 | 9311 |  |  | 9303 |  |  | -4264 | -4264 | -4255 | Critical Branch | Critical Branch | 8 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251114 | November | 0130 | 9311 |  |  | 9303 |  |  | -4264 | -4264 | -4255 | Critical Branch | Critical Branch | 8 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251114 | November | 0230 | 9311 |  |  | 9303 |  |  | -4264 | -4264 | -4255 | Critical Branch | Critical Branch | 8 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251114 | November | 0330 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251114 | November | 0430 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251114 | November | 0530 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251114 | November | 0630 | 9076 |  |  | 9076 |  |  | -4003 | -4003 | -4003 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 431
20251114 | November | 0730 |  | 9536 | 771 |  | 9259 | 771 | -4225 | -4225 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 277 | 4225 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 0830 |  | 9536 | 771 |  | 9259 | 771 | -4225 | -4225 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 277 | 4225 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 0930 | 10011 |  |  | 9899 |  |  | -3255 | -3255 | -3147 | Critical Branch | TTC Validation phase - bilateral reduction | 112 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1030 | 10011 |  |  | 9899 |  |  | -3255 | -3255 | -3147 | Critical Branch | TTC Validation phase - bilateral reduction | 112 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1130 | 10011 |  |  | 9899 |  |  | -3255 | -3255 | -3147 | Critical Branch | TTC Validation phase - bilateral reduction | 112 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1230 | 10277 |  |  | 10046 |  |  | -2670 | -2670 | -2475 | Critical Branch | TTC Validation phase - bilateral reduction | 231 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1330 | 10277 |  |  | 10046 |  |  | -2670 | -2670 | -2475 | Critical Branch | TTC Validation phase - bilateral reduction | 231 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1430 | 10277 |  |  | 10046 |  |  | -2670 | -2670 | -2475 | Critical Branch | TTC Validation phase - bilateral reduction | 231 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1530 | 10004 |  |  | 9895 |  |  | -2850 | -2850 | -2757 | Critical Branch | TTC Validation phase - bilateral reduction | 109 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border |  |  | 3685 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1
20251114 | November | 1630 | 10604 |  |  | 10593 |  |  | -3387 | -3387 | -3377 | Critical Branch | Critical Branch | 11 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border
20251114 | November | 1730 | 10804 |  |  | 10793 |  |  | -3615 | -3615 | -3605 | Critical Branch | Critical Branch | 11 | NA | 0 |  |  | 450 | Reduction because NTC over thermal limit on border
20251114 | November | 1830 |  | 10392 | 766 |  | 10362 | 766 | -3693 | -3693 | 0 | Critical Branch | Critical Branch | NA | 30 | 3693 |  |  | 450 | Reduction because NTC over thermal limit on border
20251114 | November | 1930 |  | 10392 | 766 |  | 10362 | 766 | -3693 | -3693 | 0 | Critical Branch | Critical Branch | NA | 30 | 3693 |  |  | 450 | Reduction because NTC over thermal limit on border
20251114 | November | 2030 |  | 10392 | 766 |  | 10362 | 766 | -3693 | -3693 | 0 | Critical Branch | Critical Branch | NA | 30 | 3693 |  |  | 450 | Reduction because NTC over thermal limit on border
20251114 | November | 2130 | 9409 |  |  | 9408 |  |  | -4039 | -4039 | -4039 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 398
20251114 | November | 2230 | 9409 |  |  | 9408 |  |  | -4039 | -4039 | -4039 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 398
20251114 | November | 2330 | 8599 |  |  | 8598 |  |  | -3230 | -3230 | -3229 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251116 | November | 1130 | 9750 |  |  | 9646 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 104 | NA | 0 | Smoothing | Smoothing ramp
20251116 | November | 1230 | 9750 |  |  | 8146 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1604 | NA | 0 | [10 empty] | 7896 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251116 | November | 1330 | 9525 |  |  | 8034 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1491 | NA | 0 | [10 empty] | 7784 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251116 | November | 1430 | 9525 |  |  | 8034 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1491 | NA | 0 | [10 empty] | 7784 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251119 | November | 0730 | 9507 |  |  | 8789 |  |  | -1703 | -1703 | -985 | Critical Branch | Validation phase | 718 | NA | 0 |  |  |  |  | 8539 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251119 | November | 0830 | 9507 |  |  | 8789 |  |  | -1703 | -1703 | -985 | Critical Branch | Validation phase | 718 | NA | 0 |  |  |  |  | 8539 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1530 | 9587 |  |  | 8247 |  |  | -4421 | -4421 | -3081 | Critical Branch | Validation phase | 1340 | NA | 0 |  |  |  |  | 7997 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1630 | 9587 |  |  | 8247 |  |  | -4421 | -4421 | -3081 | Critical Branch | Validation phase | 1340 | NA | 0 |  |  |  |  | 7997 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1730 | 9587 |  |  | 8247 |  |  | -4421 | -4421 | -3081 | Critical Branch | Validation phase | 1340 | NA | 0 |  |  |  |  | 7997 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1830 | 10120 |  |  | 9445 |  |  | -2559 | -2559 | -1884 | Critical Branch | Validation phase | 675 | NA | 0 |  |  |  |  | 9195 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 1930 | 10120 |  |  | 9445 |  |  | -2559 | -2559 | -1884 | Critical Branch | Validation phase | 675 | NA | 0 |  |  |  |  | 9195 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251119 | November | 2030 | 10120 |  |  | 9445 |  |  | -2559 | -2559 | -1884 | Critical Branch | Validation phase | 675 | NA | 0 |  |  |  |  | 9195 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0030 | 9375 |  |  | 9374 |  |  | -4843 | -4843 | -4843 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 206
20251120 | November | 0130 | 9375 |  |  | 9374 |  |  | -4843 | -4843 | -4843 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 206
20251120 | November | 0230 | 9375 |  |  | 9374 |  |  | -4843 | -4843 | -4843 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 206
20251120 | November | 0330 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 604 | NA | 0 |  |  | 205 |  | 8476 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0430 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 604 | NA | 0 |  |  | 205 |  | 8476 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0530 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 604 | NA | 0 |  |  | 205 |  | 8476 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0630 | 9330 |  |  | 8726 |  |  | -4371 | -4371 | -3767 | Critical Branch | Validation phase | 604 | NA | 0 |  |  | 205 |  | 8476 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251120 | November | 0730 |  | 8676 | 825 |  | 8676 | 821 | -4148 | -4148 | 0 | Critical Branch | Critical Branch | NA | 4 | 4148 |  |  | 92 | Reduction because NTC over thermal limit on border
20251120 | November | 0830 |  | 8676 | 825 |  | 8676 | 821 | -4148 | -4148 | 0 | Critical Branch | Critical Branch | NA | 4 | 4148 |  |  | 92 | Reduction because NTC over thermal limit on border
20251120 | November | 0930 |  | 8054 | 143 |  | 8017 | 81 | 5318 | 79 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 99 | -79 |  |  | 163 | Reduction because NTC over thermal limit on border |  |  | 3337 | Process fail during TSO validation phase
20251120 | November | 1030 |  | 8173 | 146 |  | 8082 | 81 | 5318 | 198 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 156 | -198 |  |  | 163 | Reduction because NTC over thermal limit on border |  |  | 3337 | Process fail during TSO validation phase
20251120 | November | 1130 |  | 8108 | 145 |  | 8046 | 81 | 5318 | 133 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 126 | -133 |  |  | 163 | Reduction because NTC over thermal limit on border |  |  | 3337 | Process fail during TSO validation phase
20251120 | November | 1230 |  | 7437 | 488 |  | 6401 | 487 | 3523 | 86 | 0 | Minimum Margin | Validation phase | NA | 1037 | -86 |  |  | 163 |  |  |  | 3337 | Process fail during TSO validation phase |  |  | 6489 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251120 | November | 1330 |  | 7433 | 488 |  | 6395 | 487 | 3523 | 82 | 0 | Minimum Margin | Validation phase | NA | 1039 | -82 |  |  | 163 |  |  |  | 3337 | Process fail during TSO validation phase |  |  | 6487 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251120 | November | 1430 |  | 7515 | 495 |  | 6584 | 493 | 3523 | 165 | 0 | Minimum Margin | Validation phase | NA | 933 | -165 |  |  | 163 |  |  |  | 3337 | Process fail during TSO validation phase |  |  | 6593 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251120 | November | 1530 |  | 9094 | 941 |  | 8066 | 925 | -4360 | -4360 | 0 | Critical Branch | Critical Branch | NA | 1044 | 4360 |  |  | 97 | Reduction because NTC over thermal limit on border
20251120 | November | 1630 |  | 9094 | 941 |  | 9094 | 925 | -4360 | -4360 | 0 | Critical Branch | Critical Branch | NA | 16 | 4360 |  |  | 97 | Reduction because NTC over thermal limit on border
20251120 | November | 1730 |  | 9094 | 941 |  | 9094 | 925 | -4360 | -4360 | 0 | Critical Branch | Critical Branch | NA | 16 | 4360 |  |  | 97 | Reduction because NTC over thermal limit on border
20251120 | November | 1830 |  | 8737 | 877 |  | 8737 | 868 | -4023 | -4023 | 0 | Critical Branch | Critical Branch | NA | 9 | 4023 |  |  | 93 | Reduction because NTC over thermal limit on border
20251120 | November | 1930 |  | 8737 | 877 |  | 8737 | 868 | -4023 | -4023 | 0 | Critical Branch | Critical Branch | NA | 9 | 4023 |  |  | 93 | Reduction because NTC over thermal limit on border
20251120 | November | 2030 |  | 8737 | 877 |  | 8737 | 868 | -4023 | -4023 | 0 | Critical Branch | Critical Branch | NA | 9 | 4023 |  |  | 93 | Reduction because NTC over thermal limit on border
20251120 | November | 2130 | 9516 |  |  | 9155 |  |  | -4818 | -4818 | -4457 | Critical Branch | Validation phase | 361 | NA | 0 |  |  | 192 |  | 8905 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251120 | November | 2230 | 9516 |  |  | 9155 |  |  | -4818 | -4818 | -4457 | Critical Branch | Validation phase | 361 | NA | 0 |  |  | 192 |  | 8905 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251120 | November | 2330 | 8721 |  |  | 8360 |  |  | -4024 | -4024 | -3663 | Critical Branch | Validation phase | 361 | NA | 0 |  |  | 191 |  | 8110 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251121 | November | 0030 | 9221 |  |  | 8297 |  |  | -4362 | -4362 | -3438 | Critical Branch | Validation phase | 924 | NA | 0 |  |  | 202 |  | 8047 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0130 | 9221 |  |  | 8297 |  |  | -4362 | -4362 | -3438 | Critical Branch | Validation phase | 924 | NA | 0 |  |  | 202 |  | 8047 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0230 | 9221 |  |  | 8297 |  |  | -4362 | -4362 | -3438 | Critical Branch | Validation phase | 924 | NA | 0 |  |  | 202 |  | 8047 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0330 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 492 | NA | 0 |  |  | 187 |  | 7813 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0430 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 492 | NA | 0 |  |  | 187 |  | 7813 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0530 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 492 | NA | 0 |  |  | 187 |  | 7813 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0630 | 8555 |  |  | 8063 |  |  | -3291 | -3291 | -2799 | Critical Branch | Validation phase | 492 | NA | 0 |  |  | 187 |  | 7813 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS
20251121 | November | 0730 |  | 8638 | 776 |  | 8638 | 775 | -2051 | -2051 | 0 | Critical Branch | Critical Branch | NA | 1 | 2051 |  |  | 92 |  |  | NTC correction
20251121 | November | 0830 |  | 8638 | 776 |  | 8638 | 775 | -2051 | -2051 | 0 | Critical Branch | Critical Branch | NA | 1 | 2051 |  |  | 92 |  |  | NTC correction
20251121 | November | 0930 | 8334 |  |  | 8333 |  |  | 5927 | 184 | 5744 | Minimum Margin | Minimum Margin | 1 | NA | 11304 |  |  | 167 |  |  | NTC correction
20251121 | November | 1030 | 8375 |  |  | 8375 |  |  | 5927 | 225 | 5703 | Minimum Margin | Minimum Margin | 0 | NA | 11181 |  |  | 168 |  |  | NTC correction
20251121 | November | 1130 | 8356 |  |  | 8140 |  |  | 5927 | 206 | 5937 | Minimum Margin | Minimum Margin | 216 | NA | 11668 |  |  | 168 |  |  | NTC correction
20251121 | November | 1230 |  | 7724 | 397 |  | 6308 | 397 | 4570 | 199 | 0 | Minimum Margin | Validation phase | NA | 1416 | -199 |  |  | 168 |  |  | NTC correction | 3337 | Process fail during TSO validation phase |  |  | 6191 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1330 |  | 7534 | 383 |  | 6016 | 324 | 4570 | 8 | 0 | Minimum Margin | Smoothing ramp | NA | 1577 | -8 | Smoothing | Smoothing ramp | 163 |  |  | NTC correction | 3338 | Process fail during TSO validation phase |  |  | 6090 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1430 |  | 7620 | 389 |  | 6149 | 204 | 4570 | 95 | 0 | Minimum Margin | Smoothing ramp | NA | 1656 | -95 | Smoothing | Smoothing ramp | 165 |  |  | NTC correction | 3338 | Process fail during TSO validation phase |  |  | 6136 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1530 |  | 7426 | 478 |  | 6751 | 129 | 6324 | 75 | 0 | Minimum Margin | Validation phase | NA | 1024 | -75 |  |  | 163 |  |  | NTC correction | 3337 | Process fail during TSO validation phase |  |  | 6850 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1630 |  | 7430 | 479 |  | 6755 | 129 | 6324 | 79 | 0 | Minimum Margin | Validation phase | NA | 1025 | -79 |  |  | 163 |  |  | NTC correction | 3337 | Process fail during TSO validation phase |  |  | 6850 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1730 |  | 7426 | 478 |  | 6751 | 129 | 6324 | 75 | 0 | Minimum Margin | Validation phase | NA | 1024 | -75 |  |  | 163 |  |  | NTC correction | 3337 | Process fail during TSO validation phase |  |  | 6850 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251121 | November | 1830 |  | 9459 | 925 |  | 8228 | 129 | -2406 | -2406 | 0 | Critical Branch | Critical Branch | NA | 2027 | 2406 |  |  | 98 | Reduction because NTC over thermal limit on border |  | NTC correction
20251121 | November | 1930 |  | 9572 | 1010 |  | 9537 | 462 | -2606 | -2606 | 0 | Critical Branch | Critical Branch | NA | 583 | 2606 |  |  | 217 | Reduction because NTC over thermal limit on border |  | NTC correction
20251121 | November | 2030 |  | 9572 | 1010 |  | 9572 | 764 | -2606 | -2606 | 0 | Critical Branch | Critical Branch | NA | 246 | 2606 |  |  | 217 | Reduction because NTC over thermal limit on border |  | NTC correction
20251121 | November | 2130 | 9252 |  |  | 9252 |  |  | -3914 | -3914 | -3913 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391 |  |  | NTC correction
20251121 | November | 2230 | 9252 |  |  | 9252 |  |  | -3914 | -3914 | -3913 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 391 |  |  | NTC correction
20251121 | November | 2330 | 8442 |  |  | 8442 |  |  | -3106 | -3106 | -3105 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 373 |  |  | NTC correction
20251122 | November | 0530 | 7852 |  |  | 7750 |  |  | 2947 | 172 | 2877 | Minimum Margin | Smoothing ramp | 102 | NA | 5582 | Smoothing | Smoothing ramp
20251122 | November | 0630 | 7905 |  |  | 6250 |  |  | 2947 | 225 | 4377 | Minimum Margin | Validation phase | 1655 | NA | 8529 | [7 empty] | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] |  |  | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 0730 | 10560 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 2810 | NA | 0 | Smoothing | Smoothing ramp |  |  | 8298 | D2CC failed. Correction of BackUp-values.
20251122 | November | 0830 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  |  |  | 8298 | D2CC failed. Correction of BackUp-values.
20251122 | November | 0930 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  |  |  | 8298 | D2CC failed. Correction of BackUp-values.
20251122 | November | 1030 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  |  |  | 8298 | D2CC failed. Correction of BackUp-values.
20251122 | November | 1130 | 10560 |  |  | 8548 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2012 | NA | 0 |  |  |  |  | 8298 | D2CC failed. Correction of BackUp-values.
20251122 | November | 1430 | 8390 |  |  | 7750 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Smoothing ramp | 640 | NA | 0 | Smoothing | Smoothing ramp
20251122 | November | 1530 | 8627 |  |  | 6250 |  |  | 3874 | 237 | 6014 | Minimum Margin | Validation phase | 2377 | NA | 11791 | [7 empty] | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] |  |  | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 1630 | 8413 |  |  | 6250 |  |  | 3874 | 23 | 6014 | Minimum Margin | Validation phase | 2163 | NA | 12005 | [10 empty] | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 1730 | 8390 |  |  | 6250 |  |  | 3874 | 0 | 6014 | TTC Selection - LTTC | Validation phase | 2140 | NA | 12028 | [10 empty] | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251122 | November | 1830 | 8390 |  |  | 7750 |  |  | -1374 | -1374 | -734 | TTC Selection - LTTC | Smoothing ramp | 640 | NA | 0 | Smoothing | Smoothing ramp
20251123 | November | 0030 | 9696 |  |  | 9696 |  |  | -4561 | -4561 | -4561 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251123 | November | 0130 | 9696 |  |  | 9696 |  |  | -4561 | -4561 | -4561 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251123 | November | 0230 | 9696 |  |  | 9696 |  |  | -4561 | -4561 | -4561 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 432
20251123 | November | 0330 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 424
20251123 | November | 0430 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 424
20251123 | November | 0530 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 424
20251123 | November | 0630 | 9525 |  |  | 9525 |  |  | -4328 | -4328 | -4327 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 424
20251123 | November | 0730 | 9606 |  |  | 9606 |  |  | -5566 | -5566 | -5566 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 428
20251123 | November | 0830 | 9606 |  |  | 9606 |  |  | -5566 | -5566 | -5566 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 428
20251123 | November | 0930 | 8594 |  |  | 8593 |  |  | -3313 | -3313 | -3312 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251123 | November | 1030 | 8594 |  |  | 8593 |  |  | -3313 | -3313 | -3312 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251123 | November | 1130 | 8594 |  |  | 8593 |  |  | -3313 | -3313 | -3312 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 380
20251123 | November | 1230 | 8960 |  |  | 8959 |  |  | -3453 | -3453 | -3452 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 397
20251123 | November | 1330 | 8960 |  |  | 8959 |  |  | -3453 | -3453 | -3452 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 397
20251123 | November | 1430 | 8960 |  |  | 8959 |  |  | -3453 | -3453 | -3452 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 397
20251123 | November | 1530 | 9885 |  |  | 9879 |  |  | -5655 | -5655 | -5649 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251123 | November | 1630 | 9885 |  |  | 9879 |  |  | -5655 | -5655 | -5649 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251123 | November | 1730 | 9885 |  |  | 9879 |  |  | -5655 | -5655 | -5649 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 435 | Reduction because NTC over thermal limit on border
20251123 | November | 1830 | 9619 |  |  | 9618 |  |  | -4856 | -4856 | -4855 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 428
20251123 | November | 1930 | 9619 |  |  | 9618 |  |  | -4856 | -4856 | -4855 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 428
20251123 | November | 2030 | 9619 |  |  | 9618 |  |  | -4856 | -4856 | -4855 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 428
20251123 | November | 2130 | 9428 |  |  | 9427 |  |  | -4382 | -4382 | -4381 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 419
20251123 | November | 2230 | 9428 |  |  | 9427 |  |  | -4382 | -4382 | -4381 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 419
20251123 | November | 2330 | 9428 |  |  | 9427 |  |  | -4382 | -4382 | -4381 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 419
20251124 | November | 0030 | 8667 |  |  | 8667 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0130 | 8667 |  |  | 8667 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0230 | 8667 |  |  | 8667 |  |  | -3275 | -3275 | -3275 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0330 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0430 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0530 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0630 | 8904 |  |  | 8904 |  |  | -1776 | -1776 | -1776 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  |  |  | 9000 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 4138 | Process failed: missing input
20251124 | November | 0730 | 9871 |  |  | 8864 |  |  | -4675 | -4675 | -3694 | Critical Branch | TTC Validation phase - bilateral reduction | 1007 | NA | 0 |  |  |  |  | 9810 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 0830 | 9871 |  |  | 8864 |  |  | -4675 | -4675 | -3694 | Critical Branch | TTC Validation phase - bilateral reduction | 1007 | NA | 0 |  |  |  |  | 9810 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 0930 | 9854 |  |  | 8210 |  |  | -4668 | -4668 | -3030 | Critical Branch | Validation phase | 1644 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 8512 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1030 | 9854 |  |  | 8210 |  |  | -4668 | -4668 | -3030 | Critical Branch | Validation phase | 1644 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 8512 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1130 | 9854 |  |  | 8210 |  |  | -4668 | -4668 | -3030 | Critical Branch | Validation phase | 1644 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 8512 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1230 | 9834 |  |  | 7498 |  |  | -2507 | -2507 | -174 | Critical Branch | Validation phase | 2336 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 7266 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1330 | 9834 |  |  | 7498 |  |  | -2507 | -2507 | -174 | Critical Branch | Validation phase | 2336 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 7266 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1430 | 9834 |  |  | 7498 |  |  | -2507 | -2507 | -174 | Critical Branch | Validation phase | 2336 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 7266 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1530 | 9250 |  |  | 7935 |  |  | -2337 | -2337 | -1066 | Critical Branch | Validation phase | 1315 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 8030 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1630 | 9250 |  |  | 7935 |  |  | -2337 | -2337 | -1066 | Critical Branch | Validation phase | 1315 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 8030 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1730 | 9250 |  |  | 7935 |  |  | -2337 | -2337 | -1066 | Critical Branch | Validation phase | 1315 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco |  |  | 8030 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20251124 | November | 1830 | 10321 |  |  | 8924 |  |  | -3403 | -3403 | -2228 | Critical Branch | Validation phase | 1397 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 1930 | 10321 |  |  | 8924 |  |  | -3403 | -3403 | -2228 | Critical Branch | Validation phase | 1397 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 2030 | 10321 |  |  | 8924 |  |  | -3403 | -3403 | -2228 | Critical Branch | Validation phase | 1397 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 2130 | 9007 |  |  | 8350 |  |  | -3519 | -3519 | -2871 | Critical Branch | TTC Validation phase - bilateral reduction | 657 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 2230 | 9007 |  |  | 8350 |  |  | -3519 | -3519 | -2871 | Critical Branch | TTC Validation phase - bilateral reduction | 657 | NA | 0 |  |  |  |  | 9760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251124 | November | 2330 | 8197 |  |  | 7720 |  |  | -2712 | -2712 | -2241 | Critical Branch | TTC Validation phase - bilateral reduction | 477 | NA | 0 |  |  |  |  | 8950 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | 2985 | Outage - Venaus - Piossasco
20251125 | November | 0030 | 8000 |  |  | 7612 |  |  | -4610 | -4610 | -4185 | Critical Branch | TTC Validation phase - bilateral reduction | 388 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0130 | 8000 |  |  | 7612 |  |  | -4610 | -4610 | -4185 | Critical Branch | TTC Validation phase - bilateral reduction | 388 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0230 | 8000 |  |  | 7612 |  |  | -4610 | -4610 | -4185 | Critical Branch | TTC Validation phase - bilateral reduction | 388 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0330 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 483 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0430 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 483 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0530 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 483 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0630 | 8210 |  |  | 7727 |  |  | -2608 | -2608 | -2126 | Critical Branch | TTC Validation phase - bilateral reduction | 483 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0730 |  | 8048 | 797 |  | 7331 | 797 | -5864 | -5864 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 717 | 5864 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0830 |  | 8048 | 797 |  | 7331 | 797 | -5864 | -5864 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 717 | 5864 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 0930 |  | 7809 | 757 |  | 7209 | 757 | -5444 | -5444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 600 | 5444 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1030 |  | 7809 | 757 |  | 7209 | 757 | -5444 | -5444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 600 | 5444 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1130 |  | 7809 | 757 |  | 7209 | 757 | -5444 | -5444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 600 | 5444 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1230 |  | 7557 | 699 |  | 7079 | 699 | -5409 | -5409 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 478 | 5409 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1330 |  | 7557 | 699 |  | 7079 | 491 | -5409 | -5409 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 686 | 5409 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1430 |  | 7557 | 699 |  | 7079 | 276 | -5409 | -5409 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 901 | 5409 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1530 |  | 8162 | 826 |  | 7390 | 60 | -5905 | -5905 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1538 | 5905 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1630 |  | 8162 | 826 |  | 7390 | 60 | -5905 | -5905 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1538 | 5905 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1730 |  | 8162 | 826 |  | 7390 | 60 | -5905 | -5905 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1538 | 5905 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1830 |  | 7809 | 757 |  | 7209 | 60 | -5360 | -5360 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1297 | 5360 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 1930 |  | 7809 | 757 |  | 7209 | 292 | -5360 | -5360 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1065 | 5360 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 2030 |  | 7809 | 757 |  | 7209 | 524 | -5360 | -5360 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 833 | 5360 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 2130 | 8340 |  |  | 7969 |  |  | -2754 | -2754 | -2387 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 371 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 2230 | 8340 |  |  | 7969 |  |  | -2754 | -2754 | -2387 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 371 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251125 | November | 2330 | 7530 |  |  | 7353 |  |  | -1949 | -1949 | -1774 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 177 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0030 | 8103 |  |  | 7517 |  |  | -3789 | -3789 | -3163 | Critical Branch | Validation phase | 586 | NA | 0 |  |  |  |  | 7678 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0130 | 8103 |  |  | 7517 |  |  | -3789 | -3789 | -3163 | Critical Branch | Validation phase | 586 | NA | 0 |  |  |  |  | 7678 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0230 | 8103 |  |  | 7517 |  |  | -3789 | -3789 | -3163 | Critical Branch | Validation phase | 586 | NA | 0 |  |  |  |  | 7678 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0330 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 526 | NA | 0 |  |  |  |  | 7687 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0430 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 526 | NA | 0 |  |  |  |  | 7687 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0530 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 526 | NA | 0 |  |  |  |  | 7687 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0630 | 8048 |  |  | 7522 |  |  | -3670 | -3670 | -3106 | Critical Branch | Validation phase | 526 | NA | 0 |  |  |  |  | 7687 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0730 | 8489 |  |  | 7994 |  |  | -5502 | -5502 | -4969 | Critical Branch | Validation phase | 495 | NA | 0 |  |  |  |  | 8225 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0830 | 8489 |  |  | 7994 |  |  | -5502 | -5502 | -4969 | Critical Branch | Validation phase | 495 | NA | 0 |  |  |  |  | 8225 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 0930 | 8307 |  |  | 7595 |  |  | 6778 | 177 | 7571 | Minimum Margin | Validation phase | 712 | NA | 14965 |  |  |  |  | 7554 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1030 | 8327 |  |  | 7595 |  |  | 6778 | 197 | 7571 | Minimum Margin | Validation phase | 732 | NA | 14945 |  |  |  |  | 7554 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1130 | 8327 |  |  | 7595 |  |  | 6778 | 197 | 7571 | Minimum Margin | Validation phase | 732 | NA | 14945 |  |  |  |  | 7554 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1230 | 8325 |  |  | 6250 |  |  | 5301 | 195 | 7181 | Minimum Margin | Validation phase | 2075 | NA | 14167 |  |  |  |  | 7313 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251126 | November | 1330 | 8325 |  |  | 6250 |  |  | 5301 | 195 | 7181 | Minimum Margin | Validation phase | 2075 | NA | 14167 |  |  |  |  | 7313 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251126 | November | 1430 | 8361 |  |  | 6250 |  |  | 5301 | 231 | 7181 | Minimum Margin | Validation phase | 2111 | NA | 14131 |  |  |  |  | 7313 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - PRAZ VILLARODIN |  |  | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered.
20251126 | November | 1530 | 8293 |  |  | 7750 |  |  | -962 | -962 | -405 | Critical Branch | TTC Validation phase - bilateral reduction | 543 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1630 | 8293 |  |  | 7871 |  |  | -962 | -962 | -525 | Critical Branch | TTC Validation phase - bilateral reduction | 422 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1730 | 8293 |  |  | 7871 |  |  | -962 | -962 | -525 | Critical Branch | TTC Validation phase - bilateral reduction | 422 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1830 | 8443 |  |  | 7955 |  |  | -1277 | -1277 | -773 | Critical Branch | TTC Validation phase - bilateral reduction | 488 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 1930 | 8443 |  |  | 7955 |  |  | -1277 | -1277 | -773 | Critical Branch | TTC Validation phase - bilateral reduction | 488 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 2030 | 8443 |  |  | 7955 |  |  | -1277 | -1277 | -773 | Critical Branch | TTC Validation phase - bilateral reduction | 488 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 2130 | 8195 |  |  | 7815 |  |  | -4213 | -4213 | -3805 | Critical Branch | TTC Validation phase - bilateral reduction | 380 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 2230 | 8195 |  |  | 7815 |  |  | -4213 | -4213 | -3805 | Critical Branch | TTC Validation phase - bilateral reduction | 380 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251126 | November | 2330 | 7385 |  |  | 7201 |  |  | -3415 | -3415 | -3218 | Critical Branch | TTC Validation phase - bilateral reduction | 184 | NA | 0 | [6 empty] | 2985 | Outage - PRAZ VILLARODIN
20251127 | November | 0030 | 8041 |  |  | 7540 |  |  | -3467 | -3467 | -2923 | Critical Branch | Validation phase | 501 | NA | 0 |  |  |  |  | 7764 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0130 | 8041 |  |  | 7540 |  |  | -3467 | -3467 | -2923 | Critical Branch | Validation phase | 501 | NA | 0 |  |  |  |  | 7764 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0230 | 8041 |  |  | 7540 |  |  | -3467 | -3467 | -2923 | Critical Branch | Validation phase | 501 | NA | 0 |  |  |  |  | 7764 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0330 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 497 | NA | 0 |  |  |  |  | 7780 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0430 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 497 | NA | 0 |  |  |  |  | 7780 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0530 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 497 | NA | 0 |  |  |  |  | 7780 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0630 | 8046 |  |  | 7549 |  |  | -3391 | -3391 | -2853 | Critical Branch | Validation phase | 497 | NA | 0 |  |  |  |  | 7780 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0730 | 8130 |  |  | 7779 |  |  | -4457 | -4457 | -4079 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 351 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0830 | 8130 |  |  | 7779 |  |  | -4457 | -4457 | -4079 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 351 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 0930 | 8193 |  |  | 7814 |  |  | -4262 | -4262 | -3858 | Critical Branch | TTC Validation phase - bilateral reduction | 379 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1030 | 8193 |  |  | 7814 |  |  | -4262 | -4262 | -3858 | Critical Branch | TTC Validation phase - bilateral reduction | 379 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1130 | 8193 |  |  | 7814 |  |  | -4262 | -4262 | -3858 | Critical Branch | TTC Validation phase - bilateral reduction | 379 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1230 | 8386 |  |  | 7665 |  |  | 2693 | 196 | 3504 | Minimum Margin | Validation phase | 721 | NA | 6812 |  |  |  |  | 7643 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1330 | 8386 |  |  | 7665 |  |  | 2693 | 196 | 3504 | Minimum Margin | Validation phase | 721 | NA | 6812 |  |  |  |  | 7643 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1430 | 8414 |  |  | 7665 |  |  | 2693 | 224 | 3504 | Minimum Margin | Validation phase | 749 | NA | 6784 |  |  |  |  | 7643 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1530 | 8190 |  |  | 7833 |  |  | -806 | -806 | -438 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 357 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1630 | 8190 |  |  | 7833 |  |  | -806 | -806 | -438 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 357 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1730 | 8190 |  |  | 7833 |  |  | -806 | -806 | -438 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 357 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1830 | 8190 |  |  | 7833 |  |  | -582 | -582 | -215 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 357 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 1930 | 8190 |  |  | 7833 |  |  | -582 | -582 | -215 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 357 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 2030 | 8190 |  |  | 7833 |  |  | -582 | -582 | -215 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 357 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 2130 | 8289 |  |  | 7889 |  |  | -3686 | -3686 | -3259 | Critical Branch | TTC Validation phase - bilateral reduction | 400 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 2230 | 8289 |  |  | 7889 |  |  | -3686 | -3686 | -3259 | Critical Branch | TTC Validation phase - bilateral reduction | 400 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251127 | November | 2330 | 7479 |  |  | 7273 |  |  | -2888 | -2888 | -2669 | Critical Branch | TTC Validation phase - bilateral reduction | 206 | NA | 0 | [6 empty] | 2985 | Outage - OUTAGE TD LA PRAZ
20251128 | November | 0030 | 7594 |  |  | 7335 |  |  | -2761 | -2761 | -2477 | Critical Branch | TTC Validation phase - bilateral reduction | 259 | NA | 0 |  |  | 223 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0130 | 7594 |  |  | 7335 |  |  | -2761 | -2761 | -2477 | Critical Branch | TTC Validation phase - bilateral reduction | 259 | NA | 0 |  |  | 223 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0230 | 7594 |  |  | 7335 |  |  | -2761 | -2761 | -2477 | Critical Branch | TTC Validation phase - bilateral reduction | 259 | NA | 0 |  |  | 223 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0330 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 297 | NA | 0 |  |  | 226 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0430 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 297 | NA | 0 |  |  | 226 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0530 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 297 | NA | 0 |  |  | 226 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0630 | 7678 |  |  | 7381 |  |  | -2746 | -2746 | -2426 | Critical Branch | TTC Validation phase - bilateral reduction | 297 | NA | 0 |  |  | 226 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0730 |  | 6832 | 680 |  | 6354 | 680 | -3571 | -3571 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 478 | 3571 |  |  | 113 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0830 |  | 6832 | 680 |  | 6354 | 680 | -3571 | -3571 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 478 | 3571 |  |  | 113 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 0930 | 7774 |  |  | 7280 |  |  | -3628 | -3628 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 494 | NA | 0 |  |  | 243 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1030 | 7774 |  |  | 7280 |  |  | -3628 | -3628 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 494 | NA | 0 |  |  | 243 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1130 | 7774 |  |  | 7280 |  |  | -3628 | -3628 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 494 | NA | 0 |  |  | 243 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1230 | 7817 |  |  | 7302 |  |  | -3894 | -3894 | -3352 | Critical Branch | TTC Validation phase - bilateral reduction | 515 | NA | 0 |  |  | 244 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1330 | 7817 |  |  | 7302 |  |  | -3894 | -3894 | -3352 | Critical Branch | TTC Validation phase - bilateral reduction | 515 | NA | 0 |  |  | 244 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1430 | 7817 |  |  | 7302 |  |  | -3894 | -3894 | -3352 | Critical Branch | TTC Validation phase - bilateral reduction | 515 | NA | 0 |  |  | 244 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1530 |  | 7527 | 801 |  | 6672 | 800 | -4485 | -4485 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 856 | 4485 |  |  | 126 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1630 |  | 7577 | 801 |  | 6719 | 800 | -4537 | -4537 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 859 | 4537 |  |  | 126 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1730 |  | 8474 | 801 |  | 7575 | 800 | -5473 | -5473 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 900 | 5473 |  |  | 128 |  |  |  | 2985 | Outage - Outage TD LA PRAZ
20251128 | November | 1830 |  | 9650 | 959 |  | 9043 | 940 | -2853 | -2853 | 0 | Critical Branch | Critical Branch | NA | 626 | 2853 |  |  | 147 | Reduction because NTC over thermal limit on border
20251128 | November | 1930 |  | 9650 | 959 |  | 9650 | 940 | -2853 | -2853 | 0 | Critical Branch | Critical Branch | NA | 19 | 2853 |  |  | 147 | Reduction because NTC over thermal limit on border
20251128 | November | 2030 |  | 9650 | 959 |  | 9650 | 940 | -2853 | -2853 | 0 | Critical Branch | Critical Branch | NA | 19 | 2853 |  |  | 147 | Reduction because NTC over thermal limit on border
20251128 | November | 2130 | 10240 |  |  | 9453 |  |  | -3059 | -3059 | -2272 | Critical Branch | Validation phase | 787 | NA | 0 |  |  | 294 |  | 9203 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251128 | November | 2230 | 10240 |  |  | 9453 |  |  | -3059 | -3059 | -2272 | Critical Branch | Validation phase | 787 | NA | 0 |  |  | 294 |  | 9203 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251128 | November | 2330 | 9430 |  |  | 8643 |  |  | -2244 | -2244 | -1457 | Critical Branch | Validation phase | 787 | NA | 0 |  |  | 279 |  | 8393 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251129 | November | 0730 | 8240 |  |  | 8174 |  |  | -3443 | -3443 | -3377 | TTC Selection - LTTC | Validation phase | 66 | NA | 0 |  |  |  |  | 7924 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 0830 | 8240 |  |  | 8174 |  |  | -3443 | -3443 | -3377 | TTC Selection - LTTC | Validation phase | 66 | NA | 0 |  |  |  |  | 7924 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 0930 | 8240 |  |  | 8208 |  |  | -3613 | -3613 | -3581 | TTC Selection - LTTC | Validation phase | 32 | NA | 0 |  |  |  |  | 7958 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1030 | 8240 |  |  | 8208 |  |  | -3613 | -3613 | -3581 | TTC Selection - LTTC | Validation phase | 32 | NA | 0 |  |  |  |  | 7958 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1130 | 8240 |  |  | 8208 |  |  | -3613 | -3613 | -3581 | TTC Selection - LTTC | Validation phase | 32 | NA | 0 |  |  |  |  | 7958 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1230 | 8240 |  |  | 8053 |  |  | -3532 | -3532 | -3345 | TTC Selection - LTTC | Validation phase | 187 | NA | 0 |  |  |  |  | 7803 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1330 | 8240 |  |  | 8053 |  |  | -3532 | -3532 | -3345 | TTC Selection - LTTC | Validation phase | 187 | NA | 0 |  |  |  |  | 7803 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 1430 | 8240 |  |  | 8053 |  |  | -3532 | -3532 | -3345 | TTC Selection - LTTC | Validation phase | 187 | NA | 0 |  |  |  |  | 7803 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 2130 | 8240 |  |  | 8163 |  |  | -3279 | -3279 | -3202 | TTC Selection - LTTC | Validation phase | 77 | NA | 0 |  |  |  |  | 7913 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 2230 | 8240 |  |  | 8163 |  |  | -3279 | -3279 | -3202 | TTC Selection - LTTC | Validation phase | 77 | NA | 0 |  |  |  |  | 7913 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251129 | November | 2330 | 7430 |  |  | 7353 |  |  | -2483 | -2483 | -2406 | TTC Selection - LTTC | Validation phase | 77 | NA | 0 |  |  |  |  | 7103 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251130 | November | 0030 | 10606 |  |  | 9589 |  |  | -3671 | -3671 | -2654 | Critical Branch | Validation phase | 1017 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9339 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0130 | 10606 |  |  | 9589 |  |  | -3671 | -3671 | -2654 | Critical Branch | Validation phase | 1017 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9339 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0230 | 10606 |  |  | 9589 |  |  | -3671 | -3671 | -2654 | Critical Branch | Validation phase | 1017 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9339 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0330 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 1145 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9192 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0430 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 1145 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9192 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0530 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 1145 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9192 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0630 | 10587 |  |  | 9442 |  |  | -2257 | -2257 | -1112 | Critical Branch | Validation phase | 1145 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9192 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0730 | 10587 |  |  | 9600 |  |  | -2438 | -2438 | -1451 | Critical Branch | Validation phase | 987 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9350 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0830 | 10587 |  |  | 9600 |  |  | -2438 | -2438 | -1451 | Critical Branch | Validation phase | 987 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9350 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 0930 | 10443 |  |  | 9592 |  |  | -2134 | -2134 | -1283 | Critical Branch | Validation phase | 851 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9342 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 1030 | 10443 |  |  | 9592 |  |  | -2134 | -2134 | -1283 | Critical Branch | Validation phase | 851 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9342 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 1130 | 10443 |  |  | 9592 |  |  | -2134 | -2134 | -1283 | Critical Branch | Validation phase | 851 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9342 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 1230 | 10380 |  |  | 9451 |  |  | -2017 | -2017 | -1088 | Critical Branch | Validation phase | 929 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9201 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251130 | November | 1330 | 10380 |  |  | 9451 |  |  | -2017 | -2017 | -1088 | Critical Branch | Validation phase | 929 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9201 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251130 | November | 1430 | 10380 |  |  | 9451 |  |  | -2017 | -2017 | -1088 | Critical Branch | Validation phase | 929 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9201 | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
20251130 | November | 1530 |  | 9244 | 860 |  | 9233 | 860 | -3752 | -3752 | 0 | Critical Branch | Critical Branch | NA | 11 | 3752 |  |  | 285 | Reduction because NTC over thermal limit on border
20251130 | November | 1630 |  | 9244 | 860 |  | 9233 | 860 | -3752 | -3752 | 0 | Critical Branch | Critical Branch | NA | 11 | 3752 |  |  | 285 | Reduction because NTC over thermal limit on border
20251130 | November | 1730 |  | 9244 | 860 |  | 9233 | 860 | -3752 | -3752 | 0 | Critical Branch | Critical Branch | NA | 11 | 3752 |  |  | 285 | Reduction because NTC over thermal limit on border
20251130 | November | 1830 | 10511 |  |  | 9940 |  |  | -4416 | -4416 | -3849 | Critical Branch | Validation phase | 571 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9701 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 1930 | 10511 |  |  | 9940 |  |  | -4416 | -4416 | -3849 | Critical Branch | Validation phase | 571 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9701 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 2030 | 10511 |  |  | 9940 |  |  | -4416 | -4416 | -3849 | Critical Branch | Validation phase | 571 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9701 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251130 | November | 2130 | 10745 |  |  | 10032 |  |  | -3780 | -3780 | -3072 | Critical Branch | Validation phase | 713 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9796 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 2230 | 10745 |  |  | 10032 |  |  | -3780 | -3780 | -3072 | Critical Branch | Validation phase | 713 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9796 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251130 | November | 2330 | 10745 |  |  | 10032 |  |  | -3780 | -3780 | -3072 | Critical Branch | Validation phase | 713 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9796 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0030 | 10348 |  |  | 9748 |  |  | -5299 | -5299 | -4701 | Critical Branch | Validation phase | 600 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9503 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0130 | 10348 |  |  | 9748 |  |  | -5299 | -5299 | -4701 | Critical Branch | Validation phase | 600 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9503 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0230 | 10348 |  |  | 9748 |  |  | -5299 | -5299 | -4701 | Critical Branch | Validation phase | 600 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9503 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0330 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 452 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9655 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0430 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 452 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9655 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0530 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 452 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9655 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0630 | 10347 |  |  | 9895 |  |  | -4983 | -4983 | -4534 | Critical Branch | Validation phase | 452 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9655 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251201 | December | 0730 |  | 9503 | 894 |  | 9503 | 884 | -2676 | -2676 | 0 | Critical Branch | Critical Branch | NA | 10 | 2676 |  |  | 144 | Reduction because NTC over thermal limit on border
20251201 | December | 0830 |  | 9503 | 894 |  | 9503 | 884 | -2676 | -2676 | 0 | Critical Branch | Critical Branch | NA | 10 | 2676 |  |  | 144 | Reduction because NTC over thermal limit on border
20251201 | December | 0930 | 9515 |  |  | 9490 |  |  | -2277 | -2277 | -2252 | Critical Branch | Validation phase | 25 | NA | 0 |  |  | 272 |  | 9240 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251201 | December | 1030 | 9515 |  |  | 9490 |  |  | -2277 | -2277 | -2252 | Critical Branch | Validation phase | 25 | NA | 0 |  |  | 272 |  | 9240 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251201 | December | 1130 | 9515 |  |  | 9490 |  |  | -2277 | -2277 | -2252 | Critical Branch | Validation phase | 25 | NA | 0 |  |  | 272 |  | 9240 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251201 | December | 1230 |  | 8932 | 862 |  | 8932 | 856 | -2009 | -2009 | 0 | Critical Branch | Critical Branch | NA | 6 | 2009 |  |  | 135 | Reduction because NTC over thermal limit on border
20251201 | December | 1330 |  | 8932 | 862 |  | 8932 | 856 | -2009 | -2009 | 0 | Critical Branch | Critical Branch | NA | 6 | 2009 |  |  | 135 | Reduction because NTC over thermal limit on border
20251201 | December | 1430 |  | 8932 | 862 |  | 8932 | 856 | -2009 | -2009 | 0 | Critical Branch | Critical Branch | NA | 6 | 2009 |  |  | 135 | Reduction because NTC over thermal limit on border
20251201 | December | 1530 |  | 9591 | 921 |  | 9591 | 907 | -2774 | -2774 | 0 | Critical Branch | Critical Branch | NA | 14 | 2774 |  |  | 146 | Reduction because NTC over thermal limit on border
20251201 | December | 1630 |  | 9591 | 921 |  | 9591 | 907 | -2774 | -2774 | 0 | Critical Branch | Critical Branch | NA | 14 | 2774 |  |  | 146 | Reduction because NTC over thermal limit on border
20251201 | December | 1730 |  | 9591 | 921 |  | 9591 | 907 | -2774 | -2774 | 0 | Critical Branch | Critical Branch | NA | 14 | 2774 |  |  | 146 | Reduction because NTC over thermal limit on border
20251201 | December | 1830 |  | 9618 | 916 |  | 9618 | 903 | -5196 | -5196 | 0 | Critical Branch | Critical Branch | NA | 13 | 5196 |  |  | 146 | Reduction because NTC over thermal limit on border
20251201 | December | 1930 |  | 9618 | 916 |  | 9618 | 903 | -5196 | -5196 | 0 | Critical Branch | Critical Branch | NA | 13 | 5196 |  |  | 146 | Reduction because NTC over thermal limit on border
20251201 | December | 2030 |  | 9618 | 916 |  | 9618 | 903 | -5196 | -5196 | 0 | Critical Branch | Critical Branch | NA | 13 | 5196 |  |  | 146 | Reduction because NTC over thermal limit on border
20251201 | December | 2130 | 10064 |  |  | 9480 |  |  | -3921 | -3921 | -3337 | Critical Branch | Validation phase | 584 | NA | 0 |  |  | 289 |  | 9230 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251201 | December | 2230 | 10064 |  |  | 9480 |  |  | -3921 | -3921 | -3337 | Critical Branch | Validation phase | 584 | NA | 0 |  |  | 289 |  | 9230 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251201 | December | 2330 | 9254 |  |  | 8670 |  |  | -3105 | -3105 | -2521 | Critical Branch | Validation phase | 584 | NA | 0 |  |  | 274 |  | 8420 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251202 | December | 0030 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0130 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0230 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0330 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0430 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0530 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0630 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251202 | December | 0730 |  | 9772 | 921 |  | 9772 | 907 | -4840 | -4840 | 0 | Critical Branch | Critical Branch | NA | 14 | 4840 |  |  | 149 | Reduction because NTC over thermal limit on border
20251202 | December | 0830 |  | 9772 | 921 |  | 9772 | 907 | -4840 | -4840 | 0 | Critical Branch | Critical Branch | NA | 14 | 4840 |  |  | 149 | Reduction because NTC over thermal limit on border
20251202 | December | 0930 |  | 9270 | 932 |  | 9270 | 916 | -2190 | -2190 | 0 | Critical Branch | Critical Branch | NA | 16 | 2190 |  |  | 141 | Reduction because NTC over thermal limit on border
20251202 | December | 1030 |  | 9270 | 932 |  | 9270 | 916 | -2190 | -2190 | 0 | Critical Branch | Critical Branch | NA | 16 | 2190 |  |  | 141 | Reduction because NTC over thermal limit on border
20251202 | December | 1130 |  | 9270 | 932 |  | 9270 | 916 | -2190 | -2190 | 0 | Critical Branch | Critical Branch | NA | 16 | 2190 |  |  | 141 | Reduction because NTC over thermal limit on border
20251202 | December | 1230 |  | 9375 | 921 |  | 9375 | 907 | -5385 | -5385 | 0 | Critical Branch | Critical Branch | NA | 14 | 5385 |  |  | 142 | Reduction because NTC over thermal limit on border
20251202 | December | 1330 |  | 9375 | 921 |  | 9375 | 907 | -5385 | -5385 | 0 | Critical Branch | Critical Branch | NA | 14 | 5385 |  |  | 142 | Reduction because NTC over thermal limit on border
20251202 | December | 1430 |  | 9375 | 921 |  | 9375 | 907 | -5385 | -5385 | 0 | Critical Branch | Critical Branch | NA | 14 | 5385 |  |  | 142 | Reduction because NTC over thermal limit on border
20251202 | December | 1530 |  | 9383 | 872 |  | 9383 | 865 | -3015 | -3015 | 0 | Critical Branch | Critical Branch | NA | 7 | 3015 |  |  | 142 | Reduction because NTC over thermal limit on border
20251202 | December | 1630 |  | 9383 | 872 |  | 9383 | 865 | -3015 | -3015 | 0 | Critical Branch | Critical Branch | NA | 7 | 3015 |  |  | 142 | Reduction because NTC over thermal limit on border
20251202 | December | 1730 |  | 9383 | 872 |  | 9383 | 865 | -3015 | -3015 | 0 | Critical Branch | Critical Branch | NA | 7 | 3015 |  |  | 142 | Reduction because NTC over thermal limit on border
20251202 | December | 1830 |  | 9669 | 902 |  | 9669 | 890 | 3734 | 34 | 0 | Minimum Margin | Minimum Margin | NA | 12 | -34 |  |  | 146 | Reduction because NTC over thermal limit on border
20251202 | December | 1930 |  | 9669 | 902 |  | 9669 | 890 | 3734 | 34 | 0 | Minimum Margin | Minimum Margin | NA | 12 | -34 |  |  | 146 | Reduction because NTC over thermal limit on border
20251202 | December | 2030 |  | 9669 | 902 |  | 9669 | 890 | 3734 | 34 | 0 | Minimum Margin | Minimum Margin | NA | 12 | -34 |  |  | 146 | Reduction because NTC over thermal limit on border
20251202 | December | 2130 | 10100 |  |  | 9787 |  |  | -2886 | -2886 | -2573 | Critical Branch | Validation phase | 313 | NA | 0 |  |  | 290 |  | 9537 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251202 | December | 2230 | 10100 |  |  | 9787 |  |  | -2886 | -2886 | -2573 | Critical Branch | Validation phase | 313 | NA | 0 |  |  | 290 |  | 9537 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251202 | December | 2330 | 9290 |  |  | 8977 |  |  | -2061 | -2061 | -1748 | Critical Branch | Validation phase | 313 | NA | 0 |  |  | 275 |  | 8727 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0030 | 9978 |  |  | 9156 |  |  | -2506 | -2506 | -1684 | Critical Branch | Validation phase | 822 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8906 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0130 | 9978 |  |  | 9156 |  |  | -2506 | -2506 | -1684 | Critical Branch | Validation phase | 822 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8906 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0230 | 9978 |  |  | 9156 |  |  | -2506 | -2506 | -1684 | Critical Branch | Validation phase | 822 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8906 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0330 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 622 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8990 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0430 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 622 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8990 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0530 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 622 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8990 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0630 | 9862 |  |  | 9240 |  |  | -2122 | -2122 | -1500 | Critical Branch | Validation phase | 622 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8990 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251203 | December | 0730 |  | 9335 | 878 |  | 9335 | 870 | -3386 | -3386 | 0 | Critical Branch | Critical Branch | NA | 8 | 3386 |  |  | 142 | Reduction because NTC over thermal limit on border
20251203 | December | 0830 |  | 9335 | 878 |  | 9335 | 870 | -3386 | -3386 | 0 | Critical Branch | Critical Branch | NA | 8 | 3386 |  |  | 142 | Reduction because NTC over thermal limit on border
20251203 | December | 0930 |  | 9678 | 899 |  | 9678 | 888 | -3466 | -3466 | 0 | Critical Branch | Critical Branch | NA | 11 | 3466 |  |  | 147 | Reduction because NTC over thermal limit on border
20251203 | December | 1030 |  | 9678 | 899 |  | 9678 | 888 | -3466 | -3466 | 0 | Critical Branch | Critical Branch | NA | 11 | 3466 |  |  | 147 | Reduction because NTC over thermal limit on border
20251203 | December | 1130 |  | 9678 | 899 |  | 9678 | 888 | -3466 | -3466 | 0 | Critical Branch | Critical Branch | NA | 11 | 3466 |  |  | 147 | Reduction because NTC over thermal limit on border
20251203 | December | 1230 |  | 9421 | 883 |  | 9421 | 874 | -2923 | -2923 | 0 | Critical Branch | Critical Branch | NA | 9 | 2923 |  |  | 143 | Reduction because NTC over thermal limit on border
20251203 | December | 1330 |  | 9421 | 883 |  | 9421 | 863 | -2923 | -2923 | 0 | Critical Branch | Critical Branch | NA | 20 | 2923 |  |  | 143 | Reduction because NTC over thermal limit on border
20251203 | December | 1430 |  | 9421 | 883 |  | 9421 | 593 | -2923 | -2923 | 0 | Critical Branch | Critical Branch | NA | 290 | 2923 |  |  | 143 | Reduction because NTC over thermal limit on border
20251203 | December | 1530 |  | 9683 | 864 |  | 9682 | 317 | 4105 | 150 | 0 | Minimum Margin | Minimum Margin | NA | 548 | -150 |  |  | 145 | Reduction because NTC over thermal limit on border
20251203 | December | 1630 |  | 9683 | 864 |  | 9683 | 53 | 4105 | 151 | 0 | Minimum Margin | Minimum Margin | NA | 811 | -151 |  |  | 145 | Reduction because NTC over thermal limit on border
20251203 | December | 1730 |  | 9567 | 854 |  | 9567 | 53 | 4105 | 35 | 0 | Minimum Margin | Minimum Margin | NA | 801 | -35 |  |  | 145 | Reduction because NTC over thermal limit on border
20251203 | December | 1830 |  | 9090 | 794 |  | 9090 | 53 | 4757 | 35 | 0 | Minimum Margin | Minimum Margin | NA | 741 | -35 |  |  | 137
20251203 | December | 1930 |  | 9090 | 794 |  | 9090 | 53 | 4757 | 35 | 0 | Minimum Margin | Minimum Margin | NA | 741 | -35 |  |  | 137
20251203 | December | 2030 |  | 9090 | 794 |  | 9090 | 297 | 4757 | 35 | 0 | Minimum Margin | Minimum Margin | NA | 497 | -35 |  |  | 137
20251203 | December | 2130 | 10485 |  |  | 9798 |  |  | -4258 | -4258 | -3571 | Critical Branch | Smoothing ramp | 687 | NA | 0 | Smoothing | Smoothing ramp | 300 | Reduction because NTC over thermal limit on border | 9548 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251203 | December | 2230 | 10485 |  |  | 9798 |  |  | -4258 | -4258 | -3571 | Critical Branch | Smoothing ramp | 687 | NA | 0 | Smoothing | Smoothing ramp | 300 | Reduction because NTC over thermal limit on border | 9548 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251203 | December | 2330 | 9675 |  |  | 8988 |  |  | -3445 | -3445 | -2758 | Critical Branch | Validation phase | 687 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8738 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 0030 | 10195 |  |  | 9344 |  |  | -2784 | -2784 | -1933 | Critical Branch | Validation phase | 851 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9094 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0130 | 10195 |  |  | 9344 |  |  | -2784 | -2784 | -1933 | Critical Branch | Validation phase | 851 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9094 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0230 | 10195 |  |  | 9344 |  |  | -2784 | -2784 | -1933 | Critical Branch | Validation phase | 851 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9094 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0330 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 659 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9018 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0430 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 659 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9018 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0530 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 659 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9018 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0630 | 9927 |  |  | 9268 |  |  | -2290 | -2290 | -1631 | Critical Branch | Validation phase | 659 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9018 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 0730 |  | 10333 | 113 |  | 9900 | 108 | -3002 | -3002 | 0 | Critical Branch | Validation phase | NA | 438 | 3002 |  |  | 151 |  | 9967 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 0830 |  | 10333 | 113 |  | 9900 | 108 | -3002 | -3002 | 0 | Critical Branch | Validation phase | NA | 438 | 3002 |  |  | 151 |  | 9967 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 0930 | 10412 |  |  | 9539 |  |  | -6110 | -6110 | -5237 | Critical Branch | Validation phase | 873 | NA | 0 |  |  | 300 |  | 9289 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251204 | December | 1030 | 10412 |  |  | 9539 |  |  | -6110 | -6110 | -5237 | Critical Branch | Validation phase | 873 | NA | 0 |  |  | 300 |  | 9289 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251204 | December | 1130 | 10412 |  |  | 9539 |  |  | -6110 | -6110 | -5237 | Critical Branch | Validation phase | 873 | NA | 0 |  |  | 300 |  | 9289 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251204 | December | 1230 |  | 10078 | 112 |  | 9397 | 105 | -3079 | -3079 | 0 | Critical Branch | Validation phase | NA | 688 | 3079 |  |  | 147 |  | 9457 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 1330 |  | 10078 | 112 |  | 9397 | 105 | -3079 | -3079 | 0 | Critical Branch | Validation phase | NA | 688 | 3079 |  |  | 147 |  | 9457 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 1430 |  | 10078 | 112 |  | 9397 | 105 | -3079 | -3079 | 0 | Critical Branch | Validation phase | NA | 688 | 3079 |  |  | 147 |  | 9457 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251204 | December | 1530 | 10515 |  |  | 9458 |  |  | -4513 | -4513 | -3456 | Critical Branch | Validation phase | 1057 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border | 9208 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1630 | 10515 |  |  | 9458 |  |  | -4513 | -4513 | -3456 | Critical Branch | Validation phase | 1057 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border | 9208 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1730 | 10515 |  |  | 9458 |  |  | -4513 | -4513 | -3456 | Critical Branch | Validation phase | 1057 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border | 9208 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1830 | 10260 |  |  | 9965 |  |  | -1750 | -1750 | -1455 | Critical Branch | Validation phase | 295 | NA | 0 |  |  | 295 |  | 9715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 1930 | 10260 |  |  | 9965 |  |  | -1750 | -1750 | -1455 | Critical Branch | Validation phase | 295 | NA | 0 |  |  | 295 |  | 9715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2030 | 10260 |  |  | 9965 |  |  | -1750 | -1750 | -1455 | Critical Branch | Validation phase | 295 | NA | 0 |  |  | 295 |  | 9715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2130 | 10002 |  |  | 9285 |  |  | -2548 | -2548 | -1831 | Critical Branch | Validation phase | 717 | NA | 0 |  |  | 287 |  | 9035 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2230 | 10002 |  |  | 9285 |  |  | -2548 | -2548 | -1831 | Critical Branch | Validation phase | 717 | NA | 0 |  |  | 287 |  | 9035 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251204 | December | 2330 | 9192 |  |  | 8475 |  |  | -1724 | -1724 | -1007 | Critical Branch | Validation phase | 717 | NA | 0 |  |  | 272 |  | 8225 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0030 | 10681 |  |  | 10170 |  |  | -2440 | -2440 | -1929 | Critical Branch | Validation phase | 511 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9938 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251205 | December | 0130 | 10681 |  |  | 10170 |  |  | -2440 | -2440 | -1929 | Critical Branch | Validation phase | 511 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9938 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251205 | December | 0230 | 10681 |  |  | 10170 |  |  | -2440 | -2440 | -1929 | Critical Branch | Validation phase | 511 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9938 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251205 | December | 0330 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Validation phase | 512 | NA | 0 |  |  | 283 |  | 8782 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0430 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Validation phase | 512 | NA | 0 |  |  | 283 |  | 8782 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0530 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Smoothing ramp | 512 | NA | 0 | Smoothing | Smoothing ramp | 283 |  | 8782 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0630 | 9544 |  |  | 9032 |  |  | -1637 | -1637 | -1125 | Critical Branch | Smoothing ramp | 512 | NA | 0 | Smoothing | Smoothing ramp | 283 |  | 8782 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 0730 |  | 9537 | 878 |  | 9537 | 322 | -5650 | -5650 | 0 | Critical Branch | Critical Branch | NA | 556 | 5650 |  |  | 145 | Reduction because NTC over thermal limit on border
20251205 | December | 0830 |  | 9537 | 878 |  | 8441 | 53 | -5650 | -5650 | 0 | Critical Branch | Critical Branch | NA | 1921 | 5650 |  |  | 145 | Reduction because NTC over thermal limit on border
20251205 | December | 0930 |  | 7794 | 673 |  | 6943 | 53 | -1282 | -1282 | 0 | Critical Branch | Validation phase | NA | 1471 | 1282 |  |  | 254 |  | 7639 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1030 |  | 7794 | 673 |  | 6943 | 53 | -1282 | -1282 | 0 | Critical Branch | Validation phase | NA | 1471 | 1282 |  |  | 254 |  | 7639 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1130 |  | 7794 | 673 |  | 6943 | 241 | -1282 | -1282 | 0 | Critical Branch | Smoothing ramp | NA | 1283 | 1282 | Smoothing | Smoothing ramp | 254 |  | 7639 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1230 |  | 9482 | 818 |  | 8316 | 499 | -3897 | -3897 | 0 | Critical Branch | Smoothing ramp | NA | 1485 | 3897 | Smoothing | Smoothing ramp | 166 |  | 8821 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1330 |  | 9482 | 818 |  | 8316 | 717 | -3897 | -3897 | 0 | Critical Branch | Validation phase | NA | 1267 | 3897 |  |  | 166 |  | 8821 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1430 |  | 9482 | 818 |  | 8316 | 499 | -3897 | -3897 | 0 | Critical Branch | Smoothing ramp | NA | 1485 | 3897 | Smoothing | Smoothing ramp | 166 |  | 8821 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1530 |  | 9210 | 835 |  | 8571 | 295 | -3169 | -3169 | 0 | Critical Branch | Validation phase | NA | 1179 | 3169 |  |  | 140 | Reduction because NTC over thermal limit on border | 9158 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1630 |  | 9210 | 835 |  | 8571 | 53 | -3169 | -3169 | 0 | Critical Branch | Validation phase | NA | 1421 | 3169 |  |  | 140 | Reduction because NTC over thermal limit on border | 9158 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1730 |  | 9210 | 835 |  | 8571 | 53 | -3169 | -3169 | 0 | Critical Branch | Validation phase | NA | 1421 | 3169 |  |  | 140 | Reduction because NTC over thermal limit on border | 9158 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
20251205 | December | 1830 |  | 9032 | 650 |  | 9031 | 38 | -6266 | -6266 | 0 | Critical Branch | Critical Branch | NA | 613 | 6266 |  |  | 280
20251205 | December | 1930 |  | 9032 | 650 |  | 9031 | 241 | -6266 | -6266 | 0 | Critical Branch | Critical Branch | NA | 410 | 6266 |  |  | 280
20251205 | December | 2030 |  | 9032 | 650 |  | 9031 | 444 | -6266 | -6266 | 0 | Critical Branch | Critical Branch | NA | 207 | 6266 |  |  | 280
20251205 | December | 2130 | 9740 |  |  | 8894 |  |  | -2646 | -2646 | -1800 | Critical Branch | Smoothing ramp | 846 | NA | 0 | Smoothing | Smoothing ramp | 279 |  | 8644 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 2230 | 9740 |  |  | 8894 |  |  | -2646 | -2646 | -1800 | Critical Branch | Validation phase | 846 | NA | 0 |  |  | 279 |  | 8644 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251205 | December | 2330 | 8930 |  |  | 8084 |  |  | -1826 | -1826 | -980 | Critical Branch | Validation phase | 846 | NA | 0 |  |  | 264 |  | 7834 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0030 | 10488 |  |  | 9686 |  |  | -2472 | -2472 | -1670 | Critical Branch | Validation phase | 802 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9439 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0130 | 10488 |  |  | 9686 |  |  | -2472 | -2472 | -1670 | Critical Branch | Validation phase | 802 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9439 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0230 | 10488 |  |  | 9686 |  |  | -2472 | -2472 | -1670 | Critical Branch | Validation phase | 802 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9439 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0330 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251206 | December | 0430 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251206 | December | 0530 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251206 | December | 0630 | 10013 |  |  | 10000 |  |  | -2882 | -2882 | -2869 | Critical Branch | Critical Branch | 13 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251206 | December | 0730 | 9539 |  |  | 9523 |  |  | -5922 | -5922 | -5906 | Critical Branch | Validation phase | 16 | NA | 0 |  |  | 297 |  | 9273 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0830 | 9539 |  |  | 9523 |  |  | -5922 | -5922 | -5906 | Critical Branch | Validation phase | 16 | NA | 0 |  |  | 297 |  | 9273 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251206 | December | 0930 | 9659 |  |  | 9657 |  |  | -5822 | -5822 | -5821 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border
20251206 | December | 1030 | 9659 |  |  | 9657 |  |  | -5822 | -5822 | -5821 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border
20251206 | December | 1130 | 9659 |  |  | 9657 |  |  | -5822 | -5822 | -5821 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border
20251206 | December | 1230 |  | 9186 | 832 |  | 9173 | 832 | -5086 | -5086 | 0 | Critical Branch | Critical Branch | NA | 13 | 5086 |  |  | 300 | Reduction because NTC over thermal limit on border
20251206 | December | 1330 |  | 9186 | 832 |  | 9173 | 832 | -5086 | -5086 | 0 | Critical Branch | Critical Branch | NA | 13 | 5086 |  |  | 300 | Reduction because NTC over thermal limit on border
20251206 | December | 1430 |  | 9186 | 832 |  | 9173 | 832 | -5086 | -5086 | 0 | Critical Branch | Critical Branch | NA | 13 | 5086 |  |  | 300 | Reduction because NTC over thermal limit on border
20251206 | December | 1530 | 9581 |  |  | 9581 |  |  | -5348 | -5348 | -5348 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 299
20251206 | December | 1630 | 9581 |  |  | 9581 |  |  | -5348 | -5348 | -5348 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 299
20251206 | December | 1730 | 10381 |  |  | 10381 |  |  | -6195 | -6195 | -6195 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 299
20251206 | December | 1830 | 10410 |  |  | 10410 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 300
20251206 | December | 1930 | 10410 |  |  | 10410 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 300
20251206 | December | 2030 | 10410 |  |  | 10410 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 300
20251206 | December | 2130 | 10403 |  |  | 9890 |  |  | -3075 | -3075 | -2562 | Critical Branch | Validation phase | 513 | NA | 0 |  |  | 299 |  | 9640 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251206 | December | 2230 | 10403 |  |  | 9890 |  |  | -3075 | -3075 | -2562 | Critical Branch | Validation phase | 513 | NA | 0 |  |  | 299 |  | 9640 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251206 | December | 2330 | 9593 |  |  | 9080 |  |  | -2232 | -2232 | -1719 | Critical Branch | Validation phase | 513 | NA | 0 |  |  | 284 |  | 8830 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0030 | 9682 |  |  | 9151 |  |  | -2941 | -2941 | -2410 | Critical Branch | Validation phase | 531 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8901 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0130 | 9682 |  |  | 9151 |  |  | -2941 | -2941 | -2410 | Critical Branch | Validation phase | 531 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8901 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0230 | 9682 |  |  | 9151 |  |  | -2941 | -2941 | -2410 | Critical Branch | Validation phase | 531 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 8901 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251207 | December | 0330 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 146 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9619 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0430 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 146 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9619 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0530 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 146 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9619 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0630 | 10007 |  |  | 9861 |  |  | -2377 | -2377 | -2231 | Critical Branch | Validation phase | 146 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9619 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0730 | 10479 |  |  | 10234 |  |  | -2837 | -2837 | -2595 | Critical Branch | Validation phase | 245 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 10005 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0830 | 10479 |  |  | 10234 |  |  | -2837 | -2837 | -2595 | Critical Branch | Validation phase | 245 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 10005 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251207 | December | 0930 | 10416 |  |  | 10390 |  |  | -2641 | -2641 | -2618 | Critical Branch | Critical Branch | 26 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251207 | December | 1030 | 10416 |  |  | 10390 |  |  | -2641 | -2641 | -2618 | Critical Branch | Critical Branch | 26 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251207 | December | 1130 | 10416 |  |  | 10390 |  |  | -2641 | -2641 | -2618 | Critical Branch | Critical Branch | 26 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251207 | December | 1230 | 10132 |  |  | 10115 |  |  | -2994 | -2994 | -2978 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251207 | December | 1330 | 10132 |  |  | 10115 |  |  | -2994 | -2994 | -2978 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251207 | December | 1430 | 10132 |  |  | 10115 |  |  | -2994 | -2994 | -2978 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251207 | December | 1530 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251207 | December | 1630 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251207 | December | 1730 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251207 | December | 1830 | 10028 |  |  | 9389 |  |  | -3354 | -3354 | -2715 | Critical Branch | Validation phase | 639 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9139 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251207 | December | 1930 | 10028 |  |  | 9389 |  |  | -3354 | -3354 | -2715 | Critical Branch | Validation phase | 639 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9139 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251207 | December | 2030 | 10028 |  |  | 9389 |  |  | -3354 | -3354 | -2715 | Critical Branch | Validation phase | 639 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9139 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251207 | December | 2130 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251207 | December | 2230 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251207 | December | 2330 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251208 | December | 0030 | 10403 |  |  | 10092 |  |  | -4964 | -4964 | -4659 | Critical Branch | Validation phase | 311 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9858 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251208 | December | 0130 | 10403 |  |  | 10092 |  |  | -4964 | -4964 | -4659 | Critical Branch | Validation phase | 311 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9858 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251208 | December | 0230 | 10403 |  |  | 10092 |  |  | -4964 | -4964 | -4659 | Critical Branch | Validation phase | 311 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9858 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251208 | December | 0330 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 35 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 0430 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 35 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 0530 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 35 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 0630 | 10714 |  |  | 10679 |  |  | -4709 | -4709 | -4686 | Critical Branch | Critical Branch | 35 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 0730 | 9242 |  |  | 9241 |  |  | -4813 | -4813 | -4812 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 273
20251208 | December | 0830 | 9242 |  |  | 9241 |  |  | -4813 | -4813 | -4812 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 273
20251208 | December | 0930 | 8996 |  |  | 8996 |  |  | -6142 | -6142 | -6142 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 266
20251208 | December | 1030 | 8996 |  |  | 8996 |  |  | -6142 | -6142 | -6142 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 266
20251208 | December | 1130 | 8996 |  |  | 8996 |  |  | -6142 | -6142 | -6142 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 266
20251208 | December | 1230 |  | 9584 | 770 |  | 9562 | 770 | -5748 | -5748 | 0 | Critical Branch | Critical Branch | NA | 22 | 5748 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 1330 |  | 9584 | 770 |  | 9562 | 770 | -5748 | -5748 | 0 | Critical Branch | Critical Branch | NA | 22 | 5748 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 1430 |  | 9584 | 770 |  | 9562 | 770 | -5748 | -5748 | 0 | Critical Branch | Critical Branch | NA | 22 | 5748 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 1530 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251208 | December | 1630 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251208 | December | 1730 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251208 | December | 1830 |  | 9733 | 810 |  | 9706 | 810 | -6514 | -6514 | 0 | Critical Branch | Critical Branch | NA | 27 | 6514 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 1930 |  | 9733 | 810 |  | 9706 | 810 | -6514 | -6514 | 0 | Critical Branch | Critical Branch | NA | 27 | 6514 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 2030 |  | 9733 | 810 |  | 9706 | 810 | -6514 | -6514 | 0 | Critical Branch | Critical Branch | NA | 27 | 6514 |  |  | 285 | Reduction because NTC over thermal limit on border
20251208 | December | 2130 | 9867 |  |  | 9541 |  |  | -2783 | -2783 | -2457 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9291 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251208 | December | 2230 | 9867 |  |  | 9541 |  |  | -2783 | -2783 | -2457 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9291 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251208 | December | 2330 | 9867 |  |  | 9541 |  |  | -2783 | -2783 | -2457 | Critical Branch | Validation phase | 326 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9291 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0030 | 9352 |  |  | 8975 |  |  | -2984 | -2984 | -2607 | Critical Branch | Validation phase | 377 | NA | 0 |  |  | 277 |  | 8725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0130 | 9352 |  |  | 8975 |  |  | -2984 | -2984 | -2607 | Critical Branch | Validation phase | 377 | NA | 0 |  |  | 277 |  | 8725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0230 | 9352 |  |  | 8975 |  |  | -2984 | -2984 | -2607 | Critical Branch | Validation phase | 377 | NA | 0 |  |  | 277 |  | 8725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0330 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 505 | NA | 0 |  |  | 273 |  | 8481 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0430 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 505 | NA | 0 |  |  | 273 |  | 8481 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0530 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 505 | NA | 0 |  |  | 273 |  | 8481 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0630 | 9236 |  |  | 8731 |  |  | -2331 | -2331 | -1826 | Critical Branch | Validation phase | 505 | NA | 0 |  |  | 273 |  | 8481 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0730 | 9795 |  |  | 9531 |  |  | -6252 | -6252 | -5988 | Critical Branch | Validation phase | 264 | NA | 0 |  |  | 285 |  | 9281 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0830 | 9795 |  |  | 9531 |  |  | -6252 | -6252 | -5988 | Critical Branch | Validation phase | 264 | NA | 0 |  |  | 285 |  | 9281 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 0930 | 9785 |  |  | 9785 |  |  | -2572 | -2572 | -2572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 285
20251209 | December | 1030 | 9785 |  |  | 9785 |  |  | -2572 | -2572 | -2572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 285
20251209 | December | 1130 | 9785 |  |  | 9785 |  |  | -2572 | -2572 | -2572 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 285
20251209 | December | 1230 | 9956 |  |  | 9956 |  |  | -2729 | -2729 | -2728 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 286
20251209 | December | 1330 | 9956 |  |  | 9956 |  |  | -2729 | -2729 | -2728 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 286
20251209 | December | 1430 | 9956 |  |  | 9956 |  |  | -2729 | -2729 | -2728 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 286
20251209 | December | 1530 |  | 9910 | 727 |  | 9900 | 727 | -6577 | -6577 | 0 | Critical Branch | Critical Branch | NA | 10 | 6577 |  |  | 300 | Reduction because NTC over thermal limit on border
20251209 | December | 1630 |  | 9910 | 727 |  | 9900 | 727 | -6577 | -6577 | 0 | Critical Branch | Critical Branch | NA | 10 | 6577 |  |  | 300 | Reduction because NTC over thermal limit on border
20251209 | December | 1730 |  | 9910 | 727 |  | 9900 | 727 | -6577 | -6577 | 0 | Critical Branch | Critical Branch | NA | 10 | 6577 |  |  | 300 | Reduction because NTC over thermal limit on border
20251209 | December | 1830 | 10410 |  |  | 9900 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 510 | NA | 0 |  |  | 300 |  | 9650 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 1930 | 10410 |  |  | 9900 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 510 | NA | 0 |  |  | 300 |  | 9650 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 2030 | 10410 |  |  | 9900 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 510 | NA | 0 |  |  | 300 |  | 9650 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251209 | December | 2130 | 10253 |  |  | 10253 |  |  | -5645 | -5645 | -5645 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 295
20251209 | December | 2230 | 10253 |  |  | 10253 |  |  | -5645 | -5645 | -5645 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 295
20251209 | December | 2330 | 9443 |  |  | 9443 |  |  | -4831 | -4831 | -4831 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 280
20251210 | December | 0030 | 10210 |  |  | 10191 |  |  | -5017 | -5017 | -5004 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0130 | 10210 |  |  | 10191 |  |  | -5017 | -5017 | -5004 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0230 | 10210 |  |  | 10191 |  |  | -5017 | -5017 | -5004 | Critical Branch | Critical Branch | 19 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0330 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0430 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0530 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0630 | 10154 |  |  | 10137 |  |  | -4955 | -4955 | -4943 | Critical Branch | Critical Branch | 17 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251210 | December | 0730 |  | 9234 | 673 |  | 9233 | 673 | -6352 | -6352 | 0 | Critical Branch | Critical Branch | NA | 1 | 6352 |  |  | 287
20251210 | December | 0830 |  | 9234 | 673 |  | 9233 | 673 | -6352 | -6352 | 0 | Critical Branch | Critical Branch | NA | 1 | 6352 |  |  | 287
20251210 | December | 0930 |  | 8596 | 786 |  | 8595 | 786 | -4916 | -4916 | 0 | Critical Branch | Critical Branch | NA | 1 | 4916 |  |  | 266
20251210 | December | 1030 |  | 8596 | 786 |  | 8595 | 786 | -4916 | -4916 | 0 | Critical Branch | Critical Branch | NA | 1 | 4916 |  |  | 266
20251210 | December | 1130 |  | 8596 | 786 |  | 8595 | 786 | -4916 | -4916 | 0 | Critical Branch | Critical Branch | NA | 1 | 4916 |  |  | 266
20251210 | December | 1230 |  | 9007 | 759 |  | 9006 | 759 | -2948 | -2948 | 0 | Critical Branch | Critical Branch | NA | 1 | 2948 |  |  | 279
20251210 | December | 1330 |  | 9007 | 759 |  | 9006 | 759 | -2948 | -2948 | 0 | Critical Branch | Critical Branch | NA | 1 | 2948 |  |  | 279
20251210 | December | 1430 |  | 9007 | 759 |  | 9006 | 759 | -2948 | -2948 | 0 | Critical Branch | Critical Branch | NA | 1 | 2948 |  |  | 279
20251210 | December | 1530 |  | 9334 | 899 |  | 9334 | 888 | -6453 | -6453 | 0 | Critical Branch | Critical Branch | NA | 11 | 6453 |  |  | 142 | Reduction because NTC over thermal limit on border
20251210 | December | 1630 |  | 9334 | 899 |  | 9334 | 888 | -6453 | -6453 | 0 | Critical Branch | Critical Branch | NA | 11 | 6453 |  |  | 142 | Reduction because NTC over thermal limit on border
20251210 | December | 1730 |  | 9334 | 899 |  | 9334 | 888 | -6453 | -6453 | 0 | Critical Branch | Critical Branch | NA | 11 | 6453 |  |  | 142 | Reduction because NTC over thermal limit on border
20251210 | December | 1830 |  | 9975 | 772 |  | 9963 | 772 | -3824 | -3824 | 0 | Critical Branch | Critical Branch | NA | 12 | 3824 |  |  | 300 | Reduction because NTC over thermal limit on border
20251210 | December | 1930 |  | 9975 | 772 |  | 9963 | 772 | -3824 | -3824 | 0 | Critical Branch | Critical Branch | NA | 12 | 3824 |  |  | 300 | Reduction because NTC over thermal limit on border
20251210 | December | 2030 |  | 9975 | 772 |  | 9963 | 772 | -3824 | -3824 | 0 | Critical Branch | Critical Branch | NA | 12 | 3824 |  |  | 300 | Reduction because NTC over thermal limit on border
20251210 | December | 2130 | 10025 |  |  | 10025 |  |  | -5205 | -5205 | -5204 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 288
20251210 | December | 2230 | 10025 |  |  | 10025 |  |  | -5205 | -5205 | -5204 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 288
20251210 | December | 2330 | 9215 |  |  | 9214 |  |  | -4389 | -4389 | -4388 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 272
20251211 | December | 0030 | 10259 |  |  | 10238 |  |  | -3474 | -3474 | -3455 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0130 | 10259 |  |  | 10238 |  |  | -3474 | -3474 | -3455 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0230 | 10259 |  |  | 10238 |  |  | -3474 | -3474 | -3455 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0330 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0430 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0530 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0630 | 10274 |  |  | 10253 |  |  | -5198 | -5198 | -5184 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251211 | December | 0730 | 9435 |  |  | 9434 |  |  | -5285 | -5285 | -5285 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 297
20251211 | December | 0830 | 9435 |  |  | 9434 |  |  | -5285 | -5285 | -5285 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 297
20251211 | December | 0930 | 8962 |  |  | 8961 |  |  | -4935 | -4935 | -4934 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 281
20251211 | December | 1030 | 8962 |  |  | 8961 |  |  | -4935 | -4935 | -4934 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 281
20251211 | December | 1130 | 8962 |  |  | 8961 |  |  | -4935 | -4935 | -4934 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 281
20251211 | December | 1230 | 9735 |  |  | 9728 |  |  | -5368 | -5368 | -5364 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border
20251211 | December | 1330 | 9735 |  |  | 9728 |  |  | -5368 | -5368 | -5364 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border
20251211 | December | 1430 | 9735 |  |  | 9728 |  |  | -5368 | -5368 | -5364 | Critical Branch | Critical Branch | 7 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border
20251211 | December | 1530 | 8836 |  |  | 8835 |  |  | -5298 | -5298 | -5298 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 277
20251211 | December | 1630 | 8836 |  |  | 8835 |  |  | -5298 | -5298 | -5298 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 277
20251211 | December | 1730 | 9736 |  |  | 9735 |  |  | -6137 | -6137 | -6137 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 279
20251211 | December | 1830 | 9510 |  |  | 9509 |  |  | -5258 | -5258 | -5258 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 272
20251211 | December | 1930 | 9510 |  |  | 9509 |  |  | -5258 | -5258 | -5258 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 272
20251211 | December | 2030 | 9510 |  |  | 9509 |  |  | -5258 | -5258 | -5258 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 272
20251211 | December | 2130 | 10245 |  |  | 10245 |  |  | -6618 | -6618 | -6618 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 295
20251211 | December | 2230 | 10245 |  |  | 10245 |  |  | -6618 | -6618 | -6618 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 295
20251211 | December | 2330 | 9435 |  |  | 9434 |  |  | -5847 | -5847 | -5846 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 279
20251212 | December | 0030 | 9664 |  |  | 9612 |  |  | -5248 | -5248 | -5195 | Critical Branch | Validation phase | 52 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9362 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251212 | December | 0130 | 9664 |  |  | 9612 |  |  | -5248 | -5248 | -5195 | Critical Branch | Validation phase | 52 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9362 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251212 | December | 0230 | 9664 |  |  | 9612 |  |  | -5248 | -5248 | -5195 | Critical Branch | Validation phase | 52 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9362 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251212 | December | 0330 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251212 | December | 0430 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251212 | December | 0530 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251212 | December | 0630 | 10290 |  |  | 10268 |  |  | -4857 | -4857 | -4843 | Critical Branch | Critical Branch | 22 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251212 | December | 0730 |  | 9180 | 808 |  | 9180 | 807 | -6082 | -6082 | 0 | Critical Branch | Critical Branch | NA | 1 | 6082 |  |  | 139
20251212 | December | 0830 |  | 9180 | 808 |  | 9180 | 807 | -6082 | -6082 | 0 | Critical Branch | Critical Branch | NA | 1 | 6082 |  |  | 139
20251212 | December | 0930 |  | 10021 | 111 |  | 10021 | 110 | -6709 | -6709 | 0 | Critical Branch | Critical Branch | NA | 1 | 6709 |  |  | 146
20251212 | December | 1030 |  | 10021 | 111 |  | 10021 | 110 | -6709 | -6709 | 0 | Critical Branch | Critical Branch | NA | 1 | 6709 |  |  | 146
20251212 | December | 1130 |  | 10021 | 111 |  | 10021 | 110 | -6709 | -6709 | 0 | Critical Branch | Critical Branch | NA | 1 | 6709 |  |  | 146
20251212 | December | 1230 |  | 9610 | 921 |  | 9610 | 907 | -6793 | -6793 | 0 | Critical Branch | Critical Branch | NA | 14 | 6793 |  |  | 146 | Reduction because NTC over thermal limit on border
20251212 | December | 1330 |  | 9610 | 921 |  | 9610 | 907 | -6793 | -6793 | 0 | Critical Branch | Critical Branch | NA | 14 | 6793 |  |  | 146 | Reduction because NTC over thermal limit on border
20251212 | December | 1430 |  | 9610 | 921 |  | 9242 | 907 | -6793 | -6793 | 0 | Critical Branch | Critical Branch | NA | 382 | 6793 |  |  | 141 | Reduction because NTC over thermal limit on border
20251212 | December | 1530 |  | 7693 | 664 |  | 7650 | 663 | 726 | 86 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 44 | -86 |  |  | 165 |  |  |  | 3463 | Process fail during TSO validation phase
20251212 | December | 1630 |  | 7753 | 670 |  | 7681 | 669 | 726 | 146 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 73 | -146 |  |  | 165 |  |  |  | 3463 | Process fail during TSO validation phase
20251212 | December | 1730 |  | 7720 | 667 |  | 7664 | 667 | 726 | 113 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 56 | -113 |  |  | 165 |  |  |  | 3463 | Process fail during TSO validation phase
20251212 | December | 1830 |  | 9784 | 107 |  | 9643 | 106 | -4669 | -4669 | 0 | Critical Branch | Critical Branch | NA | 142 | 4669 |  |  | 141
20251212 | December | 1930 |  | 9784 | 107 |  | 9784 | 106 | -4669 | -4669 | 0 | Critical Branch | Critical Branch | NA | 1 | 4669 |  |  | 142
20251212 | December | 2030 |  | 9784 | 107 |  | 9784 | 106 | -4669 | -4669 | 0 | Critical Branch | Critical Branch | NA | 1 | 4669 |  |  | 142
20251212 | December | 2130 | 9880 |  |  | 9879 |  |  | -5125 | -5125 | -5124 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 283
20251212 | December | 2230 | 9880 |  |  | 9879 |  |  | -5125 | -5125 | -5124 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 283
20251212 | December | 2330 | 9070 |  |  | 9070 |  |  | -4312 | -4312 | -4312 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 268
20251213 | December | 0030 | 10266 |  |  | 10245 |  |  | -5439 | -5439 | -5425 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0130 | 10266 |  |  | 10245 |  |  | -5439 | -5439 | -5425 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0230 | 10266 |  |  | 10245 |  |  | -5439 | -5439 | -5425 | Critical Branch | Critical Branch | 21 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0330 | 10323 |  |  | 10300 |  |  | -2796 | -2796 | -2775 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0430 | 10323 |  |  | 10300 |  |  | -2796 | -2796 | -2775 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0530 | 10323 |  |  | 10300 |  |  | -2796 | -2796 | -2775 | Critical Branch | Critical Branch | 23 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0630 | 10323 |  |  | 9928 |  |  | -2796 | -2796 | -2402 | Critical Branch | Critical Branch | 395 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251213 | December | 0730 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1982 | NA | 0 |  |  | 300 |  | 8178 | D2CC failed. Correction of BackUp-values.
20251213 | December | 0830 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1982 | NA | 0 |  |  | 300 |  | 8178 | D2CC failed. Correction of BackUp-values.
20251213 | December | 0930 | 10193 |  |  | 9401 |  |  | -5353 | -5353 | -4561 | Critical Branch | Validation phase | 792 | NA | 0 |  |  | 293 |  | 9151 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1030 | 10193 |  |  | 9401 |  |  | -5353 | -5353 | -4561 | Critical Branch | Validation phase | 792 | NA | 0 |  |  | 293 |  | 9151 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1130 | 10193 |  |  | 9401 |  |  | -5353 | -5353 | -4561 | Critical Branch | Validation phase | 792 | NA | 0 |  |  | 293 |  | 9151 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1230 | 10072 |  |  | 9201 |  |  | -5380 | -5380 | -4509 | Critical Branch | Validation phase | 871 | NA | 0 |  |  | 289 |  | 8951 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1330 | 10072 |  |  | 9201 |  |  | -5380 | -5380 | -4509 | Critical Branch | Validation phase | 871 | NA | 0 |  |  | 289 |  | 8951 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1430 | 10072 |  |  | 9201 |  |  | -5380 | -5380 | -4509 | Critical Branch | Validation phase | 871 | NA | 0 |  |  | 289 |  | 8951 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES
20251213 | December | 1530 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1982 | NA | 0 |  |  | 300 |  | 8178 | D2CC failed. Correction of BackUp-values.
20251213 | December | 1630 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1982 | NA | 0 |  |  | 300 |  | 8178 | D2CC failed. Correction of BackUp-values.
20251213 | December | 1730 | 10410 |  |  | 8428 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1982 | NA | 0 |  |  | 300 |  | 8178 | D2CC failed. Correction of BackUp-values.
20251213 | December | 1830 | 10150 |  |  | 9928 |  |  | -5453 | -5453 | -5231 | Critical Branch | Critical Branch | 222 | NA | 0 |  |  | 292
20251213 | December | 1930 | 10150 |  |  | 10150 |  |  | -5453 | -5453 | -5453 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 292
20251213 | December | 2030 | 10150 |  |  | 10150 |  |  | -5453 | -5453 | -5453 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 292
20251213 | December | 2130 | 10609 |  |  | 10551 |  |  | -3314 | -3314 | -3256 | Critical Branch | Validation phase | 58 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border | 10305 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251213 | December | 2230 | 10609 |  |  | 10551 |  |  | -3314 | -3314 | -3256 | Critical Branch | Validation phase | 58 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border | 10305 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251213 | December | 2330 | 9799 |  |  | 9740 |  |  | -2470 | -2470 | -2412 | Critical Branch | Validation phase | 59 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9495 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251214 | December | 0030 | 10604 |  |  | 10573 |  |  | -3353 | -3353 | -3324 | Critical Branch | Critical Branch | 31 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 0130 | 10604 |  |  | 10573 |  |  | -3353 | -3353 | -3324 | Critical Branch | Critical Branch | 31 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 0230 | 10604 |  |  | 10573 |  |  | -3353 | -3353 | -3324 | Critical Branch | Critical Branch | 31 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 0330 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 296 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9969 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0430 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 296 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9969 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0530 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 296 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9969 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0630 | 10496 |  |  | 10200 |  |  | -6361 | -6361 | -6071 | Critical Branch | Validation phase | 296 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9969 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 0730 | 10176 |  |  | 10158 |  |  | -5288 | -5288 | -5276 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 0830 | 10176 |  |  | 10158 |  |  | -5288 | -5288 | -5276 | Critical Branch | Critical Branch | 18 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 0930 | 9804 |  |  | 9798 |  |  | -5310 | -5310 | -5306 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 1030 | 9804 |  |  | 9798 |  |  | -5310 | -5310 | -5306 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 1130 | 9804 |  |  | 9798 |  |  | -5310 | -5310 | -5306 | Critical Branch | Critical Branch | 6 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 1230 | 9896 |  |  | 9887 |  |  | -5180 | -5180 | -5174 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 1330 | 9896 |  |  | 9887 |  |  | -5180 | -5180 | -5174 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 1430 | 9896 |  |  | 9887 |  |  | -5180 | -5180 | -5174 | Critical Branch | Critical Branch | 9 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251214 | December | 1530 | 10072 |  |  | 10049 |  |  | -6097 | -6097 | -6080 | Critical Branch | Validation phase | 23 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9814 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 1630 | 10072 |  |  | 10049 |  |  | -6097 | -6097 | -6080 | Critical Branch | Validation phase | 23 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9814 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 1730 | 10072 |  |  | 10049 |  |  | -6097 | -6097 | -6080 | Critical Branch | Validation phase | 23 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9814 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 1830 | 9040 |  |  | 9040 |  |  | -5438 | -5438 | -5438 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 267
20251214 | December | 1930 | 9040 |  |  | 9040 |  |  | -5438 | -5438 | -5438 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 267
20251214 | December | 2030 | 9040 |  |  | 9040 |  |  | -5438 | -5438 | -5438 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 267
20251214 | December | 2130 | 10332 |  |  | 10083 |  |  | -6272 | -6272 | -6029 | Critical Branch | Validation phase | 249 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9849 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 2230 | 10332 |  |  | 10083 |  |  | -6272 | -6272 | -6029 | Critical Branch | Validation phase | 249 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9849 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251214 | December | 2330 | 10332 |  |  | 10083 |  |  | -6272 | -6272 | -6029 | Critical Branch | Validation phase | 249 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border | 9849 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251215 | December | 0030 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251215 | December | 0130 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251215 | December | 0230 | 9600 |  |  | 9600 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 285
20251215 | December | 0330 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 241
20251215 | December | 0430 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 241
20251215 | December | 0530 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 241
20251215 | December | 0630 | 8221 |  |  | 8220 |  |  | -6009 | -6009 | -6008 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 241
20251215 | December | 0730 | 10499 |  |  | 9720 |  |  | -6657 | -6657 | -5886 | Critical Branch | Validation phase | 779 | NA | 0 |  |  | 284 |  | 10150 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251215 | December | 0830 | 9746 |  |  | 9641 |  |  | -6024 | -6024 | -5922 | Critical Branch | Validation phase | 105 | NA | 0 |  |  | 300 | Reduction because NTC over thermal limit on border | 9397 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251215 | December | 0930 | 8914 |  |  | 8913 |  |  | -4163 | -4163 | -4162 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 281
20251215 | December | 1030 | 8914 |  |  | 8913 |  |  | -4163 | -4163 | -4162 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 281
20251215 | December | 1130 | 8914 |  |  | 8913 |  |  | -4163 | -4163 | -4162 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 281
20251215 | December | 1230 | 8989 |  |  | 8989 |  |  | -4312 | -4312 | -4311 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 284
20251215 | December | 1330 | 8989 |  |  | 8989 |  |  | -4312 | -4312 | -4311 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 284
20251215 | December | 1430 | 8989 |  |  | 8989 |  |  | -4312 | -4312 | -4311 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 284
20251215 | December | 1530 | 9366 |  |  | 9365 |  |  | -5087 | -5087 | -5086 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 296
20251215 | December | 1630 | 9366 |  |  | 9365 |  |  | -5087 | -5087 | -5086 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 296
20251215 | December | 1730 | 10119 |  |  | 10119 |  |  | -5765 | -5765 | -5765 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 297
20251215 | December | 1830 | 9900 |  |  | 9858 |  |  | -5968 | -5968 | -5926 | Critical Branch | Validation phase | 42 | NA | 0 |  |  | 284 |  | 9608 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251215 | December | 1930 | 9900 |  |  | 9858 |  |  | -5968 | -5968 | -5926 | Critical Branch | Validation phase | 42 | NA | 0 |  |  | 284 |  | 9608 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251215 | December | 2030 | 9900 |  |  | 9858 |  |  | -5968 | -5968 | -5926 | Critical Branch | Validation phase | 42 | NA | 0 |  |  | 284 |  | 9608 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251215 | December | 2130 | 10003 |  |  | 10002 |  |  | -5130 | -5130 | -5130 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 287
20251215 | December | 2230 | 10003 |  |  | 10002 |  |  | -5130 | -5130 | -5130 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 287
20251215 | December | 2330 | 9193 |  |  | 9193 |  |  | -4316 | -4316 | -4316 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 272
20251216 | December | 0030 | 10074 |  |  | 10059 |  |  | -5560 | -5560 | -5550 | Critical Branch | Critical Branch | 15 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0130 | 10074 |  |  | 10059 |  |  | -5560 | -5560 | -5550 | Critical Branch | Critical Branch | 15 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0230 | 10074 |  |  | 10059 |  |  | -5560 | -5560 | -5550 | Critical Branch | Critical Branch | 15 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0330 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0430 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0530 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0630 | 9968 |  |  | 9956 |  |  | -7970 | -7970 | -7963 | Critical Branch | Critical Branch | 12 | NA | 0 |  |  | 285 | Reduction because NTC over thermal limit on border
20251216 | December | 0730 | 9452 |  |  | 9451 |  |  | -5583 | -5583 | -5583 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 276
20251216 | December | 0830 | 9212 |  |  | 9212 |  |  | -5374 | -5374 | -5374 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 55
20251216 | December | 0930 | 9871 |  |  | 9844 |  |  | -5425 | -5425 | -5398 | Critical Branch | Validation phase | 27 | NA | 0 |  |  | 59 |  | 9594 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251216 | December | 1030 | 9871 |  |  | 9844 |  |  | -5425 | -5425 | -5398 | Critical Branch | Validation phase | 27 | NA | 0 |  |  | 59 |  | 9594 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251216 | December | 1130 | 9871 |  |  | 9844 |  |  | -5425 | -5425 | -5398 | Critical Branch | Validation phase | 27 | NA | 0 |  |  | 59 |  | 9594 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20251216 | December | 1230 | 9825 |  |  | 9825 |  |  | -3764 | -3764 | -3764 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 59
20251216 | December | 1330 | 9825 |  |  | 9825 |  |  | -3764 | -3764 | -3764 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 59
20251216 | December | 1430 | 9825 |  |  | 9825 |  |  | -3764 | -3764 | -3764 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 59
20251216 | December | 1530 | 9288 |  |  | 9287 |  |  | -6173 | -6173 | -6173 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 55
20251216 | December | 1630 | 9288 |  |  | 9287 |  |  | -6173 | -6173 | -6173 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 55
20251216 | December | 1730 | 9288 |  |  | 9287 |  |  | -6173 | -6173 | -6173 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 55
20251216 | December | 1830 | 9740 |  |  | 9740 |  |  | -6991 | -6991 | -6991 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 57
20251216 | December | 1930 | 9740 |  |  | 9740 |  |  | -6991 | -6991 | -6991 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 57
20251216 | December | 2030 | 9740 |  |  | 9740 |  |  | -6991 | -6991 | -6991 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 57
20251216 | December | 2130 | 10139 |  |  | 10138 |  |  | -5551 | -5551 | -5550 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251216 | December | 2230 | 10139 |  |  | 10138 |  |  | -5551 | -5551 | -5550 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251216 | December | 2330 | 9344 |  |  | 9343 |  |  | -4811 | -4811 | -4810 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0030 | 9317 |  |  | 9316 |  |  | -2687 | -2687 | -2686 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0130 | 9317 |  |  | 9316 |  |  | -2687 | -2687 | -2686 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0230 | 9317 |  |  | 9316 |  |  | -2687 | -2687 | -2686 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0330 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0430 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0530 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0630 | 9331 |  |  | 9330 |  |  | -2724 | -2724 | -2723 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 59
20251217 | December | 0730 |  | 9545 | 792 |  | 9545 | 790 | -4567 | -4567 | 0 | Critical Branch | Critical Branch | NA | 2 | 4567 |  |  | 30 | Reduction because NTC over thermal limit on border
20251217 | December | 0830 |  | 9545 | 792 |  | 9545 | 790 | -4567 | -4567 | 0 | Critical Branch | Critical Branch | NA | 2 | 4567 |  |  | 30 | Reduction because NTC over thermal limit on border
20251217 | December | 0930 | 9859 |  |  | 9859 |  |  | -3214 | -3214 | -3214 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 59
20251217 | December | 1030 | 9859 |  |  | 9859 |  |  | -3214 | -3214 | -3214 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 59
20251217 | December | 1130 | 9859 |  |  | 9859 |  |  | -3214 | -3214 | -3214 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 59
20251217 | December | 1230 |  | 8785 | 18 |  | 8785 | 17 | -1997 | -1997 | 0 | Critical Branch | Critical Branch | NA | 1 | 1997 |  |  | 53
20251217 | December | 1330 |  | 8785 | 18 |  | 8785 | 17 | -1997 | -1997 | 0 | Critical Branch | Critical Branch | NA | 1 | 1997 |  |  | 53
20251217 | December | 1430 |  | 8785 | 18 |  | 8785 | 17 | -1997 | -1997 | 0 | Critical Branch | Critical Branch | NA | 1 | 1997 |  |  | 53
20251217 | December | 1530 |  | 9059 | 748 |  | 9059 | 747 | -5325 | -5325 | 0 | Critical Branch | Critical Branch | NA | 1 | 5325 |  |  | 28
20251217 | December | 1630 |  | 9059 | 748 |  | 9059 | 747 | -5325 | -5325 | 0 | Critical Branch | Critical Branch | NA | 1 | 5325 |  |  | 28
20251217 | December | 1730 |  | 9100 | 763 |  | 9100 | 762 | -5397 | -5397 | 0 | Critical Branch | Critical Branch | NA | 1 | 5397 |  |  | 68 | Reduction because NTC over thermal limit on border
20251217 | December | 1830 |  | 8814 | 646 |  | 8813 | 646 | -5011 | -5011 | 0 | Critical Branch | Critical Branch | NA | 1 | 5011 |  |  | 134
20251217 | December | 1930 |  | 8814 | 646 |  | 8813 | 646 | -5011 | -5011 | 0 | Critical Branch | Critical Branch | NA | 1 | 5011 |  |  | 134
20251217 | December | 2030 |  | 8814 | 646 |  | 8813 | 646 | -5011 | -5011 | 0 | Critical Branch | Critical Branch | NA | 1 | 5011 |  |  | 134
20251217 | December | 2130 | 10396 |  |  | 10291 |  |  | -5701 | -5701 | -5597 | Critical Branch | Validation phase | 105 | NA | 0 |  |  | 145 | Reduction because NTC over thermal limit on border | 10042 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251217 | December | 2230 | 10396 |  |  | 10291 |  |  | -5701 | -5701 | -5597 | Critical Branch | Validation phase | 105 | NA | 0 |  |  | 145 | Reduction because NTC over thermal limit on border | 10042 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251217 | December | 2330 | 9596 |  |  | 9491 |  |  | -4899 | -4899 | -4794 | Critical Branch | Validation phase | 105 | NA | 0 |  |  | 140 | Reduction because NTC over thermal limit on border | 9242 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251218 | December | 0030 | 8904 |  |  | 8904 |  |  | -4655 | -4655 | -4654 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 131
20251218 | December | 0130 | 8904 |  |  | 8904 |  |  | -4655 | -4655 | -4654 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 131
20251218 | December | 0230 | 8904 |  |  | 8904 |  |  | -4655 | -4655 | -4654 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 131
20251218 | December | 0330 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 140
20251218 | December | 0430 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 140
20251218 | December | 0530 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 140
20251218 | December | 0630 | 9455 |  |  | 9455 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 140
20251218 | December | 0730 | 10169 |  |  | 10167 |  |  | -5959 | -5959 | -5958 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 145 | Reduction because NTC over thermal limit on border
20251218 | December | 0830 | 10169 |  |  | 10167 |  |  | -5959 | -5959 | -5958 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 145 | Reduction because NTC over thermal limit on border
20251218 | December | 0930 | 9783 |  |  | 9782 |  |  | -5086 | -5086 | -5085 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 140
20251218 | December | 1030 | 9783 |  |  | 9782 |  |  | -5086 | -5086 | -5085 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 140
20251218 | December | 1130 | 9783 |  |  | 9782 |  |  | -5086 | -5086 | -5085 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 140
20251218 | December | 1230 | 8540 |  |  | 8540 |  |  | -5928 | -5928 | -5928 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 122
20251218 | December | 1330 | 8540 |  |  | 8540 |  |  | -5928 | -5928 | -5928 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 122
20251218 | December | 1430 | 8540 |  |  | 8540 |  |  | -5928 | -5928 | -5928 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 122
20251218 | December | 1530 | 8633 |  |  | 8633 |  |  | -4721 | -4721 | -4721 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 123
20251218 | December | 1630 | 8633 |  |  | 8633 |  |  | -4721 | -4721 | -4721 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 123
20251218 | December | 1730 | 8873 |  |  | 8873 |  |  | -4926 | -4926 | -4926 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 329
20251218 | December | 1830 | 10495 |  |  | 10373 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 122 | NA | 0 |  |  | 380
20251218 | December | 1930 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251218 | December | 2030 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251218 | December | 2130 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251218 | December | 2230 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251218 | December | 2330 | 9680 |  |  | 9680 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 365
20251219 | December | 0030 | 9506 |  |  | 9506 |  |  | -3440 | -3440 | -3440 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 358
20251219 | December | 0130 | 9506 |  |  | 9506 |  |  | -3440 | -3440 | -3440 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 358
20251219 | December | 0230 | 9506 |  |  | 9506 |  |  | -3440 | -3440 | -3440 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 358
20251219 | December | 0330 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 355
20251219 | December | 0430 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 355
20251219 | December | 0530 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 355
20251219 | December | 0630 | 9438 |  |  | 9438 |  |  | -3449 | -3449 | -3449 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 355
20251219 | December | 0730 |  | 9822 | 805 |  | 9808 | 805 | -4172 | -4172 | 0 | Critical Branch | Critical Branch | NA | 14 | 4172 |  |  | 385 | Reduction because NTC over thermal limit on border
20251219 | December | 0830 |  | 9822 | 805 |  | 9808 | 805 | -4172 | -4172 | 0 | Critical Branch | Critical Branch | NA | 14 | 4172 |  |  | 385 | Reduction because NTC over thermal limit on border
20251219 | December | 0930 | 9522 |  |  | 9521 |  |  | -3295 | -3295 | -3295 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 354
20251219 | December | 1030 | 9522 |  |  | 9521 |  |  | -3295 | -3295 | -3295 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 354
20251219 | December | 1130 | 9522 |  |  | 9521 |  |  | -3295 | -3295 | -3295 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 354
20251219 | December | 1230 |  | 9284 | 121 |  | 9284 | 121 | -3311 | -3311 | 0 | Critical Branch | Critical Branch | NA | 0 | 3311 |  |  | 176
20251219 | December | 1330 |  | 9284 | 121 |  | 9284 | 121 | -3311 | -3311 | 0 | Critical Branch | Critical Branch | NA | 0 | 3311 |  |  | 176
20251219 | December | 1430 |  | 9284 | 121 |  | 9284 | 121 | -3311 | -3311 | 0 | Critical Branch | Critical Branch | NA | 0 | 3311 |  |  | 176
20251219 | December | 1530 |  | 8447 | 808 |  | 8447 | 808 | -3720 | -3720 | 0 | Critical Branch | Critical Branch | NA | 0 | 3720 |  |  | 167
20251219 | December | 1630 |  | 8447 | 808 |  | 8447 | 808 | -3720 | -3720 | 0 | Critical Branch | Critical Branch | NA | 0 | 3720 |  |  | 167
20251219 | December | 1730 |  | 8447 | 808 |  | 8447 | 808 | -3720 | -3720 | 0 | Critical Branch | Critical Branch | NA | 0 | 3720 |  |  | 167
20251219 | December | 1830 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251219 | December | 1930 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251219 | December | 2030 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251219 | December | 2130 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251219 | December | 2230 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251219 | December | 2330 | 9680 |  |  | 9680 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 365
20251220 | December | 0030 | 9875 |  |  | 9795 |  |  | -5615 | -5615 | -5536 | Critical Branch | Validation phase | 80 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9550 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0130 | 9875 |  |  | 9795 |  |  | -5615 | -5615 | -5536 | Critical Branch | Validation phase | 80 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9550 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0230 | 9875 |  |  | 9795 |  |  | -5615 | -5615 | -5536 | Critical Branch | Validation phase | 80 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9550 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0330 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 337
20251220 | December | 0430 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 337
20251220 | December | 0530 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 337
20251220 | December | 0630 | 8989 |  |  | 8988 |  |  | -6689 | -6689 | -6689 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 337
20251220 | December | 0730 | 9641 |  |  | 9463 |  |  | -2342 | -2342 | -2164 | Critical Branch | Validation phase | 178 | NA | 0 |  |  | 352 |  | 9213 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0830 | 9641 |  |  | 9463 |  |  | -2342 | -2342 | -2164 | Critical Branch | Validation phase | 178 | NA | 0 |  |  | 352 |  | 9213 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251220 | December | 0930 | 8364 |  |  | 8363 |  |  | -2906 | -2906 | -2905 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 302
20251220 | December | 1030 | 8364 |  |  | 8363 |  |  | -2906 | -2906 | -2905 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 302
20251220 | December | 1130 | 8364 |  |  | 8363 |  |  | -2906 | -2906 | -2905 | Critical Branch | Critical Branch | 1 | NA | 0 |  |  | 302
20251220 | December | 1230 | 10495 |  |  | 9863 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 632 | NA | 0 |  |  | 360
20251220 | December | 1330 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251220 | December | 1430 | 10495 |  |  | 10316 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 179 | NA | 0 |  |  | 378
20251220 | December | 1530 | 8816 |  |  | 8816 |  |  | -4261 | -4261 | -4260 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 320
20251220 | December | 1630 | 8816 |  |  | 8816 |  |  | -4261 | -4261 | -4260 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 320
20251220 | December | 1730 | 8816 |  |  | 8816 |  |  | -4261 | -4261 | -4260 | Critical Branch | Critical Branch | 0 | NA | 0 |  |  | 320
20251220 | December | 1830 | 10495 |  |  | 10316 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 179 | NA | 0 |  |  | 378
20251220 | December | 1930 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251220 | December | 2030 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251220 | December | 2130 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251220 | December | 2230 | 10495 |  |  | 10495 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 385
20251220 | December | 2330 | 9680 |  |  | 9680 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | NA | 0 |  |  | 365
20251221 | December | 0030 | 10659 |  |  | 9547 |  |  | -3654 | -3654 | -2542 | Critical Branch | Validation phase | 1112 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9217 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0130 | 10659 |  |  | 9547 |  |  | -3654 | -3654 | -2542 | Critical Branch | Validation phase | 1112 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9217 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0230 | 10659 |  |  | 9547 |  |  | -3654 | -3654 | -2542 | Critical Branch | Validation phase | 1112 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9217 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0330 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 1234 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9077 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0430 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 1234 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9077 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0530 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 1234 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9077 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0630 | 10641 |  |  | 9407 |  |  | -3487 | -3487 | -2253 | Critical Branch | Validation phase | 1234 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9077 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0730 | 10649 |  |  | 9258 |  |  | -6815 | -6815 | -5424 | Critical Branch | Validation phase | 1391 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8928 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0830 | 10649 |  |  | 9258 |  |  | -6815 | -6815 | -5424 | Critical Branch | Validation phase | 1391 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8928 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 0930 |  | 10297 | 830 |  | 9743 | 788 | -7696 | -7696 | 0 | Critical Branch | Validation phase | NA | 596 | 7696 |  |  | 365 | Reduction because NTC over thermal limit on border | 10106 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251221 | December | 1030 |  | 10297 | 830 |  | 9743 | 788 | -7696 | -7696 | 0 | Critical Branch | Validation phase | NA | 596 | 7696 |  |  | 365 | Reduction because NTC over thermal limit on border | 10106 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251221 | December | 1130 |  | 10297 | 830 |  | 9743 | 788 | -7696 | -7696 | 0 | Critical Branch | Validation phase | NA | 596 | 7696 |  |  | 365 | Reduction because NTC over thermal limit on border | 10106 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES
20251221 | December | 1230 | 10570 |  |  | 9072 |  |  | -3182 | -3182 | -1684 | Critical Branch | Validation phase | 1498 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8742 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251221 | December | 1330 | 10570 |  |  | 9072 |  |  | -3182 | -3182 | -1684 | Critical Branch | Validation phase | 1498 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8742 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251221 | December | 1430 | 10570 |  |  | 9072 |  |  | -3182 | -3182 | -1684 | Critical Branch | Validation phase | 1498 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8742 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20251221 | December | 1530 |  | 10232 | 870 |  | 10183 | 870 | -6091 | -6091 | 0 | Critical Branch | Critical Branch | NA | 49 | 6091 |  |  | 365 | Reduction because NTC over thermal limit on border
20251221 | December | 1630 |  | 10232 | 870 |  | 10191 | 870 | -6091 | -6091 | 0 | Critical Branch | Critical Branch | NA | 41 | 6091 |  |  | 365 | Reduction because NTC over thermal limit on border
20251221 | December | 1730 |  | 10232 | 870 |  | 10191 | 870 | -6091 | -6091 | 0 | Critical Branch | Critical Branch | NA | 41 | 6091 |  |  | 365 | Reduction because NTC over thermal limit on border
20251221 | December | 1830 |  | 10394 | 885 |  | 10347 | 885 | -6063 | -6063 | 0 | Critical Branch | Critical Branch | NA | 47 | 6063 |  |  | 365 | Reduction because NTC over thermal limit on border
20251221 | December | 1930 |  | 10394 | 885 |  | 10347 | 885 | -6063 | -6063 | 0 | Critical Branch | Critical Branch | NA | 47 | 6063 |  |  | 365 | Reduction because NTC over thermal limit on border
20251221 | December | 2030 |  | 10394 | 885 |  | 10347 | 885 | -6063 | -6063 | 0 | Critical Branch | Critical Branch | NA | 47 | 6063 |  |  | 365 | Reduction because NTC over thermal limit on border
20251221 | December | 2130 | 10721 |  |  | 9276 |  |  | -5604 | -5604 | -4159 | Critical Branch | Validation phase | 1445 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8946 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 2230 | 10721 |  |  | 9276 |  |  | -5604 | -5604 | -4159 | Critical Branch | Validation phase | 1445 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8946 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251221 | December | 2330 | 10721 |  |  | 9276 |  |  | -5604 | -5604 | -4159 | Critical Branch | Validation phase | 1445 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 8946 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 0030 | 10033 |  |  | 7700 |  |  | -5314 | -5314 | -2981 | Critical Branch | Validation phase | 2333 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7370 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0130 | 10033 |  |  | 7700 |  |  | -5314 | -5314 | -2981 | Critical Branch | Validation phase | 2333 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7370 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0230 | 10033 |  |  | 7700 |  |  | -5314 | -5314 | -2981 | Critical Branch | Validation phase | 2333 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7370 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0330 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 1526 | NA | 0 |  |  | 361 |  | 7725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0430 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 1526 | NA | 0 |  |  | 361 |  | 7725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0530 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 1526 | NA | 0 |  |  | 361 |  | 7725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0630 | 9581 |  |  | 8055 |  |  | -3163 | -3163 | -1637 | Critical Branch | Validation phase | 1526 | NA | 0 |  |  | 361 |  | 7725 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0730 | 10495 |  |  | 8130 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2365 | NA | 0 |  |  | 385 |  | 7795 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0830 | 9095 |  |  | 8130 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 965 | NA | 0 |  |  | 385 |  | 7795 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251222 | December | 0930 |  | 8213 | 814 |  | 8086 | 803 | -2822 | -2822 | 0 | Critical Branch | Validation phase | NA | 138 | 2822 |  |  | 381 |  | 8277 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251222 | December | 1030 |  | 8213 | 814 |  | 8086 | 803 | -2822 | -2822 | 0 | Critical Branch | Validation phase | NA | 138 | 2822 |  |  | 381 |  | 8277 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251222 | December | 1130 |  | 8213 | 814 |  | 8086 | 803 | -2822 | -2822 | 0 | Critical Branch | Validation phase | NA | 138 | 2822 |  |  | 381 |  | 8277 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251222 | December | 1230 |  | 7960 | 782 |  | 7959 | 782 | -2468 | -2468 | 0 | Critical Branch | Critical Branch | NA | 1 | 2468 |  |  | 371
20251222 | December | 1330 |  | 7960 | 782 |  | 7959 | 782 | -2468 | -2468 | 0 | Critical Branch | Critical Branch | NA | 1 | 2468 |  |  | 371
20251222 | December | 1430 |  | 7960 | 782 |  | 7959 | 782 | -2468 | -2468 | 0 | Critical Branch | Critical Branch | NA | 1 | 2468 |  |  | 371
20251222 | December | 1530 |  | 8559 | 804 |  | 8283 | 784 | -1139 | -1139 | 0 | Critical Branch | Validation phase | NA | 296 | 1139 |  |  | 385 | Reduction because NTC over thermal limit on border | 8639 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 1630 |  | 9964 | 804 |  | 9689 | 784 | -2852 | -2852 | 0 | Critical Branch | Validation phase | NA | 295 | 2852 |  |  | 385 | Reduction because NTC over thermal limit on border | 10039 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 1730 |  | 9964 | 804 |  | 9689 | 784 | -2852 | -2852 | 0 | Critical Branch | Validation phase | NA | 295 | 2852 |  |  | 385 | Reduction because NTC over thermal limit on border | 10039 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 1830 |  | 10020 | 799 |  | 10010 | 799 | -5933 | -5933 | 0 | Critical Branch | Critical Branch | NA | 10 | 5933 |  |  | 385 | Reduction because NTC over thermal limit on border
20251222 | December | 1930 |  | 10020 | 799 |  | 8857 | 799 | -5933 | -5933 | 0 | Critical Branch | Critical Branch | NA | 1163 | 5933 |  |  | 385 | Reduction because NTC over thermal limit on border
20251222 | December | 2030 |  | 10020 | 799 |  | 7414 | 799 | -5933 | -5933 | 0 | Critical Branch | Critical Branch | NA | 2606 | 5933 |  |  | 385 | Reduction because NTC over thermal limit on border
20251222 | December | 2130 | 10577 |  |  | 6224 |  |  | -3078 | -3078 | 1275 | Critical Branch | Validation phase | 4353 | NA | 5628 |  |  | 385 | Reduction because NTC over thermal limit on border | 5889 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 2230 | 10577 |  |  | 6224 |  |  | -3078 | -3078 | 1275 | Critical Branch | Validation phase | 4353 | NA | 5628 |  |  | 385 | Reduction because NTC over thermal limit on border | 5889 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251222 | December | 2330 | 9762 |  |  | 5409 |  |  | -2221 | -2221 | 2132 | Critical Branch | Validation phase | 4353 | NA | 6485 |  |  | 365 | Reduction because NTC over thermal limit on border | 5079 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 0030 | 9995 |  |  | 8000 |  |  | -5307 | -5307 | -3312 | Critical Branch | Validation phase | 1995 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7670 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0130 | 9995 |  |  | 8000 |  |  | -5307 | -5307 | -3312 | Critical Branch | Validation phase | 1995 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7670 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0230 | 9995 |  |  | 8000 |  |  | -5307 | -5307 | -3312 | Critical Branch | Validation phase | 1995 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 7670 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0330 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 1661 | NA | 0 |  |  | 363 |  | 7646 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0430 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 1661 | NA | 0 |  |  | 363 |  | 7646 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0530 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 1661 | NA | 0 |  |  | 363 |  | 7646 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0630 | 9637 |  |  | 7976 |  |  | -3428 | -3428 | -1767 | Critical Branch | Validation phase | 1661 | NA | 0 |  |  | 363 |  | 7646 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0730 | 10015 |  |  | 7727 |  |  | -3329 | -3329 | -1041 | Critical Branch | Validation phase | 2288 | NA | 0 |  |  | 370 |  | 7392 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0830 | 10015 |  |  | 7727 |  |  | -3329 | -3329 | -1041 | Critical Branch | Validation phase | 2288 | NA | 0 |  |  | 370 |  | 7392 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 0930 | 9580 |  |  | 7153 |  |  | -3010 | -3010 | -583 | Critical Branch | Validation phase | 2427 | NA | 0 |  |  | 357 |  | 6818 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1030 | 9580 |  |  | 7153 |  |  | -3010 | -3010 | -583 | Critical Branch | Validation phase | 2427 | NA | 0 |  |  | 357 |  | 6818 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1130 | 9580 |  |  | 7153 |  |  | -3010 | -3010 | -583 | Critical Branch | Validation phase | 2427 | NA | 0 |  |  | 357 |  | 6818 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1230 |  | 9097 | 650 |  | 8296 | 625 | -2487 | -2487 | 0 | Critical Branch | Smoothing ramp | NA | 826 | 2487 | Smoothing | Smoothing ramp | 365 |  | 9046 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1330 |  | 9097 | 650 |  | 8752 | 625 | -2487 | -2487 | 0 | Critical Branch | Validation phase | NA | 370 | 2487 |  |  | 365 |  | 9046 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1430 |  | 9097 | 650 |  | 8752 | 625 | -2487 | -2487 | 0 | Critical Branch | Validation phase | NA | 370 | 2487 |  |  | 365 |  | 9046 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251223 | December | 1530 | 9923 |  |  | 9163 |  |  | -33 | -33 | 727 | Critical Branch | Validation phase | 760 | NA | 1487 |  |  | 367 |  | 8828 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 1630 | 9923 |  |  | 9163 |  |  | -33 | -33 | 727 | Critical Branch | Validation phase | 760 | NA | 1487 |  |  | 367 |  | 8828 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 1730 | 9923 |  |  | 9163 |  |  | -33 | -33 | 727 | Critical Branch | Validation phase | 760 | NA | 1487 |  |  | 367 |  | 8828 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20251223 | December | 1830 |  | 9186 | 777 |  | 9186 | 777 | -539 | -539 | 0 | Critical Branch | Critical Branch | NA | 0 | 539 |  |  | 368
20251223 | December | 1930 |  | 9186 | 777 |  | 9186 | 777 | -539 | -539 | 0 | Critical Branch | Critical Branch | NA | 0 | 539 |  |  | 368
20251223 | December | 2030 |  | 9186 | 777 |  | 9166 | 777 | -539 | -539 | 0 | Critical Branch | Critical Branch | NA | 20 | 539 |  |  | 368
20251223 | December | 2130 | 10260 |  |  | 8044 |  |  | -3850 | -3850 | -1634 | Critical Branch | Validation phase | 2216 | NA | 0 |  |  | 377 |  | 7709 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251223 | December | 2230 | 10260 |  |  | 8044 |  |  | -3850 | -3850 | -1634 | Critical Branch | Validation phase | 2216 | NA | 0 |  |  | 377 |  | 7709 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251223 | December | 2330 | 9445 |  |  | 7229 |  |  | -3025 | -3025 | -809 | Critical Branch | Validation phase | 2216 | NA | 0 |  |  | 357 |  | 6899 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251224 | December | 0030 |  | 9917 | 187 |  | 9917 | 181 | -3735 | -3735 | 0 | Critical Branch | Critical Branch | NA | 6 | 3735 |  |  | 189 | Reduction because NTC over thermal limit on border
20251224 | December | 0130 |  | 9917 | 187 |  | 9917 | 181 | -3735 | -3735 | 0 | Critical Branch | Critical Branch | NA | 6 | 3735 |  |  | 189 | Reduction because NTC over thermal limit on border
20251224 | December | 0230 |  | 9917 | 187 |  | 9917 | 181 | -3735 | -3735 | 0 | Critical Branch | Critical Branch | NA | 6 | 3735 |  |  | 189 | Reduction because NTC over thermal limit on border
20251224 | December | 0330 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 25 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251224 | December | 0430 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 25 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251224 | December | 0530 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 25 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251224 | December | 0630 | 10486 |  |  | 10461 |  |  | -2742 | -2742 | -2719 | Critical Branch | Critical Branch | 25 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251224 | December | 0730 |  | 9275 | 947 |  | 9275 | 931 | -2955 | -2955 | 0 | Critical Branch | Critical Branch | NA | 16 | 2955 |  |  | 182 | Reduction because NTC over thermal limit on border
20251224 | December | 0830 |  | 9275 | 947 |  | 9275 | 931 | -2955 | -2955 | 0 | Critical Branch | Critical Branch | NA | 16 | 2955 |  |  | 182 | Reduction because NTC over thermal limit on border
20251224 | December | 0930 |  | 9497 | 763 |  | 9496 | 763 | -2332 | -2332 | 0 | Critical Branch | Critical Branch | NA | 1 | 2332 |  |  | 378
20251224 | December | 1030 |  | 9497 | 763 |  | 9496 | 763 | -2332 | -2332 | 0 | Critical Branch | Critical Branch | NA | 1 | 2332 |  |  | 378
20251224 | December | 1130 |  | 9497 | 763 |  | 9496 | 763 | -2332 | -2332 | 0 | Critical Branch | Critical Branch | NA | 1 | 2332 |  |  | 378
20251224 | December | 1230 |  | 9558 | 920 |  | 9558 | 908 | -3143 | -3143 | 0 | Critical Branch | Critical Branch | NA | 12 | 3143 |  |  | 217 | Reduction because NTC over thermal limit on border
20251224 | December | 1330 |  | 9558 | 920 |  | 9558 | 908 | -3143 | -3143 | 0 | Critical Branch | Critical Branch | NA | 12 | 3143 |  |  | 217 | Reduction because NTC over thermal limit on border
20251224 | December | 1430 |  | 9558 | 920 |  | 9558 | 908 | -3143 | -3143 | 0 | Critical Branch | Critical Branch | NA | 12 | 3143 |  |  | 217 | Reduction because NTC over thermal limit on border
20251224 | December | 1530 |  | 9384 | 952 |  | 9384 | 936 | -1827 | -1827 | 0 | Critical Branch | Critical Branch | NA | 16 | 1827 |  |  | 215 | Reduction because NTC over thermal limit on border
20251224 | December | 1630 |  | 9384 | 952 |  | 9384 | 936 | -1827 | -1827 | 0 | Critical Branch | Critical Branch | NA | 16 | 1827 |  |  | 215 | Reduction because NTC over thermal limit on border
20251224 | December | 1730 |  | 9384 | 952 |  | 9384 | 936 | -1827 | -1827 | 0 | Critical Branch | Critical Branch | NA | 16 | 1827 |  |  | 215 | Reduction because NTC over thermal limit on border
20251224 | December | 1830 |  | 9856 | 990 |  | 9856 | 968 | -3626 | -3626 | 0 | Critical Branch | Critical Branch | NA | 22 | 3626 |  |  | 222 | Reduction because NTC over thermal limit on border
20251224 | December | 1930 |  | 9856 | 990 |  | 9856 | 968 | -3626 | -3626 | 0 | Critical Branch | Critical Branch | NA | 22 | 3626 |  |  | 222 | Reduction because NTC over thermal limit on border
20251224 | December | 2030 |  | 9856 | 990 |  | 9856 | 968 | -3626 | -3626 | 0 | Critical Branch | Critical Branch | NA | 22 | 3626 |  |  | 222 | Reduction because NTC over thermal limit on border
20251224 | December | 2130 |  | 10556 | 131 |  | 10556 | 130 | -5421 | -5421 | 0 | Critical Branch | Critical Branch | NA | 1 | 5421 |  |  | 196
20251224 | December | 2230 |  | 10556 | 131 |  | 10556 | 130 | -5421 | -5421 | 0 | Critical Branch | Critical Branch | NA | 1 | 5421 |  |  | 196
20251224 | December | 2330 |  | 9751 | 206 |  | 9751 | 181 | -4602 | -4602 | 0 | Critical Branch | Critical Branch | NA | 25 | 4602 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 0030 |  | 9357 | 1138 |  | 9357 | 1102 | -5031 | -5031 | 0 | Critical Branch | Critical Branch | NA | 36 | 5031 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 0130 |  | 9357 | 1138 |  | 9357 | 1102 | -5031 | -5031 | 0 | Critical Branch | Critical Branch | NA | 36 | 5031 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 0230 |  | 9357 | 1138 |  | 9357 | 1102 | -5031 | -5031 | 0 | Critical Branch | Critical Branch | NA | 36 | 5031 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 0330 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251225 | December | 0430 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251225 | December | 0530 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251225 | December | 0630 | 9756 |  |  | 9754 |  |  | -2565 | -2565 | -2562 | Critical Branch | Critical Branch | 2 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border
20251225 | December | 0730 |  | 9341 | 1108 |  | 9341 | 1076 | -4909 | -4909 | 0 | Critical Branch | Critical Branch | NA | 32 | 4909 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 0830 |  | 9341 | 1108 |  | 9341 | 1076 | -4909 | -4909 | 0 | Critical Branch | Critical Branch | NA | 32 | 4909 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 0930 |  | 9783 | 1071 |  | 9783 | 1045 | -5334 | -5334 | 0 | Critical Branch | Critical Branch | NA | 26 | 5334 |  |  | 193 | Reduction because NTC over thermal limit on border
20251225 | December | 1030 |  | 9783 | 1071 |  | 9783 | 1045 | -5334 | -5334 | 0 | Critical Branch | Critical Branch | NA | 26 | 5334 |  |  | 193 | Reduction because NTC over thermal limit on border
20251225 | December | 1130 |  | 9783 | 1071 |  | 9783 | 1045 | -5334 | -5334 | 0 | Critical Branch | Critical Branch | NA | 26 | 5334 |  |  | 193 | Reduction because NTC over thermal limit on border
20251225 | December | 1230 |  | 9782 | 1046 |  | 9782 | 1023 | -5511 | -5511 | 0 | Critical Branch | Critical Branch | NA | 23 | 5511 |  |  | 193 | Reduction because NTC over thermal limit on border
20251225 | December | 1330 |  | 9782 | 1046 |  | 9782 | 1023 | -5511 | -5511 | 0 | Critical Branch | Critical Branch | NA | 23 | 5511 |  |  | 193 | Reduction because NTC over thermal limit on border
20251225 | December | 1430 |  | 9782 | 1046 |  | 9782 | 1023 | -5511 | -5511 | 0 | Critical Branch | Critical Branch | NA | 23 | 5511 |  |  | 193 | Reduction because NTC over thermal limit on border
20251225 | December | 1530 |  | 9383 | 1120 |  | 9383 | 1086 | -4937 | -4937 | 0 | Critical Branch | Critical Branch | NA | 34 | 4937 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 1630 |  | 9383 | 1120 |  | 9383 | 1086 | -4937 | -4937 | 0 | Critical Branch | Critical Branch | NA | 34 | 4937 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 1730 |  | 9383 | 1120 |  | 9383 | 1086 | -4937 | -4937 | 0 | Critical Branch | Critical Branch | NA | 34 | 4937 |  |  | 186 | Reduction because NTC over thermal limit on border
20251225 | December | 1830 |  | 9511 | 1169 |  | 9511 | 1128 | -5209 | -5209 | 0 | Critical Branch | Critical Branch | NA | 41 | 5209 |  |  | 188 | Reduction because NTC over thermal limit on border
20251225 | December | 1930 |  | 9511 | 1169 |  | 9511 | 1128 | -5209 | -5209 | 0 | Critical Branch | Critical Branch | NA | 41 | 5209 |  |  | 188 | Reduction because NTC over thermal limit on border
20251225 | December | 2030 |  | 9511 | 1169 |  | 9511 | 1128 | -5209 | -5209 | 0 | Critical Branch | Critical Branch | NA | 41 | 5209 |  |  | 188 | Reduction because NTC over thermal limit on border
20251225 | December | 2130 |  | 9288 | 1132 |  | 9288 | 1097 | -3098 | -3098 | 0 | Critical Branch | Critical Branch | NA | 35 | 3098 |  |  | 185 | Reduction because NTC over thermal limit on border
20251225 | December | 2230 |  | 9288 | 1132 |  | 9288 | 1097 | -3098 | -3098 | 0 | Critical Branch | Critical Branch | NA | 35 | 3098 |  |  | 185 | Reduction because NTC over thermal limit on border
20251225 | December | 2330 |  | 9288 | 1132 |  | 9288 | 1097 | -3098 | -3098 | 0 | Critical Branch | Critical Branch | NA | 35 | 3098 |  |  | 185 | Reduction because NTC over thermal limit on border
20251226 | December | 0030 |  | 10145 | 1126 |  | 10145 | 1091 | -5841 | -5841 | 0 | Critical Branch | Critical Branch | NA | 35 | 5841 |  |  | 199 | Reduction because NTC over thermal limit on border
20251226 | December | 0130 |  | 10145 | 1126 |  | 10145 | 1091 | -5841 | -5841 | 0 | Critical Branch | Critical Branch | NA | 35 | 5841 |  |  | 199 | Reduction because NTC over thermal limit on border
20251226 | December | 0230 |  | 10145 | 1126 |  | 10145 | 1091 | -5841 | -5841 | 0 | Critical Branch | Critical Branch | NA | 35 | 5841 |  |  | 199 | Reduction because NTC over thermal limit on border
20251226 | December | 0330 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | NA | 20 | 5205 |  |  | 187 | Reduction because NTC over thermal limit on border
20251226 | December | 0430 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | NA | 20 | 5205 |  |  | 187 | Reduction because NTC over thermal limit on border
20251226 | December | 0530 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | NA | 20 | 5205 |  |  | 187 | Reduction because NTC over thermal limit on border
20251226 | December | 0630 |  | 9409 | 1028 |  | 9409 | 1008 | -5205 | -5205 | 0 | Critical Branch | Critical Branch | NA | 20 | 5205 |  |  | 187 | Reduction because NTC over thermal limit on border
20251226 | December | 0730 |  | 9924 | 1016 |  | 9924 | 998 | -5833 | -5833 | 0 | Critical Branch | Critical Branch | NA | 18 | 5833 |  |  | 264 | Reduction because NTC over thermal limit on border
20251226 | December | 0830 |  | 9924 | 1016 |  | 9924 | 998 | -5833 | -5833 | 0 | Critical Branch | Critical Branch | NA | 18 | 5833 |  |  | 264 | Reduction because NTC over thermal limit on border
20251226 | December | 0930 |  | 10060 | 1156 |  | 10060 | 1117 | -4726 | -4726 | 0 | Critical Branch | Critical Branch | NA | 39 | 4726 |  |  | 197 | Reduction because NTC over thermal limit on border
20251226 | December | 1030 |  | 10060 | 1156 |  | 10060 | 1117 | -4726 | -4726 | 0 | Critical Branch | Critical Branch | NA | 39 | 4726 |  |  | 197 | Reduction because NTC over thermal limit on border
20251226 | December | 1130 |  | 10060 | 1156 |  | 10060 | 1117 | -4726 | -4726 | 0 | Critical Branch | Critical Branch | NA | 39 | 4726 |  |  | 197 | Reduction because NTC over thermal limit on border
20251226 | December | 1230 |  | 8758 | 918 |  | 8758 | 915 | -4149 | -4149 | 0 | Critical Branch | Critical Branch | NA | 3 | 4149 |  |  | 176 | Reduction because NTC over thermal limit on border
20251226 | December | 1330 |  | 8758 | 918 |  | 8758 | 915 | -4149 | -4149 | 0 | Critical Branch | Critical Branch | NA | 3 | 4149 |  |  | 176 | Reduction because NTC over thermal limit on border
20251226 | December | 1430 |  | 8758 | 918 |  | 8758 | 915 | -4149 | -4149 | 0 | Critical Branch | Critical Branch | NA | 3 | 4149 |  |  | 176 | Reduction because NTC over thermal limit on border
20251226 | December | 1530 |  | 10103 | 1040 |  | 10103 | 1018 | -7022 | -7022 | 0 | Critical Branch | Critical Branch | NA | 22 | 7022 |  |  | 198 | Reduction because NTC over thermal limit on border
20251226 | December | 1630 |  | 10103 | 1040 |  | 10103 | 1018 | -7022 | -7022 | 0 | Critical Branch | Critical Branch | NA | 22 | 7022 |  |  | 198 | Reduction because NTC over thermal limit on border
20251226 | December | 1730 |  | 10103 | 1040 |  | 10103 | 1018 | -7022 | -7022 | 0 | Critical Branch | Critical Branch | NA | 22 | 7022 |  |  | 198 | Reduction because NTC over thermal limit on border
20251226 | December | 1830 | 10459 |  |  | 10271 |  |  | -3287 | -3287 | -3099 | Critical Branch | Validation phase | 188 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9960 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251226 | December | 1930 | 10459 |  |  | 10271 |  |  | -3287 | -3287 | -3099 | Critical Branch | Validation phase | 188 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9960 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251226 | December | 2030 | 10459 |  |  | 10271 |  |  | -3287 | -3287 | -3099 | Critical Branch | Validation phase | 188 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9960 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251226 | December | 2130 |  | 10263 | 1101 |  | 10263 | 1070 | -6256 | -6256 | 0 | Critical Branch | Critical Branch | NA | 31 | 6256 |  |  | 201 | Reduction because NTC over thermal limit on border
20251226 | December | 2230 |  | 10263 | 1101 |  | 10263 | 1070 | -6256 | -6256 | 0 | Critical Branch | Critical Branch | NA | 31 | 6256 |  |  | 201 | Reduction because NTC over thermal limit on border
20251226 | December | 2330 |  | 10263 | 1101 |  | 10263 | 1070 | -6256 | -6256 | 0 | Critical Branch | Critical Branch | NA | 31 | 6256 |  |  | 201 | Reduction because NTC over thermal limit on border
20251227 | December | 0030 |  | 10318 | 1346 |  | 10318 | 1278 | -6595 | -6595 | 0 | Critical Branch | Critical Branch | NA | 68 | 6595 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0130 |  | 10318 | 1346 |  | 10318 | 1278 | -6595 | -6595 | 0 | Critical Branch | Critical Branch | NA | 68 | 6595 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0230 |  | 10318 | 1346 |  | 10318 | 1278 | -6595 | -6595 | 0 | Critical Branch | Critical Branch | NA | 68 | 6595 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0330 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | NA | 80 | 6255 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0430 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | NA | 80 | 6255 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0530 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | NA | 80 | 6255 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0630 |  | 10321 | 1426 |  | 10321 | 1346 | -6255 | -6255 | 0 | Critical Branch | Critical Branch | NA | 80 | 6255 |  |  | 202 | Reduction because NTC over thermal limit on border
20251227 | December | 0730 |  | 10223 | 1228 |  | 10223 | 1174 | -6330 | -6330 | 0 | Critical Branch | Critical Branch | NA | 54 | 6330 |  |  | 198 | Reduction because NTC over thermal limit on border
20251227 | December | 0830 |  | 10223 | 1228 |  | 10223 | 1174 | -6330 | -6330 | 0 | Critical Branch | Critical Branch | NA | 54 | 6330 |  |  | 198 | Reduction because NTC over thermal limit on border
20251227 | December | 0930 |  | 10130 | 1071 |  | 10130 | 1038 | -7719 | -7719 | 0 | Critical Branch | Critical Branch | NA | 33 | 7719 |  |  | 196 | Reduction because NTC over thermal limit on border
20251227 | December | 1030 |  | 10130 | 1071 |  | 10130 | 1038 | -7719 | -7719 | 0 | Critical Branch | Critical Branch | NA | 33 | 7719 |  |  | 196 | Reduction because NTC over thermal limit on border
20251227 | December | 1130 |  | 10130 | 1071 |  | 9866 | 1038 | -7719 | -7719 | 0 | Critical Branch | Critical Branch | NA | 297 | 7719 |  |  | 190 | Reduction because NTC over thermal limit on border
20251227 | December | 1230 |  | 8411 | 904 |  | 8411 | 894 | -7093 | -7093 | 0 | Critical Branch | Critical Branch | NA | 10 | 7093 |  |  | 169 | Reduction because NTC over thermal limit on border
20251227 | December | 1330 |  | 8411 | 904 |  | 8411 | 894 | -7093 | -7093 | 0 | Critical Branch | Critical Branch | NA | 10 | 7093 |  |  | 169 | Reduction because NTC over thermal limit on border
20251227 | December | 1430 |  | 8411 | 904 |  | 8411 | 894 | -7093 | -7093 | 0 | Critical Branch | Critical Branch | NA | 10 | 7093 |  |  | 169 | Reduction because NTC over thermal limit on border
20251227 | December | 1530 |  | 10334 | 1028 |  | 9843 | 1001 | -6928 | -6928 | 0 | Critical Branch | Critical Branch | NA | 518 | 6928 |  |  | 189 | Reduction because NTC over thermal limit on border
20251227 | December | 1630 |  | 10334 | 1028 |  | 10334 | 1001 | -6928 | -6928 | 0 | Critical Branch | Critical Branch | NA | 27 | 6928 |  |  | 199 | Reduction because NTC over thermal limit on border
20251227 | December | 1730 |  | 10334 | 1028 |  | 10334 | 1001 | -6928 | -6928 | 0 | Critical Branch | Critical Branch | NA | 27 | 6928 |  |  | 199 | Reduction because NTC over thermal limit on border
20251227 | December | 1830 |  | 10098 | 1071 |  | 10098 | 1038 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | NA | 33 | 7001 |  |  | 196 | Reduction because NTC over thermal limit on border
20251227 | December | 1930 |  | 10098 | 1071 |  | 10098 | 1038 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | NA | 33 | 7001 |  |  | 196 | Reduction because NTC over thermal limit on border
20251227 | December | 2030 |  | 10098 | 1071 |  | 10098 | 1038 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | NA | 33 | 7001 |  |  | 196 | Reduction because NTC over thermal limit on border
20251227 | December | 2130 |  | 10516 | 975 |  | 10489 | 975 | -7941 | -7941 | 0 | Critical Branch | Critical Branch | NA | 27 | 7941 |  |  | 385 | Reduction because NTC over thermal limit on border
20251227 | December | 2230 |  | 10516 | 975 |  | 10489 | 975 | -7941 | -7941 | 0 | Critical Branch | Critical Branch | NA | 27 | 7941 |  |  | 385 | Reduction because NTC over thermal limit on border
20251227 | December | 2330 |  | 9761 | 995 |  | 9735 | 995 | -7240 | -7240 | 0 | Critical Branch | Critical Branch | NA | 26 | 7240 |  |  | 365 | Reduction because NTC over thermal limit on border
20251228 | December | 0030 |  | 9037 | 1193 |  | 9037 | 1148 | -5191 | -5191 | 0 | Critical Branch | Critical Branch | NA | 45 | 5191 |  |  | 181 | Reduction because NTC over thermal limit on border
20251228 | December | 0130 |  | 9037 | 1193 |  | 9037 | 1148 | -5191 | -5191 | 0 | Critical Branch | Critical Branch | NA | 45 | 5191 |  |  | 181 | Reduction because NTC over thermal limit on border
20251228 | December | 0230 |  | 9037 | 1193 |  | 9037 | 1148 | -5191 | -5191 | 0 | Critical Branch | Critical Branch | NA | 45 | 5191 |  |  | 181 | Reduction because NTC over thermal limit on border
20251228 | December | 0330 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | NA | 49 | 5805 |  |  | 188 | Reduction because NTC over thermal limit on border
20251228 | December | 0430 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | NA | 49 | 5805 |  |  | 188 | Reduction because NTC over thermal limit on border
20251228 | December | 0530 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | NA | 49 | 5805 |  |  | 188 | Reduction because NTC over thermal limit on border
20251228 | December | 0630 |  | 9490 | 1224 |  | 9490 | 1175 | -5805 | -5805 | 0 | Critical Branch | Critical Branch | NA | 49 | 5805 |  |  | 188 | Reduction because NTC over thermal limit on border
20251228 | December | 0730 |  | 10098 | 1224 |  | 10087 | 1175 | -5719 | -5719 | 0 | Critical Branch | Critical Branch | NA | 60 | 5719 |  |  | 197 | Reduction because NTC over thermal limit on border
20251228 | December | 0830 |  | 10098 | 1224 |  | 8688 | 1175 | -5719 | -5719 | 0 | Critical Branch | Critical Branch | NA | 1459 | 5719 |  |  | 168 | Reduction because NTC over thermal limit on border
20251228 | December | 0930 |  | 7213 | 1352 |  | 7213 | 1284 | -3577 | -3577 | 0 | Critical Branch | Critical Branch | NA | 68 | 3577 |  |  | 150 | Reduction because NTC over thermal limit on border
20251228 | December | 1030 |  | 7213 | 1352 |  | 7213 | 1284 | -3577 | -3577 | 0 | Critical Branch | Critical Branch | NA | 68 | 3577 |  |  | 150 | Reduction because NTC over thermal limit on border
20251228 | December | 1130 |  | 7213 | 1352 |  | 7213 | 1284 | -3577 | -3577 | 0 | Critical Branch | Critical Branch | NA | 68 | 3577 |  |  | 150 | Reduction because NTC over thermal limit on border
20251228 | December | 1230 |  | 7067 | 948 |  | 7067 | 940 | -3831 | -3831 | 0 | Critical Branch | Critical Branch | NA | 8 | 3831 |  |  | 148 | Reduction because NTC over thermal limit on border
20251228 | December | 1330 |  | 7067 | 948 |  | 7067 | 940 | -3831 | -3831 | 0 | Critical Branch | Critical Branch | NA | 8 | 3831 |  |  | 148 | Reduction because NTC over thermal limit on border
20251228 | December | 1430 |  | 7067 | 948 |  | 7067 | 940 | -3831 | -3831 | 0 | Critical Branch | Critical Branch | NA | 8 | 3831 |  |  | 148 | Reduction because NTC over thermal limit on border
20251228 | December | 1530 |  | 9190 | 1181 |  | 8506 | 1138 | -6334 | -6334 | 0 | Critical Branch | Critical Branch | NA | 727 | 6334 |  |  | 168 | Reduction because NTC over thermal limit on border
20251228 | December | 1630 |  | 9190 | 1181 |  | 9190 | 1138 | -6334 | -6334 | 0 | Critical Branch | Critical Branch | NA | 43 | 6334 |  |  | 183 | Reduction because NTC over thermal limit on border
20251228 | December | 1730 |  | 9190 | 1181 |  | 9190 | 1138 | -6334 | -6334 | 0 | Critical Branch | Critical Branch | NA | 43 | 6334 |  |  | 183 | Reduction because NTC over thermal limit on border
20251228 | December | 1830 | 10508 |  |  | 9961 |  |  | -3451 | -3451 | -2903 | Critical Branch | Validation phase | 547 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9640 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251228 | December | 1930 | 10508 |  |  | 9961 |  |  | -3451 | -3451 | -2903 | Critical Branch | Validation phase | 547 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9640 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251228 | December | 2030 | 10508 |  |  | 9961 |  |  | -3451 | -3451 | -2903 | Critical Branch | Validation phase | 547 | NA | 0 |  |  | 365 | Reduction because NTC over thermal limit on border | 9640 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251228 | December | 2130 |  | 9901 | 1334 |  | 9901 | 1268 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | NA | 66 | 7001 |  |  | 195 | Reduction because NTC over thermal limit on border
20251228 | December | 2230 |  | 9901 | 1334 |  | 9901 | 1268 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | NA | 66 | 7001 |  |  | 195 | Reduction because NTC over thermal limit on border
20251228 | December | 2330 |  | 9901 | 1334 |  | 9901 | 1268 | -7001 | -7001 | 0 | Critical Branch | Critical Branch | NA | 66 | 7001 |  |  | 195 | Reduction because NTC over thermal limit on border
20251229 | December | 0030 |  | 7234 | 1052 |  | 7234 | 1029 | -274 | -274 | 0 | Critical Branch | Critical Branch | NA | 23 | 274 |  |  | 151 | Reduction because NTC over thermal limit on border
20251229 | December | 0130 |  | 7234 | 1052 |  | 7234 | 1029 | -274 | -274 | 0 | Critical Branch | Critical Branch | NA | 23 | 274 |  |  | 151 | Reduction because NTC over thermal limit on border
20251229 | December | 0230 |  | 7234 | 1052 |  | 7234 | 1029 | -274 | -274 | 0 | Critical Branch | Critical Branch | NA | 23 | 274 |  |  | 151 | Reduction because NTC over thermal limit on border
20251229 | December | 0330 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | NA | 38 | 14 |  |  | 150 | Reduction because NTC over thermal limit on border
20251229 | December | 0430 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | NA | 38 | 14 |  |  | 150 | Reduction because NTC over thermal limit on border
20251229 | December | 0530 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | NA | 38 | 14 |  |  | 150 | Reduction because NTC over thermal limit on border
20251229 | December | 0630 |  | 7161 | 1150 |  | 7161 | 1112 | -14 | -14 | 0 | Critical Branch | Critical Branch | NA | 38 | 14 |  |  | 150 | Reduction because NTC over thermal limit on border
20251229 | December | 0730 |  | 9145 | 925 |  | 8538 | 912 | -6532 | -6532 | 0 | Critical Branch | Critical Branch | NA | 620 | 6532 |  |  | 197 | Reduction because NTC over thermal limit on border
20251229 | December | 0830 |  | 9145 | 925 |  | 9145 | 912 | -6532 | -6532 | 0 | Critical Branch | Critical Branch | NA | 13 | 6532 |  |  | 211 | Reduction because NTC over thermal limit on border
20251229 | December | 0930 |  | 7818 | 941 |  | 7818 | 926 | -49 | -49 | 0 | Critical Branch | Critical Branch | NA | 15 | 49 |  |  | 190 | Reduction because NTC over thermal limit on border
20251229 | December | 1030 |  | 7818 | 941 |  | 7818 | 926 | -49 | -49 | 0 | Critical Branch | Critical Branch | NA | 15 | 49 |  |  | 190 | Reduction because NTC over thermal limit on border
20251229 | December | 1130 |  | 7818 | 941 |  | 7818 | 926 | -49 | -49 | 0 | Critical Branch | Critical Branch | NA | 15 | 49 |  |  | 190 | Reduction because NTC over thermal limit on border
20251229 | December | 1230 |  | 7818 | 736 |  | 7818 | 735 | -6861 | -6861 | 0 | Critical Branch | Critical Branch | NA | 1 | 6861 |  |  | 190
20251229 | December | 1330 |  | 7818 | 736 |  | 7818 | 735 | -6861 | -6861 | 0 | Critical Branch | Critical Branch | NA | 1 | 6861 |  |  | 190
20251229 | December | 1430 |  | 7818 | 736 |  | 7818 | 735 | -6861 | -6861 | 0 | Critical Branch | Critical Branch | NA | 1 | 6861 |  |  | 190
20251229 | December | 1530 |  | 9588 | 860 |  | 9230 | 833 | -2222 | -2222 | 0 | Critical Branch | Validation phase | NA | 385 | 2222 |  |  | 180 | Reduction because NTC over thermal limit on border | 9859 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1630 |  | 9588 | 860 |  | 9276 | 833 | -2222 | -2222 | 0 | Critical Branch | Validation phase | NA | 339 | 2222 |  |  | 187 | Reduction because NTC over thermal limit on border | 9859 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1730 |  | 9588 | 860 |  | 9276 | 833 | -2222 | -2222 | 0 | Critical Branch | Validation phase | NA | 339 | 2222 |  |  | 187 | Reduction because NTC over thermal limit on border | 9859 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1830 |  | 9482 | 833 |  | 8985 | 790 | -2833 | -2833 | 0 | Critical Branch | Validation phase | NA | 540 | 2833 |  |  | 219 |  | 9756 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251229 | December | 1930 |  | 9482 | 833 |  | 8985 | 790 | -2833 | -2833 | 0 | Critical Branch | Validation phase | NA | 540 | 2833 |  |  | 219 |  | 9756 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251229 | December | 2030 |  | 9482 | 833 |  | 8985 | 790 | -2833 | -2833 | 0 | Critical Branch | Validation phase | NA | 540 | 2833 |  |  | 219 |  | 9756 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251229 | December | 2130 |  | 9324 | 909 |  | 9324 | 899 | -2466 | -2466 | 0 | Critical Branch | Critical Branch | NA | 10 | 2466 |  |  | 183 | Reduction because NTC over thermal limit on border
20251229 | December | 2230 |  | 9324 | 909 |  | 9324 | 899 | -2466 | -2466 | 0 | Critical Branch | Critical Branch | NA | 10 | 2466 |  |  | 183 | Reduction because NTC over thermal limit on border
20251229 | December | 2330 |  | 8576 | 1004 |  | 8576 | 988 | -1566 | -1566 | 0 | Critical Branch | Critical Branch | NA | 16 | 1566 |  |  | 173 | Reduction because NTC over thermal limit on border
20251230 | December | 0030 |  | 8950 | 1059 |  | 8950 | 1035 | -2643 | -2643 | 0 | Critical Branch | Critical Branch | NA | 24 | 2643 |  |  | 179 | Reduction because NTC over thermal limit on border
20251230 | December | 0130 |  | 8950 | 1059 |  | 8950 | 1035 | -2643 | -2643 | 0 | Critical Branch | Critical Branch | NA | 24 | 2643 |  |  | 179 | Reduction because NTC over thermal limit on border
20251230 | December | 0230 |  | 8950 | 1059 |  | 8950 | 1035 | -2643 | -2643 | 0 | Critical Branch | Critical Branch | NA | 24 | 2643 |  |  | 179 | Reduction because NTC over thermal limit on border
20251230 | December | 0330 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 433 | NA | 0 |  |  | 356 |  | 8642 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0430 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 433 | NA | 0 |  |  | 356 |  | 8642 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0530 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 433 | NA | 0 |  |  | 356 |  | 8642 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0630 | 9405 |  |  | 8972 |  |  | -2787 | -2787 | -2354 | Critical Branch | Validation phase | 433 | NA | 0 |  |  | 356 |  | 8642 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20251230 | December | 0730 |  | 9719 | 1044 |  | 9719 | 1015 | -6101 | -6101 | 0 | Critical Branch | Critical Branch | NA | 29 | 6101 |  |  | 190 | Reduction because NTC over thermal limit on border
20251230 | December | 0830 |  | 9719 | 1044 |  | 9719 | 1015 | -6101 | -6101 | 0 | Critical Branch | Critical Branch | NA | 29 | 6101 |  |  | 190 | Reduction because NTC over thermal limit on border
20251230 | December | 0930 |  | 9605 | 963 |  | 9605 | 945 | -2627 | -2627 | 0 | Critical Branch | Critical Branch | NA | 18 | 2627 |  |  | 188 | Reduction because NTC over thermal limit on border
20251230 | December | 1030 |  | 9605 | 963 |  | 9605 | 945 | -2627 | -2627 | 0 | Critical Branch | Critical Branch | NA | 18 | 2627 |  |  | 188 | Reduction because NTC over thermal limit on border
20251230 | December | 1130 |  | 9605 | 963 |  | 9605 | 945 | -2627 | -2627 | 0 | Critical Branch | Critical Branch | NA | 18 | 2627 |  |  | 188 | Reduction because NTC over thermal limit on border
20251230 | December | 1230 |  | 9440 | 968 |  | 9440 | 949 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | NA | 19 | 3208 |  |  | 185 | Reduction because NTC over thermal limit on border
20251230 | December | 1330 |  | 9440 | 968 |  | 9440 | 949 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | NA | 19 | 3208 |  |  | 185 | Reduction because NTC over thermal limit on border
20251230 | December | 1430 |  | 9440 | 968 |  | 9440 | 949 | -3208 | -3208 | 0 | Critical Branch | Critical Branch | NA | 19 | 3208 |  |  | 185 | Reduction because NTC over thermal limit on border
20251230 | December | 1530 |  | 9585 | 1028 |  | 9585 | 1001 | -2965 | -2965 | 0 | Critical Branch | Critical Branch | NA | 27 | 2965 |  |  | 187 | Reduction because NTC over thermal limit on border
20251230 | December | 1630 |  | 9585 | 1028 |  | 9585 | 1001 | -2965 | -2965 | 0 | Critical Branch | Critical Branch | NA | 27 | 2965 |  |  | 187 | Reduction because NTC over thermal limit on border
20251230 | December | 1730 |  | 9585 | 1028 |  | 9585 | 1001 | -2965 | -2965 | 0 | Critical Branch | Critical Branch | NA | 27 | 2965 |  |  | 187 | Reduction because NTC over thermal limit on border
20251230 | December | 1830 |  | 9311 | 1006 |  | 9311 | 982 | -3132 | -3132 | 0 | Critical Branch | Critical Branch | NA | 24 | 3132 |  |  | 213 | Reduction because NTC over thermal limit on border
20251230 | December | 1930 |  | 9311 | 1006 |  | 9311 | 982 | -3132 | -3132 | 0 | Critical Branch | Critical Branch | NA | 24 | 3132 |  |  | 213 | Reduction because NTC over thermal limit on border
20251230 | December | 2030 |  | 9311 | 1006 |  | 9311 | 982 | -3132 | -3132 | 0 | Critical Branch | Critical Branch | NA | 24 | 3132 |  |  | 213 | Reduction because NTC over thermal limit on border
20251230 | December | 2130 |  | 8801 | 1006 |  | 8801 | 982 | -2427 | -2427 | 0 | Critical Branch | Critical Branch | NA | 24 | 2427 |  |  | 175 | Reduction because NTC over thermal limit on border
20251230 | December | 2230 |  | 8801 | 1006 |  | 8801 | 982 | -2427 | -2427 | 0 | Critical Branch | Critical Branch | NA | 24 | 2427 |  |  | 175 | Reduction because NTC over thermal limit on border
20251230 | December | 2330 |  | 8052 | 1101 |  | 8052 | 1070 | -1518 | -1518 | 0 | Critical Branch | Critical Branch | NA | 31 | 1518 |  |  | 164 | Reduction because NTC over thermal limit on border

## DA FLAGS processing
FLAGS processing
TSO | Long description | Short | Type | # of TS | CB | CO
AT | Reduction because NTC over thermal limit on border | Reduction because NTC over thermal limit on border | NTC over thermal limit | 1446
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | : CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | Overload | 429 | : 380kV Fiorano-Robbia [DIR] [CH], | 80KV GORLAGO-ROBBIA
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT Issues | 192
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 87 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 Pradella-Robbia + Filisur-Robbia
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 AVISE-RIDDES | Overload | 65 | 220kV Riddes - Valpelline [DIR] [CH], | -1 AVISE-RIDDES
CH | NTC correction | NTC correction | NTC over thermal limit | 58
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 55 | 220kV Avise - Riddes [OPP] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 54 | 380kV Bulciago - Soazza [DIR] [CH], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES | CNE: 220kV Avise - Riddes [OPP] [CH], C: N-1 VALPELLINE-RIDDES | Overload | 50 | 220kV Avise - Riddes [OPP] [CH], | -1 VALPELLINE-RIDDES
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 21 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | manual values cause of to high BackUP values | manual values cause of to high BackUP values | Not Specified | 32
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 31 | 220kV Riddes - Valpelline [DIR] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 11 | 380kV Bulciago - Soazza [DIR] [CH], | -2 Pradella-Robbia + Filisur-Robbia
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano | Overload | 9 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 Robbia-Gorlago + Piancamuno-S.Fiorano
CH | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | Overload | 9 | 220kV Pressy-Vallorcine [OPP] [CH], | -2 ALBERTVILLE-GRANDE ILE
CH | Values from previous day, cause of missing data | Values from previous day, cause of missing data | Process Fail | 9
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 VILLARODIN-VENAUS | Overload | 9 | 220kV Riddes - Valpelline [DIR] [CH], | -1 VILLARODIN-VENAUS
CH | Calculation not possible, values manuell adapted | Calculation not possible, values manuell adapted | Not Specified | 6
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Piancamuno-S.Fiorano | Overload | 6 | ted overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], | -2 Robbia-Gorlago + Piancamuno-S.Fiorano
CH | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | Overload | 6 | 380kV Lavorgo - Musignano [DIR] [CH], | -2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS
CH | Expected overloading on the following CNEC: CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | CNE: 380kV Filisur - Robbia [DIR], C: N-1 PRADELLA-ROBBIA | Overload | 5 | 380kV Filisur - Robbia [DIR],
CH | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | Overload | 4 | 220kV Pressy-Vallorcine [OPP] [CH],
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | Overload | 4 | 380kV Fiorano-Robbia [DIR][IT],
FR | Outage - Bus bar 2.1 GENISSIAT | Outage - Bus bar 2.1 GENISSIAT | Outage | 3
FR | Outage - PRAZ VILLARODIN | Outage - PRAZ VILLARODIN | Outage | 3
FR | Outage - CHAFFARD GRANDE ILE 1 | Outage - CHAFFARD GRANDE ILE 1 | Outage | 3
FR | Process failed: missing input | Process failed: missing input | Process Fail | 6
FR | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | Outage | 223
FR | Process fail during TSO validation phase | Process fail during TSO validation phase | Process Fail | 58
FR | Outage - Venaus - Piossasco | Outage - Venaus - Piossasco | Outage | 23
FR | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 | Outage -Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 | Outage | 54
FR | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1 | Outage - Planned maintenance of the HVDC G.ILE - PIOSSASCO 1 | Outage | 16
FR | Outage - RDCR FIL Link 1 & 2 | Outage - RDCR FIL Link 1 & 2 | Outage | 6
FR | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | Overload | 4 | #VALUE!
FR | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | Overload | 3 | #VALUE!
FR | Outage - OUTAGE TD LA PRAZ | Outage - OUTAGE TD LA PRAZ | Outage | 2
IT | Forecasted security violation | Forecasted security violation | Tense Situation | 39
SI | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | Outage | 24
Smoothing | Smoothing ramp | Smoothing ramp | Smoothing | 20

## ID Full Results Data 2025Q3 (hidden)
ID results
|  |  | TTC Adjustment |  |  | TTC Validated |  |  | ANTC |  |  | LimitedBy | [8 empty] | AT | AT | AT | AT | AT | AT | CH | CH | CH | CH | CH | CH | FR | FR | FR | FR | FR | FR | SI | SI | SI | SI | SI | SI | IT | IT | IT | IT | IT | IT
Business day | Month | Timestamp | TTC_Full_Import | TTCImport | TTCExport | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | 70% red | TTCRed_Import | TTCRed_Transit_Import | TTCRed_Transit_Export | TTRed_Transit | TTC and 70% red | FLAG | Bilateral - MNII | MNII | Reason | Bilateral - MIEC | MNIE | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason
2025-12-01 | December | 12:30 | 9648 |  |  | 9647 |  |  | -4454 | -4454 | -4452 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 105 | None | None | 259 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-01 | December | 13:30 | 9648 |  |  | 9647 |  |  | -4459 | -4459 | -4458 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 105 | None | None | 257 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-01 | December | 14:30 | 9648 |  |  | 9648 |  |  | -4486 | -4486 | -4485 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 264 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-01 | December | 15:30 |  | 9426 | 953 |  | 9426 | 934 | -2841 | -2841 | -2841 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 19 | 19 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 59 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-01 | December | 16:30 |  | 9581 | 953 |  | 9581 | 934 | -2875 | -2875 | -2875 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 19 | 19 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 31 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 17:30 |  | 9568 | 953 |  | 9568 | 934 | -2879 | -2879 | -2879 | Critical Branch | ID schedules | 0 | NA | 0 | 19 | 19 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 125 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 18:30 |  | 9458 | 965 |  | 9458 | 945 | -1738 | -1738 | -1738 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 20 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 19:30 |  | 9499 | 965 |  | 9499 | 945 | -1746 | -1746 | -1746 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 13 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 20:30 |  | 9116 | 965 |  | 9116 | 945 | -1681 | -1681 | -1681 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 146 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 21:30 |  | 8941 | 698 |  | 8940 | 698 | -3891 | -3891 | -3891 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 104 | None | None | 277 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 22:30 |  | 8629 | 698 |  | 8619 | 698 | -3742 | -3742 | -3742 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 10 | 0 | 10 | 0 | 1 | 104 | None | None | 263 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-01 | December | 23:30 |  | 8039 | 535 |  | 7927 | 538 | -3054 | -3054 | -3054 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 112 | -3 | 109 | 0 | 1 | 120 | None | None | 253 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 12:30 |  | 9087 | 939 |  | 9023 | 922 | 3669 | 233 | 3669 | Minimum Margin | TTC Validation phase - bilateral reduction | 3436 | NA | 64 | 17 | 81 | 233 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 112 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 13:30 |  | 9085 | 939 |  | 9022 | 922 | 3670 | 233 | 3670 | Minimum Margin | TTC Validation phase - bilateral reduction | 3437 | NA | 63 | 17 | 80 | 233 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 112 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 14:30 |  | 9198 | 939 |  | 9088 | 922 | 3630 | 233 | 3630 | Minimum Margin | TTC Validation phase - bilateral reduction | 3397 | NA | 110 | 17 | 127 | 233 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 100 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 15:30 |  | 9762 | 760 |  | 9563 | 760 | 3275 | 223 | 3275 | Minimum Margin | TTC Validation phase - bilateral reduction | 3052 | NA | 199 | 0 | 199 | 223 | 1 | 105 | None | None | 166 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 16:30 |  | 9395 | 760 |  | 9198 | 760 | 3477 | 223 | 3477 | Minimum Margin | TTC Validation phase - bilateral reduction | 3254 | NA | 197 | 0 | 197 | 223 | 1 | 103 | None | None | 189 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 17:30 |  | 8628 | 740 |  | 8634 | 740 | 3770 | 223 | 3770 | Minimum Margin | ID schedules | 3547 | NA | -6 | 0 | -6 | 223 | 1 | 104 | None | None | 198 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 18:30 |  | 8732 | 852 |  | 8731 | 847 | 3567 | 222 | 3567 | Minimum Margin | TTC Validation phase - bilateral reduction | 3345 | NA | 1 | 5 | 6 | 222 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 146 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 4351 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 19:30 |  | 9093 | 852 |  | 9018 | 847 | 3451 | 222 | 3451 | Minimum Margin | TTC Validation phase - bilateral reduction | 3229 | NA | 75 | 5 | 80 | 222 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 82 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 4351 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 20:30 |  | 9117 | 919 |  | 9037 | 905 | 3442 | 222 | 3442 | Minimum Margin | TTC Validation phase - bilateral reduction | 3220 | NA | 80 | 14 | 94 | 222 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 84 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 4351 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 21:30 | 9777 |  |  | 9777 |  |  | -2083 | -2083 | -2082 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | None | 281 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 22:30 | 9777 |  |  | 9777 |  |  | -2082 | -2082 | -2081 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | None | 281 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-02 | December | 23:30 | 8967 |  |  | 8967 |  |  | -1259 | -1259 | -1258 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 265 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-03 | December | 12:30 |  | 8574 | 881 |  | 8574 | 873 | -5389 | -5389 | -5389 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 8 | 8 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 108 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 13:30 |  | 8574 | 870 |  | 8574 | 863 | -5389 | -5389 | -5389 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 7 | 7 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 108 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 14:30 |  | 8566 | 846 |  | 8567 | 592 | -5385 | -5385 | -5385 | Critical Branch | ID schedules | 0 | NA | -1 | 254 | 253 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 108 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 15:30 | 8201 |  |  | 8201 |  |  | -4888 | -4888 | -4887 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 152 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 16:30 | 8201 |  |  | 8201 |  |  | -4864 | -4864 | -4862 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 152 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | None | Forecasted security violation | 0 | None | Forecasted security violation
2025-12-03 | December | 17:30 | 8201 |  |  | 8201 |  |  | -4858 | -4858 | -4857 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 160 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | None | Forecasted security violation | 0 | None | Forecasted security violation
2025-12-03 | December | 18:30 | 9826 |  |  | 9755 |  |  | -6259 | -6259 | -6187 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 71 | NA | NA | NA | 0 | 1 | 104 | None | None | 272 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | None | Forecasted security violation | 0 | None | Forecasted security violation
2025-12-03 | December | 19:30 | 9826 |  |  | 9825 |  |  | -6259 | -6259 | -6258 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 104 | None | None | 276 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | None | Forecasted security violation | 0 | None | Forecasted security violation
2025-12-03 | December | 20:30 | 9826 |  |  | 9022 |  |  | -6260 | -6260 | -5446 | Critical Branch | ID schedules | 0 | 804 | NA | NA | NA | 0 | 1 | 104 | None | None | 234 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 21:30 |  | 5902 | 544 |  | 5898 | 396 | 245 | -103 | 245 | Critical Branch | TTC Validation phase - bilateral reduction | 348 | NA | 4 | 148 | 152 | -103 | 1 | 67 | None | None | 242 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 22:30 |  | 6216 | 646 |  | 6474 | 667 | 296 | -103 | 296 | ID schedules | TTC Validation phase - bilateral reduction | 399 | NA | -258 | -21 | -279 | -103 | 1 | 103 | None | None | 116 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-03 | December | 23:30 |  | 5606 | 769 |  | 5914 | 781 | 630 | -103 | 630 | ID schedules | ID schedules | 733 | NA | -308 | -12 | -320 | -103 | 1 | 115 | None | None | 71 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-04 | December | 12:30 |  | 8247 | 816 |  | 8100 | 815 | -5000 | -5000 | -5000 | ID schedules | ID schedules | 0 | NA | 147 | 1 | 148 | 0 | 1 | 104 | None | None | 244 | None | None | None | 8759 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | 7812 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 13:30 |  | 8258 | 816 |  | 7781 | 810 | -5007 | -5007 | -5007 | ID schedules | ID schedules | 0 | NA | 477 | 6 | 483 | 0 | 1 | 104 | None | None | 245 | None | None | None | 8372 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | 7425 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 14:30 |  | 8190 | 745 |  | 6157 | 583 | -4969 | -4969 | -4969 | Critical Branch | ID schedules | 0 | NA | 2033 | 162 | 2195 | 0 | 1 | 94 | None | None | 254 | None | None | None | 7070 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | 6123 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 15:30 | 8589 |  |  | 8470 |  |  | -2234 | -2234 | -2150 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 119 | NA | NA | NA | 0 | 1 | 104 | None | None | 281 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 16:30 | 8589 |  |  | 8589 |  |  | -2236 | -2236 | -2230 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 239 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 17:30 | 8589 |  |  | 8588 |  |  | -2259 | -2259 | -2258 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 105 | None | None | 233 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 18:30 | 8112 |  |  | 8112 |  |  | -4588 | -4588 | -4587 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | None | 166 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 19:30 | 8112 |  |  | 8110 |  |  | -4678 | -4678 | -4675 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2 | NA | NA | NA | 0 | 1 | 105 | None | None | 41 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 20:30 | 8112 |  |  | 8112 |  |  | -4649 | -4649 | -4639 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | None | -2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 21:30 | 9805 |  |  | 9612 |  |  | -4880 | -4880 | -4687 | Critical Branch | ID schedules | 0 | 193 | NA | NA | NA | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 275 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 22:30 | 9805 |  |  | 9804 |  |  | -4880 | -4880 | -4878 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 104 | None | None | 281 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-04 | December | 23:30 | 8995 |  |  | 8995 |  |  | -4061 | -4061 | -4060 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 266 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 12:30 | 9702 |  |  | 9702 |  |  | -6562 | -6562 | -6560 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 13:30 | 9702 |  |  | 9702 |  |  | -6562 | -6562 | -6560 | Critical Branch | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 14:30 | 9702 |  |  | 9702 |  |  | -6562 | -6562 | -6560 | Critical Branch | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 15:30 | 8824 |  |  | 8824 |  |  | 3377 | -66 | 3717 | Critical Branch | Smoothing ramp | 3443 | 0 | NA | NA | NA | 274 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 16:30 | 8824 |  |  | 8824 |  |  | 3380 | -66 | 3886 | Critical Branch | ID schedules | 3446 | 0 | NA | NA | NA | 440 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | forecasted security violation | None | 0 | forecasted security violation
2025-12-05 | December | 17:30 | 8824 |  |  | 8824 |  |  | 3374 | -66 | 3880 | Critical Branch | ID schedules | 3440 | 0 | NA | NA | NA | 440 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | forecasted security violation | None | 0 | forecasted security violation
2025-12-05 | December | 18:30 |  | 9316 | 46 |  | 9302 | 36 | -4077 | -4077 | -4077 | Critical Branch | ID schedules | 0 | NA | 14 | 10 | 24 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 0 | forecasted security violation | None | 0 | forecasted security violation
2025-12-05 | December | 19:30 |  | 9323 | 49 |  | 9312 | 49 | -4082 | -4082 | -4082 | ID schedules | ID schedules | 0 | NA | 11 | 0 | 11 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 20:30 |  | 9316 | 69 |  | 9302 | 69 | -4078 | -4078 | -4078 | ID schedules | ID schedules | 0 | NA | 14 | 0 | 14 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 21:30 | 9902 |  |  | 9902 |  |  | -3124 | -3124 | -3122 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 22:30 | 9902 |  |  | 9902 |  |  | -3124 | -3124 | -3122 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-05 | December | 23:30 | 9092 |  |  | 9092 |  |  | -2310 | -2310 | -2308 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 12:30 |  | 6701 | 831 |  | 5206 | 831 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1495 | 0 | 1495 | 0 | 1 | 101 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-06 | December | 13:30 |  | 6926 | 831 |  | 5258 | 831 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1668 | 0 | 1668 | 0 | 1 | 101 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 253 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-06 | December | 14:30 |  | 6971 | 831 |  | 5605 | 831 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1366 | 0 | 1366 | 0 | 1 | 101 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -40 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-06 | December | 15:30 |  | 9157 | 744 |  | 6097 | 744 | -4343 | -4343 | -4343 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 3060 | 0 | 3060 | 0 | 1 | 103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 299 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-06 | December | 16:30 |  | 9157 | 744 |  | 7836 | 744 | -4343 | -4343 | -4343 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1321 | 0 | 1321 | 0 | 1 | 103 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 17:30 |  | 9821 | 744 |  | 8811 | 744 | -5185 | -5185 | -5185 | Critical Branch | ID schedules | 0 | NA | 1010 | 0 | 1010 | 0 | 1 | 103 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 18:30 | 10574 |  |  | 10180 |  |  | -5278 | -5278 | -4876 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 394 | NA | NA | NA | 0 | 1 | 104 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 19:30 | 10574 |  |  | 10569 |  |  | -5278 | -5278 | -5273 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 5 | NA | NA | NA | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 20:30 | 10574 |  |  | 10569 |  |  | -5278 | -5278 | -5273 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 5 | NA | NA | NA | 0 | 1 | 104 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 21:30 | 10201 |  |  | 10200 |  |  | -5347 | -5347 | -5345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 104 | None | None | 293 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 22:30 | 10201 |  |  | 10200 |  |  | -5347 | -5347 | -5345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 104 | None | None | 293 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-06 | December | 23:30 | 9391 |  |  | 9391 |  |  | -4489 | -4489 | -4486 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 278 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 12:30 |  | 6744 | 715 |  | 5434 | 715 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1310 | 0 | 1310 | 0 | 1 | 120 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 228 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-07 | December | 13:30 |  | 6728 | 715 |  | 5432 | 715 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1296 | 0 | 1296 | 0 | 1 | 120 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-07 | December | 14:30 |  | 6847 | 715 |  | 6781 | 715 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 66 | 0 | 66 | 0 | 1 | 120 | None | None | 39 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 15:30 |  | 8901 | 715 |  | 8128 | 715 | -3792 | -3792 | -3792 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 773 | 0 | 773 | 0 | 1 | 120 | None | None | 239 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 16:30 |  | 8902 | 715 |  | 8863 | 715 | -3793 | -3793 | -3793 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 39 | 0 | 39 | 0 | 1 | 120 | None | None | 285 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 17:30 |  | 8897 | 715 |  | 8897 | 715 | -3784 | -3784 | -3784 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | None | 295 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 18:30 | 10631 |  |  | 10602 |  |  | -5331 | -5331 | -5310 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 29 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 288 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 19:30 | 10631 |  |  | 10599 |  |  | -5331 | -5331 | -5308 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 32 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 20:30 | 10631 |  |  | 10599 |  |  | -5331 | -5331 | -5308 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 32 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 21:30 | 10061 |  |  | 10047 |  |  | -3630 | -3630 | -3620 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 14 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 22:30 | 10061 |  |  | 10047 |  |  | -3630 | -3630 | -3620 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 14 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-07 | December | 23:30 | 10061 |  |  | 10047 |  |  | -3630 | -3630 | -3620 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 14 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 12:30 |  | 4598 | 2446 |  | 4598 | 2637 | 516 | 0 | 516 | ID schedules | TTC Validation phase - bilateral reduction | 516 | NA | 0 | -191 | -191 | 0 | 1 | 118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-08 | December | 13:30 |  | 4687 | 2448 |  | 4687 | 2640 | 432 | 0 | 432 | ID schedules | TTC Validation phase - bilateral reduction | 432 | NA | 0 | -192 | -192 | 0 | 1 | 118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-08 | December | 14:30 |  | 4687 | 2434 |  | 4687 | 2620 | 438 | 0 | 438 | ID schedules | TTC Validation phase - bilateral reduction | 438 | NA | 0 | -186 | -186 | 0 | 1 | 118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-08 | December | 15:30 |  | 8076 | 851 |  | 4637 | 851 | 1838 | -109 | 1838 | ID schedules | TTC Validation phase - bilateral reduction | 1947 | NA | 3439 | 0 | 3439 | -109 | 1 | 120 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -120 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-08 | December | 16:30 |  | 8117 | 851 |  | 6783 | 851 | 1847 | -109 | 1847 | ID schedules | TTC Validation phase - bilateral reduction | 1956 | NA | 1334 | 0 | 1334 | -109 | 1 | 120 | None | None | 243 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 17:30 |  | 8123 | 851 |  | 7417 | 851 | 1848 | -109 | 1848 | ID schedules | TTC Validation phase - bilateral reduction | 1957 | NA | 706 | 0 | 706 | -109 | 1 | 120 | None | None | 285 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 18:30 |  | 9295 | 809 |  | 8889 | 809 | -3180 | -3180 | -3180 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 406 | 0 | 406 | 0 | 1 | 117 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 19:30 |  | 9275 | 809 |  | 9266 | 809 | -3176 | -3176 | -3176 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 9 | 0 | 9 | 0 | 1 | 117 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 20:30 |  | 9247 | 808 |  | 9240 | 808 | -3169 | -3169 | -3169 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 7 | 0 | 7 | 0 | 1 | 117 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 21:30 | 10444 |  |  | 10418 |  |  | -4624 | -4624 | -4606 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 22:30 | 10444 |  |  | 10418 |  |  | -4624 | -4624 | -4606 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-08 | December | 23:30 | 10444 |  |  | 10418 |  |  | -4624 | -4624 | -4606 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-09 | December | 12:30 |  | 8683 | 846 |  | 8683 | 842 | -3235 | -3235 | -3235 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 4 | 4 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 123 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 13:30 |  | 8681 | 846 |  | 8681 | 842 | -3234 | -3234 | -3234 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 4 | 4 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 123 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 14:30 |  | 8686 | 846 |  | 8686 | 842 | -3238 | -3238 | -3238 | Critical Branch | ID schedules | 0 | NA | 0 | 4 | 4 | 0 | 1 | 95 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 127 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 15:30 |  | 8977 | 831 |  | 8977 | 831 | -4542 | -4542 | -4542 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 201 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 16:30 |  | 9432 | 851 |  | 9432 | 851 | -4880 | -4880 | -4880 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 34 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 86 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 17:30 |  | 9365 | 831 |  | 9365 | 831 | -4908 | -4908 | -4908 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 96 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -44 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 18:30 |  | 8634 | 766 |  | 8634 | 618 | -4766 | -4766 | -4766 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 148 | 148 | 0 | 1 | -64 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 143 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 19:30 |  | 8797 | 676 |  | 8797 | 649 | -4850 | -4850 | -4850 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 27 | 27 | 0 | 1 | 58 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 31 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 20:30 |  | 8132 | 676 |  | 8068 | 676 | -4472 | -4472 | -4472 | Critical Branch | ID schedules | 0 | NA | 64 | 0 | 64 | 0 | 1 | 86 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 118 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 21:30 | 9824 |  |  | 9824 |  |  | -3691 | -3691 | -3690 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 246 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 22:30 | 9824 |  |  | 9824 |  |  | -3669 | -3669 | -3669 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -211 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 295 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-09 | December | 23:30 | 9014 |  |  | 9014 |  |  | -2857 | -2857 | -2857 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -106 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 280 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 12:30 | 9814 |  |  | 9785 |  |  | -3146 | -3146 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 29 | NA | NA | NA | 0 | 1 | 104 | None | None | 289 | None | None | None | 10160 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 13:30 | 9814 |  |  | 9784 |  |  | -3149 | -3149 | -3120 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | 104 | None | None | 281 | None | None | None | 10160 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 14:30 | 9814 |  |  | 9784 |  |  | -3149 | -3149 | -3120 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | 104 | None | None | 281 | None | None | None | 10160 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 15:30 |  | 8929 | 863 |  | 8930 | 120 | -2294 | -2294 | -2294 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -1 | 743 | 742 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 63 | None | Reduction because NTC over thermal limit on border | None | 8758 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | 9905 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 16:30 |  | 9477 | 871 |  | 9474 | 120 | -2636 | -2636 | -2636 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 3 | 751 | 754 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | -96 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 17:30 |  | 9560 | 871 |  | 9560 | 120 | -2831 | -2831 | -2831 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 751 | 751 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 146 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 18:30 |  | 9721 | 772 |  | 9721 | 772 | -2994 | -2994 | -2994 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 103 | None | None | 279 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-10 | December | 19:30 |  | 9860 | 772 |  | 9860 | 772 | -2991 | -2991 | -2991 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 103 | None | None | 300 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-10 | December | 20:30 |  | 9077 | 765 |  | 9078 | 765 | -2724 | -2724 | -2724 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -1 | 0 | -1 | 0 | 1 | 113 | None | None | 161 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-10 | December | 21:30 | 10127 |  |  | 10127 |  |  | -2803 | -2803 | -2801 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 291 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-10 | December | 22:30 | 10127 |  |  | 10127 |  |  | -2803 | -2803 | -2801 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | None | 291 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-10 | December | 23:30 | 9317 |  |  | 9317 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 276 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-11 | December | 12:30 | 6055 |  |  | 6055 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -104 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 13:30 | 5873 |  |  | 5912 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -39 | NA | NA | NA | 0 | 1 | 105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 14:30 | 6839 |  |  | 6868 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -29 | NA | NA | NA | 0 | 1 | -32 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 32 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 15:30 | 9348 |  |  | 8605 |  |  | -2839 | -2839 | -2150 | Critical Branch | ID schedules | 0 | 743 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 294 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 16:30 | 9348 |  |  | 9010 |  |  | -2839 | -2839 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 338 | NA | NA | NA | 0 | 1 | 104 | None | None | 294 | None | None | None | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-11 | December | 17:30 | 10248 |  |  | 9910 |  |  | -3634 | -3634 | -3295 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | 104 | None | None | 295 | None | None | None | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-11 | December | 18:30 | 9367 |  |  | 9367 |  |  | -2924 | -2924 | -2924 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 272 | None | None | None | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-11 | December | 19:30 | 9356 |  |  | 9356 |  |  | -2916 | -2916 | -2916 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 104 | None | None | 272 | None | None | None | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-11 | December | 20:30 | 9279 |  |  | 9278 |  |  | -2863 | -2863 | -2862 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 85 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 248 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 21:30 | 9529 |  |  | 9528 |  |  | -2898 | -2898 | -2897 | Critical Branch | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | 105 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 226 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 22:30 | 9529 |  |  | 9529 |  |  | -2869 | -2869 | -2869 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -104 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 295 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-11 | December | 23:30 | 8719 |  |  | 8719 |  |  | -2055 | -2055 | -2055 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 279 | None | None | None | 8850 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 12:30 |  | 4648 | 2274 |  | 4648 | 2513 | 2314 | 0 | 2314 | ID schedules | ID schedules | 2314 | NA | 0 | -239 | -239 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 13:30 |  | 4648 | 2784 |  | 4648 | 2890 | 2237 | 0 | 2237 | ID schedules | ID schedules | 2237 | NA | 0 | -106 | -106 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 14:30 |  | 4470 | 2278 |  | 4470 | 2516 | 2482 | 0 | 2482 | ID schedules | ID schedules | 2482 | NA | 0 | -238 | -238 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 15:30 | 7888 |  |  | 7888 |  |  | -4133 | -4133 | -4132 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 16:30 | 7888 |  |  | 7888 |  |  | -4152 | -4152 | -4151 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 17:30 | 7888 |  |  | 7888 |  |  | -4143 | -4143 | -4140 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 18:30 |  | 7959 | 698 |  | 7959 | 698 | -2404 | -2404 | -2404 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 19:30 |  | 8261 | 678 |  | 8267 | 678 | -2507 | -2507 | -2507 | Critical Branch | ID schedules | 0 | NA | -6 | 0 | -6 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 20:30 |  | 8265 | 698 |  | 8264 | 698 | -2511 | -2511 | -2511 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 21:30 | 9932 |  |  | 9932 |  |  | -2786 | -2786 | -2785 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 22:30 | 9932 |  |  | 9932 |  |  | -2786 | -2786 | -2785 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-12 | December | 23:30 | 9122 |  |  | 9122 |  |  | -2066 | -2066 | -2065 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 12:30 | 8204 |  |  | 8204 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-13 | December | 13:30 | 8204 |  |  | 8204 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-13 | December | 14:30 | 8204 |  |  | 8204 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-13 | December | 15:30 |  | 6459 | 798 |  | 6661 | 798 | 3603 | -18 | 3603 | ID schedules | ID schedules | 3621 | NA | -202 | 0 | -202 | -18 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 16:30 |  | 6382 | 798 |  | 6532 | 798 | 3590 | -18 | 3590 | ID schedules | ID schedules | 3608 | NA | -150 | 0 | -150 | -18 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 17:30 |  | 6550 | 580 |  | 6712 | 587 | 3598 | -18 | 3598 | ID schedules | ID schedules | 3616 | NA | -162 | -7 | -169 | -18 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 18:30 | 9890 |  |  | 9427 |  |  | -5877 | -5877 | -5397 | Critical Branch | ID schedules | 0 | 463 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 19:30 | 9890 |  |  | 9890 |  |  | -5864 | -5864 | -5863 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 20:30 | 9890 |  |  | 9890 |  |  | -5868 | -5868 | -5865 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 21:30 | 10368 |  |  | 10368 |  |  | -5311 | -5311 | -5310 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 22:30 | 10368 |  |  | 10368 |  |  | -5302 | -5302 | -5302 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-13 | December | 23:30 | 9558 |  |  | 9558 |  |  | -4488 | -4488 | -4488 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 12:30 |  | 5195 | 1262 |  | 5016 | 1299 | 2101 | 0 | 2101 | ID schedules | TTC Validation phase - bilateral reduction | 2101 | NA | 179 | -37 | 142 | 0 | 1 | 114 | None | None | 285 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 13:30 |  | 5196 | 1253 |  | 5086 | 1276 | 2100 | 0 | 2100 | ID schedules | TTC Validation phase - bilateral reduction | 2100 | NA | 110 | -23 | 87 | 0 | 1 | 105 | None | None | 285 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 14:30 |  | 4717 | 1211 |  | 4578 | 1210 | 2142 | 0 | 2142 | ID schedules | TTC Validation phase - bilateral reduction | 2142 | NA | 139 | 1 | 140 | 0 | 1 | 57 | None | None | 252 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 15:30 |  | 8827 | 133 |  | 7960 | 133 | -3320 | -3320 | -3320 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 867 | 0 | 867 | 0 | 1 | 117 | None | None | 206 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 16:30 |  | 8875 | 136 |  | 8707 | 136 | -3386 | -3386 | -3386 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 168 | 0 | 168 | 0 | 1 | 120 | None | None | 211 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 17:30 |  | 8874 | 136 |  | 8936 | 136 | -3404 | -3404 | -3404 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -62 | 0 | -62 | 0 | 1 | 120 | None | None | 226 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 18:30 |  | 9209 | 136 |  | 9209 | 136 | -1674 | -1674 | -1674 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 19:30 |  | 9209 | 136 |  | 9209 | 136 | -1674 | -1674 | -1674 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 20:30 |  | 9209 | 146 |  | 9209 | 146 | -1674 | -1674 | -1674 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 21:30 | 10112 |  |  | 10096 |  |  | -3250 | -3250 | -3239 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 22:30 | 10112 |  |  | 10096 |  |  | -3250 | -3250 | -3239 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-14 | December | 23:30 | 10112 |  |  | 10096 |  |  | -3250 | -3250 | -3239 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-15 | December | 12:30 |  | 8197 | 122 |  | 8197 | 122 | -2958 | -2958 | -2958 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 13:30 |  | 8197 | 122 |  | 8197 | 122 | -2958 | -2958 | -2958 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 14:30 |  | 8166 | 122 |  | 8166 | 122 | -2949 | -2949 | -2949 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 15:30 |  | 7186 | 122 |  | 7124 | 122 | -2258 | -2258 | -2258 | ID schedules | ID schedules | 0 | NA | 62 | 0 | 62 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 16:30 |  | 7395 | 122 |  | 7395 | 122 | -2356 | -2356 | -2356 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 17:30 |  | 7187 | 102 |  | 7130 | -270 | -2410 | -2410 | -2410 | Critical Branch | ID schedules | 0 | NA | 57 | 372 | 429 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 18:30 |  | 7940 | 796 |  | 7940 | 525 | -3332 | -3332 | -3332 | Critical Branch | ID schedules | 0 | NA | 0 | 271 | 271 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 19:30 |  | 8019 | 818 |  | 8019 | 818 | -3373 | -3373 | -3373 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 20:30 |  | 7801 | 818 |  | 7663 | 818 | -3226 | -3226 | -3226 | ID schedules | ID schedules | 0 | NA | 138 | 0 | 138 | 0 | 1 | None | None | None | None | None | None | None | 8049 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE" | None | 7468 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 21:30 | 9373 |  |  | 9373 |  |  | -3088 | -3088 | -3099 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 22:30 | 9373 |  |  | 9373 |  |  | -3070 | -3070 | -3093 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-15 | December | 23:30 | 8563 |  |  | 8563 |  |  | -2249 | -2249 | -2249 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-16 | December | 12:30 | 9493 |  |  | 9491 |  |  | -5468 | -5468 | -5469 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 20 | None | None | 52 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 13:30 | 9493 |  |  | 9491 |  |  | -5463 | -5463 | -5464 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 20 | None | None | 52 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 14:30 | 9493 |  |  | 9492 |  |  | -5488 | -5488 | -5489 | Critical Branch | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | 19 | None | Reduction because NTC over thermal limit on border | 60 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 15:30 |  | 7516 | 723 |  | 7654 | 700 | -5055 | -5055 | -5058 | ID schedules | ID schedules | 0 | NA | -138 | 23 | -115 | 0 | 1 | 20 | None | None | 55 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 16:30 |  | 7590 | 723 |  | 7749 | 700 | -5100 | -5100 | -5072 | ID schedules | ID schedules | 0 | NA | -159 | 23 | -136 | 0 | 1 | 20 | None | None | 55 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 17:30 |  | 7577 | 720 |  | 7761 | 700 | -5092 | -5092 | -5095 | ID schedules | ID schedules | 0 | NA | -184 | 20 | -164 | 0 | 1 | 19 | None | None | 55 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 18:30 |  | 7972 | 699 |  | 7971 | 699 | -2690 | -2690 | -2690 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | 20 | None | None | 57 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 19:30 |  | 7940 | 699 |  | 7941 | 699 | -2682 | -2682 | -2682 | ID schedules | ID schedules | 0 | NA | -1 | 0 | -1 | 0 | 1 | 19 | None | None | 57 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 20:30 |  | 7947 | 699 |  | 7947 | 699 | -2687 | -2687 | -2687 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 20 | None | None | 39 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 21:30 | 9297 |  |  | 9296 |  |  | -2130 | -2130 | -2130 | Critical Branch | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | 20 | None | None | 59 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 22:30 | 9297 |  |  | 9297 |  |  | -2115 | -2115 | -2115 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 20 | None | None | 59 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-16 | December | 23:30 | 8502 |  |  | 8502 |  |  | -1424 | -1424 | -1424 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 20 | None | None | 59 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 12:30 |  | 8797 | 816 |  | 8796 | 813 | -4235 | -4235 | -4235 | Critical Branch | Critical Branch | 0 | NA | 1 | 3 | 4 | 0 | 1 | 20 | None | Reduction because NTC over thermal limit on border | 27 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 13:30 |  | 8797 | 816 |  | 8796 | 813 | -4235 | -4235 | -4235 | Critical Branch | Critical Branch | 0 | NA | 1 | 3 | 4 | 0 | 1 | 20 | None | Reduction because NTC over thermal limit on border | 27 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 14:30 |  | 8797 | 816 |  | 8796 | 813 | -4235 | -4235 | -4235 | Critical Branch | Critical Branch | 0 | NA | 1 | 3 | 4 | 0 | 1 | 20 | None | Reduction because NTC over thermal limit on border | 27 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 15:30 |  | 8230 | 748 |  | 8229 | 747 | -5478 | -5478 | -5478 | ID schedules | ID schedules | 0 | NA | 1 | 1 | 2 | 0 | 1 | 20 | None | None | 16 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 16:30 |  | 8336 | 748 |  | 8336 | 747 | -5497 | -5497 | -5497 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | 20 | None | None | 11 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 17:30 |  | 8484 | 762 |  | 8484 | 761 | -5587 | -5587 | -5587 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | 35 | None | Reduction because NTC over thermal limit on border | 24 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 18:30 |  | 9037 | 809 |  | 9036 | 805 | -2565 | -2565 | -2565 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 4 | 5 | 0 | 1 | 35 | None | Reduction because NTC over thermal limit on border | 66 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 19:30 |  | 9037 | 809 |  | 9036 | 805 | -2565 | -2565 | -2565 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 4 | 5 | 0 | 1 | 35 | None | Reduction because NTC over thermal limit on border | 66 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 20:30 |  | 9037 | 809 |  | 8228 | 805 | -2565 | -2565 | -2565 | Critical Branch | ID schedules | 0 | NA | 809 | 4 | 813 | 0 | 1 | 35 | None | Reduction because NTC over thermal limit on border | 57 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 21:30 |  | 6572 | 55 |  | 6709 | 42 | 2878 | -78 | 2878 | ID schedules | ID schedules | 2956 | NA | -137 | 13 | -124 | -78 | 1 | 35 | None | Reduction because NTC over thermal limit on border | -10 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 22:30 |  | 6932 | 55 |  | 7067 | 42 | 2856 | -78 | 2856 | ID schedules | ID schedules | 2934 | NA | -135 | 13 | -122 | -78 | 1 | 35 | None | Reduction because NTC over thermal limit on border | -8 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-17 | December | 23:30 |  | 6346 | 85 |  | 6436 | 73 | 3163 | -78 | 3163 | ID schedules | ID schedules | 3241 | NA | -90 | 12 | -78 | -78 | 1 | 65 | None | Reduction because NTC over thermal limit on border | 29 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 12:30 |  | 3829 | 1954 |  | 3829 | 1963 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -9 | -9 | 0 | 1 | 35 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 102 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-18 | December | 13:30 |  | 3829 | 1954 |  | 3829 | 1962 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -8 | -8 | 0 | 1 | 35 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-18 | December | 14:30 |  | 3829 | 2114 |  | 3829 | 2247 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -133 | -133 | 0 | 1 | 35 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-18 | December | 15:30 |  | 7276 | 742 |  | 7276 | 742 | -618 | -618 | -618 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 35 | None | None | 38 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 16:30 |  | 7340 | 742 |  | 7340 | 742 | -658 | -658 | -658 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 35 | None | None | 33 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 17:30 |  | 7451 | 838 |  | 7451 | 838 | -855 | -855 | -855 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | None | 97 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 18:30 |  | 8251 | 837 |  | 8250 | 837 | -1528 | -1528 | -1528 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | 120 | None | None | 81 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 19:30 |  | 8249 | 837 |  | 8248 | 837 | -1523 | -1523 | -1523 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | 120 | None | None | 81 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 20:30 |  | 8174 | 837 |  | 7866 | 837 | -1481 | -1481 | -1481 | ID schedules | ID schedules | 0 | NA | 308 | 0 | 308 | 0 | 1 | 120 | None | None | 89 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 21:30 |  | 5916 | 141 |  | 6195 | 139 | 3401 | 78 | 3401 | Minimum Margin | TTC Validation phase - bilateral reduction | 3323 | NA | -279 | 2 | -277 | 78 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 5 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 4250 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 22:30 |  | 6280 | 141 |  | 6561 | 139 | 2997 | 78 | 2997 | Minimum Margin | TTC Validation phase - bilateral reduction | 2919 | NA | -281 | 2 | -279 | 78 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 6 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 4250 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-18 | December | 23:30 |  | 5253 | 186 |  | 5354 | 185 | 3392 | 78 | 3392 | Minimum Margin | TTC Validation phase - bilateral reduction | 3314 | NA | -101 | 1 | -100 | 78 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 161 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 4103 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 12:30 |  | 4227 | 494 |  | 4227 | 692 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -198 | -198 | 0 | 1 | 3 | None | None | 176 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 13:30 |  | 4227 | 658 |  | 4227 | 738 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -80 | -80 | 0 | 1 | 101 | None | None | 176 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 14:30 |  | 4227 | -192 |  | 4227 | -44 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -148 | -148 | 0 | 1 | 101 | None | None | -100 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 15:30 | 6054 |  |  | 6073 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -19 | NA | NA | NA | 0 | 1 | 115 | None | None | -114 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 16:30 | 6125 |  |  | 6125 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | 118 | None | None | -115 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 17:30 | 6426 |  |  | 6427 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 1 | 120 | None | None | -114 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 18:30 |  | 7104 | 837 |  | 7104 | 837 | -2013 | -2013 | -2013 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | None | -120 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 19:30 |  | 6604 | 837 |  | 6604 | 837 | -1630 | -1630 | -1630 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 20:30 |  | 5685 | 837 |  | 5685 | 837 | -921 | -921 | -921 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 120 | None | None | -120 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 21:30 |  | 8777 | 139 |  | 7598 | 139 | 3182 | -89 | 3182 | ID schedules | ID schedules | 3271 | NA | 1179 | 0 | 1179 | -89 | 1 | 120 | None | None | 218 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 22:30 |  | 8792 | 139 |  | 8410 | 139 | 3151 | -89 | 3151 | ID schedules | ID schedules | 3240 | NA | 382 | 0 | 382 | -89 | 1 | 120 | None | None | 261 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-19 | December | 23:30 |  | 7912 | 154 |  | 7911 | 154 | 3461 | -89 | 3461 | Critical Branch | ID schedules | 3550 | NA | 1 | 0 | 1 | -89 | 1 | 134 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 12:30 |  | 5256 | 837 |  | 5256 | 837 | 1895 | -82 | 1895 | ID schedules | ID schedules | 1977 | NA | 0 | 0 | 0 | -82 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 13:30 |  | 5237 | 837 |  | 5237 | 837 | 1386 | -82 | 1386 | ID schedules | ID schedules | 1468 | NA | 0 | 0 | 0 | -82 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 14:30 |  | 4983 | 837 |  | 4983 | 837 | 1540 | -82 | 1540 | ID schedules | ID schedules | 1622 | NA | 0 | 0 | 0 | -82 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 15:30 |  | 6871 | 837 |  | 6277 | 837 | -1786 | -1786 | -1786 | ID schedules | ID schedules | 0 | NA | 594 | 0 | 594 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 16:30 |  | 6897 | 837 |  | 6896 | 837 | -1794 | -1794 | -1794 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 17:30 |  | 6836 | 837 |  | 6834 | 837 | -1772 | -1772 | -1772 | ID schedules | ID schedules | 0 | NA | 2 | 0 | 2 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 18:30 | 6191 |  |  | 6216 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -25 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 19:30 | 6632 |  |  | 6633 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 20:30 | 6438 |  |  | 6438 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 21:30 | 10287 |  |  | 9146 |  |  | -5186 | -5186 | -3954 | Critical Branch | ID schedules | 0 | 1141 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 22:30 | 10287 |  |  | 9908 |  |  | -5181 | -5181 | -4758 | Critical Branch | ID schedules | 0 | 379 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-20 | December | 23:30 | 9472 |  |  | 9472 |  |  | -4363 | -4363 | -4363 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 12:30 |  | 6000 | 715 |  | 5301 | 715 | 1239 | -57 | 1239 | ID schedules | TTC Validation phase - bilateral reduction | 1296 | NA | 699 | 0 | 699 | -57 | 1 | 165 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 345 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-21 | December | 13:30 |  | 5932 | 715 |  | 5226 | 715 | 1241 | -57 | 1241 | ID schedules | TTC Validation phase - bilateral reduction | 1298 | NA | 706 | 0 | 706 | -57 | 1 | 164 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 345 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-21 | December | 14:30 |  | 6165 | 715 |  | 5484 | 715 | 1235 | -57 | 1235 | ID schedules | TTC Validation phase - bilateral reduction | 1292 | NA | 681 | 0 | 681 | -57 | 1 | 165 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 146 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-21 | December | 15:30 |  | 9298 | 1072 |  | 7661 | 1050 | -3 | -91 | -3 | ID schedules | ID schedules | 88 | NA | 1637 | 22 | 1659 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 350 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 16:30 |  | 9251 | 951 |  | 8246 | 971 | -32 | -91 | -32 | ID schedules | ID schedules | 59 | NA | 1005 | -20 | 985 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 17:30 |  | 9230 | 976 |  | 8821 | 964 | -33 | -91 | -33 | Critical Branch | ID schedules | 58 | NA | 409 | 12 | 421 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 18:30 | 7764 |  |  | 7764 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 164 | None | None | 365 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 19:30 | 8323 |  |  | 8323 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 164 | None | None | 365 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 20:30 | 7887 |  |  | 7887 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 164 | None | None | 138 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 21:30 |  | 8866 | 181 |  | 8870 | 181 | -3234 | -3234 | -3234 | ID schedules | ID schedules | 0 | NA | -4 | 0 | -4 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 22:30 |  | 8861 | 181 |  | 8861 | 181 | -3231 | -3231 | -3231 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-21 | December | 23:30 |  | 8861 | 181 |  | 8861 | 181 | -3231 | -3231 | -3231 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 12:30 | 5738 |  |  | 5821 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -83 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 13:30 | 5497 |  |  | 5704 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -207 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 14:30 | 6339 |  |  | 6455 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -116 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 15:30 |  | 7637 | 783 |  | 7637 | 783 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 16:30 |  | 8135 | 784 |  | 8135 | 784 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 17:30 |  | 8201 | 784 |  | 8201 | 784 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 18:30 | 9548 |  |  | 9321 |  |  | -1822 | -1822 | -1816 | Critical Branch | ID schedules | 0 | 227 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 19:30 | 9548 |  |  | 9275 |  |  | -703 | -703 | -690 | Critical Branch | ID schedules | 0 | 273 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 20:30 | 9548 |  |  | 7769 |  |  | -660 | -660 | 859 | Critical Branch | ID schedules | 0 | 1779 | NA | NA | NA | 859 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 21:30 | 6069 |  |  | 6069 |  |  | 0 | 0 | 3553 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 3553 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 22:30 | 6069 |  |  | 6069 |  |  | 0 | 0 | 3553 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 3553 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-22 | December | 23:30 | 5254 |  |  | 5254 |  |  | 0 | 0 | 3906 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 3906 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 12:30 | 4166 |  |  | 4166 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 13:30 | 4028 |  |  | 4028 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 14:30 | 4598 |  |  | 4598 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 15:30 | 10529 |  |  | 6989 |  |  | 0 | 0 | 2953 | Critical Branch | ID schedules | 0 | 3540 | NA | NA | NA | 2953 | 1 | 120 | None | None | 215 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 16:30 | 10529 |  |  | 7851 |  |  | 0 | 0 | 2901 | Critical Branch | ID schedules | 0 | 2678 | NA | NA | NA | 2901 | 1 | 120 | None | None | 273 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 17:30 | 10529 |  |  | 9096 |  |  | 0 | 0 | 2009 | Critical Branch | Smoothing ramp | 0 | 1433 | NA | NA | NA | 2009 | 1 | 120 | None | None | 330 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 18:30 |  | 8791 | 996 |  | 8790 | 973 | -2231 | -2231 | -2231 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 23 | 24 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 175 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 19:30 |  | 8791 | 981 |  | 8790 | 960 | -2231 | -2231 | -2231 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 21 | 22 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 175 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 20:30 |  | 8791 | 996 |  | 8790 | 973 | -2231 | -2231 | -2231 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 23 | 24 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 175 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 21:30 |  | 9166 | 995 |  | 9165 | 972 | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | NA | 1 | 23 | 24 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 385 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 22:30 |  | 9166 | 995 |  | 9165 | 972 | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | NA | 1 | 23 | 24 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 385 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-23 | December | 23:30 |  | 8483 | 1090 |  | 8482 | 1061 | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | NA | 1 | 29 | 30 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 365 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 12:30 |  | 6736 | 917 |  | 6735 | 907 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 10 | 11 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 142 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 13:30 |  | 6736 | 917 |  | 6735 | 907 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 10 | 11 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 142 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 14:30 |  | 6736 | 917 |  | 6735 | 907 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 10 | 11 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 142 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 15:30 | 9754 |  |  | 8680 |  |  | -4043 | -4043 | -2985 | Critical Branch | Smoothing ramp | 0 | 1074 | NA | NA | NA | 0 | 1 | 120 | None | None | 320 | None | None | None | 9255 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 16:30 | 9754 |  |  | 9752 |  |  | -4043 | -4043 | -4041 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 120 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 17:30 | 9754 |  |  | 9752 |  |  | -4043 | -4043 | -4041 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 120 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 18:30 | 9458 |  |  | 9456 |  |  | -3091 | -3091 | -3089 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 120 | None | None | 353 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 19:30 | 9458 |  |  | 9456 |  |  | -3091 | -3091 | -3089 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 120 | None | None | 353 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 20:30 | 9458 |  |  | 9456 |  |  | -3091 | -3091 | -3089 | Critical Branch | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 120 | None | None | 353 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 21:30 |  | 8723 | 832 |  | 8722 | 832 | -2993 | -2993 | -2993 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | 119 | None | None | 174 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 22:30 |  | 8723 | 832 |  | 8722 | 832 | -2993 | -2993 | -2993 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | 119 | None | None | 174 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-24 | December | 23:30 |  | 8080 | 897 |  | 7973 | 896 | -2254 | -2254 | -2254 | Critical Branch | Min import NTC Threshold | 0 | NA | 107 | 1 | 108 | 0 | 1 | 165 | None | None | 192 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 12:30 |  | 5148 | 1042 |  | 5147 | 1023 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 19 | 20 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 116 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 13:30 |  | 5148 | 1042 |  | 5147 | 1023 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 19 | 20 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 116 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 14:30 |  | 5148 | 1042 |  | 5147 | 1023 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 19 | 20 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 116 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 15:30 |  | 4393 | 1116 |  | 4647 | 1086 | -327 | -327 | -327 | ID schedules | ID schedules | 0 | NA | -254 | 30 | -224 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 16:30 |  | 4388 | 1116 |  | 4644 | 1086 | -326 | -326 | -326 | ID schedules | ID schedules | 0 | NA | -256 | 30 | -226 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 284 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 17:30 |  | 4524 | 1116 |  | 4771 | 1086 | -435 | -435 | -435 | ID schedules | ID schedules | 0 | NA | -247 | 30 | -217 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 287 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 18:30 | 9429 |  |  | 6876 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | 2553 | NA | NA | NA | 0 | 1 | 165 | None | None | 255 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 19:30 | 9429 |  |  | 8375 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | 1054 | NA | NA | NA | 0 | 1 | 165 | None | None | 315 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 20:30 | 9429 |  |  | 9427 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 165 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 21:30 |  | 8514 | 1127 |  | 8513 | 1096 | -180 | -180 | -180 | Critical Branch | ID schedules | 0 | NA | 1 | 31 | 32 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 172 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 22:30 |  | 8514 | 1127 |  | 8513 | 1096 | -180 | -180 | -180 | Critical Branch | ID schedules | 0 | NA | 1 | 31 | 32 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 172 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-25 | December | 23:30 |  | 8514 | 1127 |  | 8513 | 1096 | -180 | -180 | -180 | Critical Branch | ID schedules | 0 | NA | 1 | 31 | 32 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 172 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 12:30 |  | 3903 | 928 |  | 3903 | 923 | 1065 | -78 | 1065 | ID schedules | ID schedules | 1143 | NA | 0 | 5 | 5 | -78 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 0 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 13:30 |  | 4008 | 928 |  | 4008 | 923 | 1007 | -78 | 1007 | ID schedules | ID schedules | 1085 | NA | 0 | 5 | 5 | -78 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 0 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 14:30 |  | 3864 | 928 |  | 3864 | 923 | 1050 | -78 | 1050 | ID schedules | ID schedules | 1128 | NA | 0 | 5 | 5 | -78 | 1 | 165 | None | Reduction because NTC over thermal limit on border | -164 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 15:30 |  | 7242 | 1036 |  | 4769 | 1018 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 2473 | 18 | 2491 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 85 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 16:30 |  | 7242 | 1038 |  | 5737 | 1028 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 1505 | 10 | 1515 | 0 | 1 | 175 | None | Reduction because NTC over thermal limit on border | 116 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 17:30 |  | 7242 | 1038 |  | 7135 | 1028 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 107 | 10 | 117 | 0 | 1 | 175 | None | Reduction because NTC over thermal limit on border | 148 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 18:30 |  | 8861 | 1041 |  | 8562 | 1019 | -2868 | -2868 | -2868 | Critical Branch | Smoothing ramp | 0 | NA | 299 | 22 | 321 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 171 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 19:30 |  | 8861 | 996 |  | 8860 | 981 | -2868 | -2868 | -2868 | Critical Branch | Critical Branch | 0 | NA | 1 | 15 | 16 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 178 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 20:30 |  | 8861 | 1041 |  | 8860 | 1019 | -2868 | -2868 | -2868 | Critical Branch | Critical Branch | 0 | NA | 1 | 22 | 23 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 178 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 21:30 |  | 7719 | 1096 |  | 7718 | 1070 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 26 | 27 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 159 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 22:30 |  | 7719 | 1096 |  | 7718 | 1070 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 26 | 27 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 159 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-26 | December | 23:30 |  | 7719 | 1096 |  | 7718 | 1070 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 26 | 27 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 159 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 12:30 | 2801 |  |  | 2802 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 1 | 120 | None | None | -120 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 13:30 | 2385 |  |  | 2385 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 14:30 | 2452 |  |  | 2452 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 15:30 | 3200 |  |  | 3200 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -120 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 16:30 | 3710 |  |  | 3710 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 17:30 | 4020 |  |  | 4020 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 18:30 | 4100 |  |  | 4100 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 19:30 | 3900 |  |  | 3900 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 20:30 | 3900 |  |  | 3900 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -119 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 21:30 |  | 10703 | 1140 |  | 5678 | 1110 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 5025 | 30 | 5055 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 96 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 22:30 |  | 10703 | 1140 |  | 6512 | 1110 | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | NA | 4191 | 30 | 4221 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 126 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-27 | December | 23:30 |  | 10020 | 1235 |  | 7914 | 1184 | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | NA | 2106 | 51 | 2157 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 161 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 12:30 |  | 4392 | 946 |  | 4342 | 940 | 225 | -97 | 225 | ID schedules | ID schedules | 322 | NA | 50 | 6 | 56 | -97 | 1 | 165 | None | Reduction because NTC over thermal limit on border | -165 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 13:30 |  | 3980 | 946 |  | 3980 | 940 | 225 | -97 | 225 | ID schedules | ID schedules | 322 | NA | 0 | 6 | 6 | -97 | 1 | 165 | None | Reduction because NTC over thermal limit on border | -164 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 14:30 |  | 4049 | 946 |  | 4049 | 940 | 225 | -97 | 225 | ID schedules | ID schedules | 322 | NA | 0 | 6 | 6 | -97 | 1 | 165 | None | Reduction because NTC over thermal limit on border | -164 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 15:30 |  | 9306 | 1209 |  | 5542 | 1162 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 3764 | 47 | 3811 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 87 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 16:30 |  | 9306 | 1209 |  | 6240 | 1162 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 3066 | 47 | 3113 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 118 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 17:30 |  | 9306 | 1209 |  | 7266 | 1162 | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | NA | 2040 | 47 | 2087 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 149 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 18:30 |  | 8737 | 912 |  | 8682 | 909 | -3078 | -3078 | -3078 | Critical Branch | Smoothing ramp | 0 | NA | 55 | 3 | 58 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 174 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 19:30 |  | 8737 | 896 |  | 8736 | 896 | -3078 | -3078 | -3078 | ID schedules | Min import NTC Threshold | 0 | NA | 1 | 0 | 1 | 0 | 1 | 165 | None | None | 176 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 20:30 |  | 8737 | 912 |  | 8736 | 909 | -3078 | -3078 | -3078 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 3 | 4 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 176 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 21:30 | 8739 |  |  | 8737 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 2 | NA | NA | NA | 0 | 1 | 164 | None | None | 335 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 22:30 | 8739 |  |  | 8737 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 2 | NA | NA | NA | 0 | 1 | 164 | None | None | 335 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-28 | December | 23:30 | 8739 |  |  | 8737 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 2 | NA | NA | NA | 0 | 1 | 157 | None | None | 335 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 12:30 | 4923 |  |  | 4921 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 2 | NA | NA | NA | 0 | 1 | 120 | None | None | 216 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 13:30 | 4923 |  |  | 4922 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | 120 | None | None | 216 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 14:30 | 4923 |  |  | 4915 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 8 | NA | NA | NA | 0 | 1 | 120 | None | None | 39 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 15:30 |  | 5581 | 832 |  | 5713 | 831 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -132 | 1 | -131 | 0 | 1 | 119 | None | None | 339 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 16:30 |  | 5623 | 832 |  | 5859 | 831 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -236 | 1 | -235 | 0 | 1 | 119 | None | None | 358 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 17:30 |  | 5623 | 832 |  | 5859 | 831 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -236 | 1 | -235 | 0 | 1 | 119 | None | None | 358 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 18:30 |  | 8266 | 924 |  | 7773 | 909 | 719 | 229 | 719 | Minimum Margin | Smoothing ramp | 490 | NA | 493 | 15 | 508 | 229 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 152 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 19:30 |  | 8266 | 909 |  | 8265 | 900 | 719 | 229 | 719 | Minimum Margin | Min import NTC Threshold | 490 | NA | 1 | 9 | 10 | 229 | 1 | 124 | None | Reduction because NTC over thermal limit on border | 163 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 20:30 |  | 8266 | 924 |  | 8265 | 909 | 719 | 229 | 719 | Minimum Margin | Min import NTC Threshold | 490 | NA | 1 | 15 | 16 | 229 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 163 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 21:30 |  | 8594 | 925 |  | 8593 | 912 | -4299 | -4299 | -4299 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 13 | 14 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 172 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 22:30 |  | 8594 | 925 |  | 8593 | 912 | -4299 | -4299 | -4299 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 13 | 14 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 172 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-29 | December | 23:30 |  | 7950 | 1020 |  | 7843 | 1001 | -3565 | -3565 | -3565 | Critical Branch | Min import NTC Threshold | 0 | NA | 107 | 19 | 126 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 190 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 12:30 |  | 2159 | 450 |  | 2235 | 449 | 3422 | 0 | 3422 | ID schedules | ID schedules | 3422 | NA | -76 | 1 | -75 | 0 | 1 | 67 | None | None | 189 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 13:30 |  | 3615 | 965 |  | 3867 | 949 | 748 | 0 | 748 | ID schedules | ID schedules | 748 | NA | -252 | 16 | -236 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 114 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 14:30 |  | 4258 | 965 |  | 4627 | 949 | 825 | 0 | 825 | ID schedules | ID schedules | 825 | NA | -369 | 16 | -353 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 55 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 15:30 |  | 4956 | 1024 |  | 5306 | 1001 | 1100 | 0 | 1100 | ID schedules | ID schedules | 1100 | NA | -350 | 23 | -327 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 306 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 16:30 |  | 5327 | 1024 |  | 5590 | 1001 | 1070 | 0 | 1070 | ID schedules | ID schedules | 1070 | NA | -263 | 23 | -240 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 329 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 17:30 |  | 5345 | 1024 |  | 5604 | 1001 | 1069 | 0 | 1069 | ID schedules | ID schedules | 1069 | NA | -259 | 23 | -236 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 330 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 18:30 | 10372 |  |  | 7875 |  |  | -2674 | -2674 | -242 | Critical Branch | Smoothing ramp | 0 | 2497 | NA | NA | NA | 0 | 1 | 120 | None | None | 284 | None | None | None | 9714 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Divaca-Redipuglia + Divaca-Padriciano" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 19:30 | 10372 |  |  | 9375 |  |  | -2674 | -2674 | -1704 | Critical Branch | Smoothing ramp | 0 | 997 | NA | NA | NA | 0 | 1 | 120 | None | None | 342 | None | None | None | 9812 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Divaca-Redipuglia + Divaca-Padriciano" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 20:30 | 10372 |  |  | 9834 |  |  | -2674 | -2674 | -2151 | Critical Branch | Smoothing ramp | 0 | 538 | NA | NA | NA | 0 | 1 | 120 | None | None | 360 | None | None | None | 9871 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 21:30 |  | 9665 | 1042 |  | 7828 | 1013 | 0 | 0 | 0 | GSK Limitation | Full import calculation | 0 | NA | 1837 | 29 | 1866 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 159 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 22:30 |  | 9665 | 1042 |  | 7828 | 1013 | 0 | 0 | 0 | GSK Limitation | Full import calculation | 0 | NA | 1837 | 29 | 1866 | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 159 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-30 | December | 23:30 |  | 8982 | 1137 |  | 7077 | 1100 | 0 | 0 | 0 | GSK Limitation | Full import calculation | 0 | NA | 1905 | 37 | 1942 | 0 | 1 | 165 | None | Reduction because NTC over thermal limit on border | 150 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-12-31 | December | 12:30 | 2972 |  |  | 2971 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 120 | None | None | 190 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 13:30 | 2972 |  |  | 2844 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 128 | NA | NA | NA | 0 | 1 | 120 | None | None | 125 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 14:30 | 2972 |  |  | 2941 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 31 | NA | NA | NA | 0 | 1 | 137 | None | None | -88 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 15:30 |  | 7475 | 1059 |  | 5307 | 1059 | -873 | -873 | -873 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 2168 | 0 | 2168 | 0 | 1 | 151 | None | None | 82 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 16:30 |  | 7475 | 1059 |  | 6019 | 1059 | -873 | -873 | -873 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1456 | 0 | 1456 | 0 | 1 | 151 | None | None | 113 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 17:30 |  | 7475 | 1059 |  | 7291 | 1059 | -873 | -873 | -873 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 184 | 0 | 184 | 0 | 1 | 151 | None | None | 144 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 18:30 |  | 9235 | 1047 |  | 8692 | 1040 | -3249 | -3249 | -3249 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 543 | 7 | 550 | 0 | 1 | 144 | None | Reduction because NTC over thermal limit on border | 165 | None | Reduction because NTC over thermal limit on border | None | 9486 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | None | 9034 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 19:30 |  | 9235 | 1032 |  | 9173 | 1023 | -3249 | -3249 | -3249 | Critical Branch | Validation phase | 0 | NA | 62 | 9 | 71 | 0 | 1 | 144 | None | Reduction because NTC over thermal limit on border | 182 | None | Reduction because NTC over thermal limit on border | None | 9486 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | None | 8984 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 20:30 |  | 9235 | 1047 |  | 8660 | 1011 | -3249 | -3249 | -3249 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 575 | 36 | 611 | 0 | 1 | 144 | None | Reduction because NTC over thermal limit on border | 182 | None | Reduction because NTC over thermal limit on border | None | 9446 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 SOAZZA-BULCIAGO" | None | 8471 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 SOAZZA-BULCIAGO" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 21:30 |  | 8911 | 973 |  | 8748 | 973 | -3784 | -3784 | -3784 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 163 | 0 | 163 | 0 | 1 | 139 | None | None | 177 | None | None | None | 9144 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | None | 8558 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 22:30 |  | 8911 | 973 |  | 8411 | 973 | -3784 | -3784 | -3784 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 500 | 0 | 500 | 0 | 1 | 139 | None | None | 177 | None | None | None | 9144 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | None | 8221 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-12-31 | December | 23:30 |  | 8268 | 1069 |  | 7869 | 1068 | -3017 | -3017 | -3017 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 399 | 1 | 400 | 0 | 1 | 190 | None | None | 168 | None | None | None | 8334 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | None | 7680 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-01 | November | 12:30 |  | 6195 | 133 |  | 6195 | 133 | -2117 | -2117 | -2117 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-01 | November | 13:30 |  | 6454 | 197 |  | 6454 | 197 | -2163 | -2163 | -2163 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-01 | November | 14:30 |  | 6206 | 133 |  | 6206 | 133 | -2231 | -2231 | -2231 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-01 | November | 15:30 | 6917 |  |  | 6917 |  |  | -2291 | -2291 | -2291 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-01 | November | 16:30 | 7455 |  |  | 7455 |  |  | -2636 | -2636 | -2636 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 17:30 | 7445 |  |  | 7445 |  |  | -2629 | -2629 | -2629 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 18:30 | 7501 |  |  | 7501 |  |  | -3466 | -3466 | -3466 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 19:30 | 7501 |  |  | 7501 |  |  | -3466 | -3466 | -3466 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 20:30 | 7501 |  |  | 7501 |  |  | -3466 | -3466 | -3466 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 21:30 | 8920 |  |  | 8920 |  |  | -3868 | -3868 | -3866 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 22:30 | 8920 |  |  | 8920 |  |  | -3868 | -3868 | -3866 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-01 | November | 23:30 | 8920 |  |  | 8920 |  |  | -3868 | -3868 | -3866 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-02 | November | 12:30 |  | 7805 | 191 |  | 6526 | -384 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1279 | 575 | 1854 | 0 | 1 | -412 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 412 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-02 | November | 13:30 |  | 7805 | 191 |  | 6645 | 129 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1160 | 62 | 1222 | 0 | 1 | 101 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 402 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-02 | November | 14:30 |  | 7805 | 191 |  | 6727 | 10 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1078 | 181 | 1259 | 0 | 1 | -210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 402 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-02 | November | 15:30 |  | 7552 | 1260 |  | 5089 | 1259 | -3490 | -3490 | -3490 | Critical Branch | ID schedules | 0 | NA | 2463 | 1 | 2464 | 0 | 1 | 79 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 428 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-02 | November | 16:30 |  | 7552 | 1280 |  | 6501 | 1279 | -3490 | -3490 | -3490 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1051 | 1 | 1052 | 0 | 1 | 170 | None | None | 428 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | forecasted violations | 3800 | None | forecasted violations
2025-11-02 | November | 17:30 |  | 7552 | 1259 |  | 6687 | 1257 | -3490 | -3490 | -3490 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 865 | 2 | 867 | 0 | 1 | 180 | None | None | 428 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted violations | 3500 | None | forecasted violations
2025-11-02 | November | 18:30 | 9010 |  |  | 7430 |  |  | -3740 | -3740 | -2042 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1580 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted violations | 3500 | None | forecasted violations
2025-11-02 | November | 19:30 | 9010 |  |  | 7430 |  |  | -3740 | -3740 | -2042 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1580 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted violations | 3500 | None | forecasted violations
2025-11-02 | November | 20:30 | 9010 |  |  | 7430 |  |  | -3740 | -3740 | -2042 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1580 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted violations | 3500 | None | forecasted violations
2025-11-02 | November | 21:30 |  | 9207 | 962 |  | 6694 | 962 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2513 | 0 | 2513 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted violations | 3500 | None | forecasted violations
2025-11-02 | November | 22:30 |  | 9207 | 962 |  | 6694 | 962 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2513 | 0 | 2513 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted violations | 3500 | None | forecasted violations
2025-11-02 | November | 23:30 |  | 9407 | 962 |  | 7195 | 962 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2212 | 0 | 2212 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | forecasted violations | 3800 | None | forecasted violations
2025-11-03 | November | 12:30 | 9141 |  |  | 7800 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1341 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted security violation | 3500 | None | forecasted security violation
2025-11-03 | November | 13:30 | 9141 |  |  | 7800 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1341 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted security violation | 3500 | None | forecasted security violation
2025-11-03 | November | 14:30 | 9141 |  |  | 7800 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1341 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted security violation | 3500 | None | forecasted security violation
2025-11-03 | November | 15:30 |  | 6437 | 766 |  | 6412 | 815 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 25 | -49 | -24 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted security violation | 3200 | None | forecasted security violation
2025-11-03 | November | 16:30 |  | 6437 | 486 |  | 6412 | 486 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 25 | 0 | 25 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted security violation | 3200 | None | forecasted security violation
2025-11-03 | November | 17:30 |  | 6029 | 486 |  | 6012 | 486 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 17 | 0 | 17 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | forecasted security violation | 3000 | None | forecasted security violation
2025-11-03 | November | 18:30 | 7888 |  |  | 6233 |  |  | 0 | 0 | 945 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1655 | NA | NA | NA | 945 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-03 | November | 19:30 | 7888 |  |  | 6233 |  |  | 0 | 0 | 944 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1655 | NA | NA | NA | 944 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-03 | November | 20:30 | 7888 |  |  | 6233 |  |  | 0 | 0 | 945 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1655 | NA | NA | NA | 945 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-03 | November | 21:30 | 8465 |  |  | 6306 |  |  | 0 | 0 | 465 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2159 | NA | NA | NA | 465 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-03 | November | 22:30 | 8465 |  |  | 6706 |  |  | 0 | 0 | 28 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1759 | NA | NA | NA | 28 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | forecasted security violation | 2900 | None | forecasted security violation
2025-11-03 | November | 23:30 | 7855 |  |  | 7183 |  |  | -1273 | -1273 | -546 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 672 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2300 | None | forecasted security violation | 3400 | None | forecasted security violation
2025-11-04 | November | 12:30 |  | 5971 | 327 |  | 5971 | 327 | 2170 | -50 | 2170 | ID schedules | TTC Validation phase - bilateral reduction | 2220 | NA | 0 | 0 | 0 | -50 | 1 | 154 | None | None | 439 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted security violation | 3500 | None | forecasted security violation
2025-11-04 | November | 13:30 |  | 6079 | 545 |  | 6103 | 598 | 2220 | -50 | 2220 | ID schedules | TTC Validation phase - bilateral reduction | 2270 | NA | -24 | -53 | -77 | -50 | 1 | 155 | None | None | 439 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted security violation | 3500 | None | forecasted security violation
2025-11-04 | November | 14:30 |  | 6526 | 703 |  | 6526 | 703 | 2170 | -50 | 2170 | ID schedules | TTC Validation phase - bilateral reduction | 2220 | NA | 0 | 0 | 0 | -50 | 1 | 154 | None | None | 439 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted security violation | 3500 | None | forecasted security violation
2025-11-04 | November | 15:30 |  | 9600 | 1252 |  | 6031 | 1182 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3569 | 70 | 3639 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 431 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted security violation | 3200 | None | forecasted security violation
2025-11-04 | November | 16:30 |  | 9600 | 1252 |  | 6031 | 1182 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3569 | 70 | 3639 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 202 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted security violation | 3200 | None | forecasted security violation
2025-11-04 | November | 17:30 |  | 9600 | 1252 |  | 5631 | 1182 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3969 | 70 | 4039 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 202 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | forecasted security violation | 3000 | None | forecasted security violation
2025-11-04 | November | 18:30 |  | 8650 | 952 |  | 5607 | 952 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3043 | 0 | 3043 | 0 | 1 | 145 | None | None | 450 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-04 | November | 19:30 |  | 8650 | 952 |  | 5607 | 952 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3043 | 0 | 3043 | 0 | 1 | 145 | None | None | 450 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-04 | November | 20:30 |  | 8650 | 952 |  | 5595 | 952 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3055 | 0 | 3055 | 0 | 1 | 145 | None | None | 439 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-04 | November | 21:30 | 8923 |  |  | 6420 |  |  | 0 | 0 | -756 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2503 | NA | NA | NA | 0 | 1 | 154 | None | None | 450 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-04 | November | 22:30 | 8923 |  |  | 6820 |  |  | 0 | 0 | -1179 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2103 | NA | NA | NA | 0 | 1 | -450 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 450 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 2200 | None | forecasted security violation
2025-11-04 | November | 23:30 | 8313 |  |  | 7292 |  |  | -2790 | -2790 | -1717 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1021 | NA | NA | NA | 0 | 1 | -435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 2300 | None | forecasted security violation
2025-11-05 | November | 12:30 |  | 7115 | 701 |  | 7072 | 701 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 43 | 0 | 43 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 2600 | None | forecasted security violation
2025-11-05 | November | 13:30 |  | 7115 | 701 |  | 7072 | 701 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 43 | 0 | 43 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 2600 | None | forecasted security violation
2025-11-05 | November | 14:30 |  | 7083 | 703 |  | 7051 | 703 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 32 | 0 | 32 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 2600 | None | forecasted security violation
2025-11-05 | November | 15:30 |  | 6568 | 703 |  | 6605 | 703 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -37 | 0 | -37 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted security violation | 3600 | None | forecasted security violation
2025-11-05 | November | 16:30 |  | 6412 | 660 |  | 6473 | 660 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | -61 | 0 | -61 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted security violation | 3300 | None | forecasted security violation
2025-11-05 | November | 17:30 |  | 7812 | 660 |  | 6020 | 660 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1792 | 0 | 1792 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2500 | None | forecasted security violation | 2700 | None | forecasted security violation
2025-11-05 | November | 18:30 | 9031 |  |  | 6720 |  |  | 0 | 0 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2311 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2700 | None | forecasted security violation | 2500 | None | forecasted security violation
2025-11-05 | November | 19:30 | 9031 |  |  | 6720 |  |  | 0 | 0 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2311 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2700 | None | forecasted security violation | 2500 | None | forecasted security violation
2025-11-05 | November | 20:30 | 9031 |  |  | 6720 |  |  | 0 | 0 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2311 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2700 | None | forecasted security violation | 2500 | None | forecasted security violation
2025-11-05 | November | 21:30 | 9290 |  |  | 6751 |  |  | -3126 | -3126 | -457 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2539 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2700 | None | forecasted security violation | 2500 | None | forecasted security violation
2025-11-05 | November | 22:30 | 9290 |  |  | 7351 |  |  | -3126 | -3126 | -1071 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1939 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2900 | None | forecasted security violation | 2900 | None | forecasted security violation
2025-11-05 | November | 23:30 | 8480 |  |  | 7228 |  |  | -2309 | -2309 | -968 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1252 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2700 | None | forecasted security violation | 3100 | None | forecasted security violation
2025-11-06 | November | 12:30 | 8990 |  |  | 7769 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1221 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | forecasted security violation | 3000 | None | forecasted security violation
2025-11-06 | November | 13:30 | 8990 |  |  | 7764 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1226 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | forecasted security violation | 3000 | None | forecasted security violation
2025-11-06 | November | 14:30 | 8990 |  |  | 7869 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1121 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | forecasted security violation | 3000 | None | forecasted security violation
2025-11-06 | November | 15:30 |  | 7358 | 713 |  | 7071 | 713 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 287 | 0 | 287 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | forecasted security violation | 3000 | None | forecasted security violation
2025-11-06 | November | 16:30 |  | 7358 | 713 |  | 6671 | 713 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 687 | 0 | 687 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | forecasted security violation | 2800 | None | forecasted security violation
2025-11-06 | November | 17:30 |  | 7358 | 713 |  | 7532 | 713 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | -174 | 0 | -174 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-06 | November | 18:30 |  | 8820 | 697 |  | 8821 | 697 | 282 | -94 | 282 | ID schedules | ID schedules | 376 | NA | -1 | 0 | -1 | -94 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-06 | November | 19:30 |  | 8867 | 697 |  | 8868 | 697 | 288 | -94 | 288 | ID schedules | ID schedules | 382 | NA | -1 | 0 | -1 | -94 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-06 | November | 20:30 |  | 8514 | 695 |  | 8486 | 695 | 242 | -94 | 242 | Critical Branch | ID schedules | 336 | NA | 28 | 0 | 28 | -94 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-06 | November | 21:30 | 9447 |  |  | 9447 |  |  | -3409 | -3409 | -3409 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-06 | November | 22:30 | 9447 |  |  | 9447 |  |  | -3409 | -3409 | -3409 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-06 | November | 23:30 | 8637 |  |  | 8637 |  |  | -2676 | -2676 | -2676 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 12:30 | 9704 |  |  | 9704 |  |  | 145 | 145 | 3 | Adjustment reached | Adjustment reached | 0 | 0 | NA | NA | NA | 3 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 13:30 | 9704 |  |  | 9704 |  |  | 145 | 145 | 3 | Adjustment reached | Adjustment reached | 0 | 0 | NA | NA | NA | 3 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 14:30 | 9704 |  |  | 9704 |  |  | 145 | 145 | 3 | Adjustment reached | ID schedules | 0 | 0 | NA | NA | NA | 3 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 15:30 |  | 8105 | 903 |  | 8002 | 909 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 103 | -6 | 97 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 16:30 |  | 8371 | 909 |  | 7621 | 901 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 750 | 8 | 758 | 0 | 1 | None | None | None | None | None | None | None | 8422 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | 7413 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 17:30 |  | 8450 | 911 |  | 8450 | 911 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 18:30 |  | 6833 | 782 |  | 7251 | 782 | -3747 | -3747 | -3747 | ID schedules | ID schedules | 0 | NA | -418 | 0 | -418 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 19:30 |  | 7363 | 782 |  | 7760 | 782 | -4326 | -4326 | -4326 | ID schedules | ID schedules | 0 | NA | -397 | 0 | -397 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 20:30 |  | 7284 | 762 |  | 7487 | 767 | -4425 | -4425 | -4425 | ID schedules | ID schedules | 0 | NA | -203 | -5 | -208 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 21:30 | 6836 |  |  | 6836 |  |  | 1266 | -64 | 1266 | ID schedules | ID schedules | 1330 | 0 | NA | NA | NA | -64 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 22:30 | 6987 |  |  | 6987 |  |  | 1266 | -64 | 1266 | ID schedules | ID schedules | 1330 | 0 | NA | NA | NA | -64 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-07 | November | 23:30 | 6647 |  |  | 6647 |  |  | 0 | 0 | 1634 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 1634 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 12:30 |  | 5109 | 697 |  | 4446 | 697 | -173 | -173 | -173 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 663 | 0 | 663 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 15 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-08 | November | 13:30 |  | 5033 | 697 |  | 4365 | 697 | -177 | -177 | -177 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 668 | 0 | 668 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 59 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-08 | November | 14:30 |  | 5397 | 697 |  | 4865 | 697 | -260 | -260 | -260 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 532 | 0 | 532 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-08 | November | 15:30 |  | 6009 | 1013 |  | 5059 | 992 | 1771 | -84 | 1771 | ID schedules | TTC Validation phase - bilateral reduction | 1855 | NA | 950 | 21 | 971 | -84 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-08 | November | 16:30 |  | 5890 | 1013 |  | 6239 | 992 | 1486 | -84 | 1486 | ID schedules | TTC Validation phase - bilateral reduction | 1570 | NA | -349 | 21 | -328 | -84 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 17:30 |  | 6535 | 1013 |  | 7155 | 992 | 1518 | -84 | 1518 | ID schedules | ID schedules | 1602 | NA | -620 | 21 | -599 | -84 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 188 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 18:30 |  | 8869 | 177 |  | 8709 | 177 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 160 | 0 | 160 | 0 | 1 | 155 | None | None | 367 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 19:30 |  | 8863 | 177 |  | 8885 | 177 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -22 | 0 | -22 | 0 | 1 | 155 | None | None | 381 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 20:30 |  | 8829 | 177 |  | 8818 | 177 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 11 | 0 | 11 | 0 | 1 | 155 | None | None | 414 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 21:30 | 9726 |  |  | 9725 |  |  | -926 | -926 | -924 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 155 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 22:30 | 9726 |  |  | 9725 |  |  | -926 | -926 | -924 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 155 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-08 | November | 23:30 | 8916 |  |  | 8915 |  |  | -520 | -520 | -518 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 170 | None | None | 395 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-09 | November | 12:30 |  | 3842 | 591 |  | 3842 | 618 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -27 | -27 | 0 | 1 | 106 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 238 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-09 | November | 13:30 |  | 3697 | 647 |  | 3697 | 650 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -3 | -3 | 0 | 1 | 121 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -65 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-09 | November | 14:30 |  | 4380 | 628 |  | 4380 | 640 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -12 | -12 | 0 | 1 | 113 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 143 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-09 | November | 15:30 |  | 8903 | 756 |  | 7038 | 756 | 2758 | -59 | 2758 | Critical Branch | TTC Validation phase - bilateral reduction | 2817 | NA | 1865 | 0 | 1865 | -59 | 1 | 168 | None | None | 243 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-09 | November | 16:30 |  | 9032 | 854 |  | 8048 | 854 | 1488 | -59 | 1488 | ID schedules | TTC Validation phase - bilateral reduction | 1547 | NA | 984 | 0 | 984 | -59 | 1 | 170 | None | None | 292 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-09 | November | 17:30 |  | 9052 | 854 |  | 8705 | 854 | 1490 | -59 | 1490 | ID schedules | TTC Validation phase - bilateral reduction | 1549 | NA | 347 | 0 | 347 | -59 | 1 | 164 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-09 | November | 18:30 | 9014 |  |  | 9014 |  |  | -2846 | -2846 | -2845 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 168 | None | None | 435 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-09 | November | 19:30 | 9014 |  |  | 9014 |  |  | -2826 | -2826 | -2825 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 435 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-09 | November | 20:30 | 9014 |  |  | 9014 |  |  | -2801 | -2801 | -2801 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 430 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-09 | November | 21:30 | 10786 |  |  | 10619 |  |  | -6134 | -6134 | -5979 | Critical Branch | ID schedules | 0 | 167 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-09 | November | 22:30 | 10786 |  |  | 10738 |  |  | -6134 | -6134 | -6098 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 48 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-09 | November | 23:30 | 10786 |  |  | 10737 |  |  | -6134 | -6134 | -6099 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 49 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-10 | November | 12:30 |  | 4903 | 3905 |  | 4903 | 2559 | 7789 | 0 | 7789 | Critical Branch | TTC Validation phase - bilateral reduction | 7789 | NA | 0 | 1346 | 1346 | 0 | 1 | 153 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 149 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-10 | November | 13:30 |  | 4903 | 3905 |  | 4903 | 2432 | 7789 | 0 | 7789 | Critical Branch | TTC Validation phase - bilateral reduction | 7789 | NA | 0 | 1473 | 1473 | 0 | 1 | 153 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 149 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-10 | November | 14:30 |  | 4903 | 3905 |  | 4903 | 1775 | 7789 | 0 | 7789 | Critical Branch | TTC Validation phase - bilateral reduction | 7789 | NA | 0 | 2130 | 2130 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 149 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 15:30 |  | 6795 | 876 |  | 7234 | 876 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -439 | 0 | -439 | 0 | 1 | 155 | None | None | 223 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 16:30 |  | 6687 | 876 |  | 7059 | 876 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -372 | 0 | -372 | 0 | 1 | 155 | None | None | 333 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 17:30 |  | 6875 | 875 |  | 7256 | 875 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -381 | 0 | -381 | 0 | 1 | 155 | None | None | 333 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 18:30 |  | 9458 | 705 |  | 9258 | 705 | -3334 | -3334 | -3334 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 200 | 0 | 200 | 0 | 1 | 154 | None | None | 439 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 19:30 |  | 9463 | 705 |  | 9464 | 705 | -3337 | -3337 | -3337 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -1 | 0 | -1 | 0 | 1 | 154 | None | None | 416 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 20:30 |  | 9453 | 705 |  | 9064 | 705 | -3334 | -3334 | -3334 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 389 | 0 | 389 | 0 | 1 | 154 | None | None | 394 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 21:30 |  | 7126 | 180 |  | 7351 | 177 | 2528 | 187 | 2528 | Minimum Margin | TTC Validation phase - bilateral reduction | 2341 | NA | -225 | 3 | -222 | 187 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 186 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 22:30 |  | 6379 | 180 |  | 6511 | 177 | 2719 | 187 | 2719 | Minimum Margin | TTC Validation phase - bilateral reduction | 2532 | NA | -132 | 3 | -129 | 187 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 279 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-10 | November | 23:30 |  | 6067 | 193 |  | 6064 | 193 | 2621 | 187 | 2621 | Minimum Margin | TTC Validation phase - bilateral reduction | 2434 | NA | 3 | 0 | 3 | 187 | 1 | 169 | None | None | 393 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 12:30 |  | 6736 | 726 |  | 7269 | 726 | -938 | -938 | -938 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -533 | 0 | -533 | 0 | 1 | 153 | None | None | 298 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 13:30 |  | 6888 | 726 |  | 7417 | 726 | -968 | -968 | -968 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -529 | 0 | -529 | 0 | 1 | 153 | None | None | 450 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 14:30 |  | 6270 | 726 |  | 6456 | 726 | -1057 | -1057 | -1057 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -186 | 0 | -186 | 0 | 1 | 153 | None | None | 450 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 15:30 |  | 8196 | 815 |  | 8082 | 178 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 114 | 637 | 751 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 436 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 16:30 |  | 8196 | 815 |  | 8321 | 178 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | -125 | 637 | 512 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 267 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 17:30 |  | 8396 | 815 |  | 8479 | 177 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | -83 | 638 | 555 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 311 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 18:30 |  | 9416 | 869 |  | 9188 | 869 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 228 | 0 | 228 | 0 | 1 | 155 | None | None | 208 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 19:30 |  | 9416 | 869 |  | 9188 | 870 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 228 | -1 | 227 | 0 | 1 | 155 | None | None | 208 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 20:30 |  | 9416 | 869 |  | 9188 | 870 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 228 | -1 | 227 | 0 | 1 | 155 | None | None | 208 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 21:30 |  | 8318 | 177 |  | 8367 | 177 | -2811 | -2811 | -2811 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -49 | 0 | -49 | 0 | 1 | 155 | None | None | 381 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 22:30 |  | 8347 | 177 |  | 8421 | 177 | -2805 | -2805 | -2805 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -74 | 0 | -74 | 0 | 1 | 155 | None | None | 357 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-11 | November | 23:30 |  | 7476 | 194 |  | 7481 | 194 | -1968 | -1968 | -1968 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -5 | 0 | -5 | 0 | 1 | 170 | None | None | 414 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 12:30 |  | 5404 | 69 |  | 5246 | 69 | 15319 | -15 | 15319 | ID schedules | ID schedules | 15334 | NA | 158 | 0 | 158 | -15 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 13:30 |  | 5951 | 121 |  | 5819 | 121 | 15283 | -15 | 15283 | ID schedules | ID schedules | 15298 | NA | 132 | 0 | 132 | -15 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 14:30 |  | 6038 | 179 |  | 5911 | 179 | 15291 | -15 | 15291 | ID schedules | ID schedules | 15306 | NA | 127 | 0 | 127 | -15 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 15:30 |  | 6762 | 859 |  | 6799 | 863 | 5149 | 14 | 5149 | Minimum Margin | ID schedules | 5135 | NA | -37 | -4 | -41 | 14 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 16:30 |  | 8089 | 856 |  | 8081 | 860 | 4251 | 14 | 4251 | Minimum Margin | ID schedules | 4237 | NA | 8 | -4 | 4 | 14 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3685 | None | Outage - Outage Gd-Ile - Piossasco 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 17:30 |  | 8348 | 856 |  | 8338 | 860 | 3989 | 14 | 3989 | Minimum Margin | ID schedules | 3975 | NA | 10 | -4 | 6 | 14 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3685 | None | Outage - Gd-Ile- PIOSSASCO 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 18:30 |  | 9203 | 825 |  | 9120 | 834 | -3696 | -3696 | -3696 | ID schedules | ID schedules | 0 | NA | 83 | -9 | 74 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 19:30 |  | 9100 | 825 |  | 9024 | 834 | -3665 | -3665 | -3665 | ID schedules | ID schedules | 0 | NA | 76 | -9 | 67 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 20:30 |  | 9072 | 790 |  | 8979 | 797 | -3670 | -3670 | -3670 | Critical Branch | ID schedules | 0 | NA | 93 | -7 | 86 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 21:30 |  | 9085 | 860 |  | 8985 | 863 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 100 | -3 | 97 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 22:30 |  | 9074 | 852 |  | 8984 | 856 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 90 | -4 | 86 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-12 | November | 23:30 |  | 8622 | 190 |  | 8066 | 331 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 556 | -141 | 415 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 12:30 | 5424 |  |  | 5543 |  |  | 15136 | -72 | 15118 | ID schedules | TTC Validation phase - bilateral reduction | 15208 | -119 | NA | NA | NA | -90 | 1 | 155 | None | None | 403 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 13:30 | 5737 |  |  | 5779 |  |  | 15122 | -72 | 15116 | ID schedules | TTC Validation phase - bilateral reduction | 15194 | -42 | NA | NA | NA | -78 | 1 | 155 | None | None | 403 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 14:30 | 6175 |  |  | 6175 |  |  | 15052 | -72 | 15052 | ID schedules | TTC Validation phase - bilateral reduction | 15124 | 0 | NA | NA | NA | -72 | 1 | 155 | None | None | 403 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 15:30 | 8589 |  |  | 8052 |  |  | -2807 | -2807 | -2261 | Critical Branch | ID schedules | 0 | 537 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 330 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 16:30 | 8589 |  |  | 8589 |  |  | -2858 | -2858 | -2856 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 165 | None | None | 332 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 17:30 | 8789 |  |  | 8789 |  |  | -3075 | -3075 | -3075 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | None | 334 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 18:30 |  | 8595 | 897 |  | 8595 | 903 | -4210 | -4210 | -4210 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -6 | -6 | 0 | 1 | 165 | None | None | 207 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 19:30 |  | 8569 | 897 |  | 8557 | 903 | -4203 | -4203 | -4203 | ID schedules | ID schedules | 0 | NA | 12 | -6 | 6 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 254 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 20:30 |  | 8468 | 845 |  | 8376 | 871 | -4172 | -4172 | -4172 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 92 | -26 | 66 | 0 | 1 | 147 | None | None | 417 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 21:30 | 8873 |  |  | 8873 |  |  | -2776 | -2776 | -2775 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | None | 434 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 22:30 | 8873 |  |  | 8873 |  |  | -2757 | -2757 | -2757 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | None | 434 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-13 | November | 23:30 | 8063 |  |  | 8063 |  |  | -1926 | -1926 | -1902 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 418 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 12:30 |  | 8385 | 832 |  | 8404 | 880 | -4818 | -4818 | -4818 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -19 | -48 | -67 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3685 | None | N situation / [AT-AT] PST Nauders 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 13:30 |  | 8387 | 880 |  | 8406 | 880 | -4819 | -4819 | -4819 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -19 | 0 | -19 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3685 | None | N situation / [AT-AT] PST Nauders 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 14:30 |  | 8381 | 880 |  | 8396 | 880 | -4818 | -4818 | -4818 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -15 | 0 | -15 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3685 | None | N situation / [AT-AT] PST Nauders 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 15:30 |  | 7950 | 1009 |  | 7957 | 984 | -1829 | -1829 | -1829 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -7 | 25 | 18 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3685 | None | N situation / [IT-IT] Rondissone-Trino [DIR][IT] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-14 | November | 16:30 |  | 8873 | 1009 |  | 8873 | 994 | -2749 | -2749 | -2749 | Critical Branch | ID schedules | 0 | NA | 0 | 15 | 15 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-14 | November | 17:30 |  | 9007 | 1009 |  | 9007 | 983 | -2880 | -2880 | -2880 | Critical Branch | ID schedules | 0 | NA | 0 | 26 | 26 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-14 | November | 18:30 |  | 8977 | 955 |  | 8977 | 958 | -3927 | -3927 | -3927 | ID schedules | ID schedules | 0 | NA | 0 | -3 | -3 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 19:30 |  | 8900 | 955 |  | 8901 | 958 | -3912 | -3912 | -3912 | ID schedules | ID schedules | 0 | NA | -1 | -3 | -4 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 20:30 |  | 8619 | 899 |  | 8619 | 900 | -3862 | -3862 | -3862 | ID schedules | ID schedules | 0 | NA | 0 | -1 | -1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 21:30 |  | 8508 | 423 |  | 8508 | 507 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -84 | -84 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 22:30 |  | 8508 | 623 |  | 8508 | 670 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -47 | -47 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-14 | November | 23:30 |  | 7825 | 908 |  | 7825 | 908 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 12:30 | 7923 |  |  | 7923 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | None | 382 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 13:30 | 7923 |  |  | 7923 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | None | 382 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 14:30 | 7923 |  |  | 7923 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | None | 382 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 15:30 |  | 8546 | 988 |  | 8435 | 966 | -541 | -541 | -541 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 111 | 22 | 133 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 417 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 16:30 |  | 8736 | 988 |  | 8736 | 966 | -589 | -589 | -589 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 22 | 22 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 197 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 17:30 |  | 8736 | 988 |  | 8736 | 966 | -589 | -589 | -589 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 22 | 22 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 197 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 18:30 |  | 8999 | 806 |  | 8998 | 806 | -1222 | -1222 | -1222 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 155 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 19:30 |  | 8999 | 806 |  | 8998 | 806 | -1222 | -1222 | -1222 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 0 | 1 | 0 | 1 | 150 | None | None | 412 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 20:30 |  | 8747 | 806 |  | 8746 | 806 | -1112 | -1112 | -1112 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 150 | None | None | 400 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 21:30 |  | 8823 | 230 |  | 8675 | 235 | 186 | 0 | 186 | ID schedules | ID schedules | 186 | NA | 148 | -5 | 143 | 0 | 1 | 155 | None | None | 404 | None | None | None | 9295 | "Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE" | None | 8426 | "Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE" | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 22:30 |  | 8771 | 695 |  | 8770 | 697 | 213 | 0 | 213 | ID schedules | TTC Validation phase - bilateral reduction | 213 | NA | 1 | -2 | -1 | 0 | 1 | 154 | None | None | 401 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-15 | November | 23:30 |  | 8181 | 267 |  | 8079 | 319 | 960 | 0 | 960 | ID schedules | ID schedules | 960 | NA | 102 | -52 | 50 | 0 | 1 | 169 | None | None | 389 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 12:30 | 6193 |  |  | 6193 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 359 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 13:30 | 6006 |  |  | 6028 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -22 | NA | NA | NA | 0 | 1 | 69 | None | None | 175 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 14:30 | 5728 |  |  | 5805 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -77 | NA | NA | NA | 0 | 1 | 69 | None | None | 175 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 15:30 | 6158 |  |  | 6160 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -2 | NA | NA | NA | 0 | 1 | 70 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 16:30 | 6085 |  |  | 6085 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 197 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 17:30 | 6772 |  |  | 6774 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -2 | NA | NA | NA | 0 | 1 | 69 | None | None | 194 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 18:30 | 9177 |  |  | 8726 |  |  | -2573 | -2573 | -2248 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 451 | NA | NA | NA | 0 | 1 | 69 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 19:30 | 9177 |  |  | 9177 |  |  | -2572 | -2572 | -2572 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 69 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 20:30 | 9177 |  |  | 9177 |  |  | -2572 | -2572 | -2572 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 210 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 21:30 | 9920 |  |  | 9911 |  |  | -416 | -416 | -407 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 9 | NA | NA | NA | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 210 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 22:30 | 9920 |  |  | 9911 |  |  | -416 | -416 | -407 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 9 | NA | NA | NA | 0 | 1 | 69 | None | Reduction because NTC over thermal limit on border | 210 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-16 | November | 23:30 | 9920 |  |  | 9911 |  |  | -416 | -416 | -407 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 9 | NA | NA | NA | 0 | 1 | 69 | None | Reduction because NTC over thermal limit on border | 210 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 12:30 | 4514 |  |  | 4548 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -34 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 13:30 | 4628 |  |  | 4628 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 14:30 | 5409 |  |  | 5439 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -30 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 15:30 | 7068 |  |  | 7072 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -4 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 16:30 | 8366 |  |  | 8366 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 17:30 | 8729 |  |  | 8729 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 18:30 | 8911 |  |  | 8911 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 19:30 | 9206 |  |  | 9206 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 20:30 | 8613 |  |  | 8613 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 21:30 | 8068 |  |  | 8068 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 22:30 | 7509 |  |  | 7509 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-17 | November | 23:30 | 7101 |  |  | 7101 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-18 | November | 12:30 | 6961 |  |  | 6961 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 13:30 | 7050 |  |  | 7050 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 14:30 | 7844 |  |  | 7844 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 15:30 | 7816 |  |  | 7820 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -4 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 16:30 | 6731 |  |  | 6744 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -13 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 17:30 | 6550 |  |  | 6549 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 18:30 |  | 8980 | 698 |  | 8233 | 698 | -3235 | -3235 | -3235 | ID schedules | ID schedules | 0 | NA | 747 | 0 | 747 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 19:30 |  | 9049 | 698 |  | 9043 | 698 | -3331 | -3331 | -3331 | ID schedules | ID schedules | 0 | NA | 6 | 0 | 6 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 20:30 |  | 8534 | 653 |  | 8265 | 653 | -3223 | -3223 | -3223 | Critical Branch | ID schedules | 0 | NA | 269 | 0 | 269 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 21:30 | 9483 |  |  | 9318 |  |  | -3928 | -3928 | -3750 | Critical Branch | ID schedules | 0 | 165 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 22:30 | 9483 |  |  | 9483 |  |  | -3934 | -3934 | -3934 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-18 | November | 23:30 | 8688 |  |  | 8688 |  |  | -3138 | -3138 | -3138 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-19 | November | 12:30 | 8999 |  |  | 8998 |  |  | -4339 | -4339 | -4336 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 70 | None | None | 181 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 13:30 | 8999 |  |  | 8998 |  |  | -4339 | -4339 | -4336 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 70 | None | None | 181 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 14:30 | 8999 |  |  | 8998 |  |  | -4339 | -4339 | -4336 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 70 | None | None | 181 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 15:30 |  | 9533 | 1034 |  | 9533 | 1010 | -4466 | -4466 | -4466 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 24 | 24 | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 102 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 16:30 |  | 9533 | 1034 |  | 9533 | 1010 | -4466 | -4466 | -4466 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 24 | 24 | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 102 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 17:30 |  | 9490 | 1034 |  | 9454 | 1010 | -4453 | -4453 | -4453 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 36 | 24 | 60 | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 162 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 18:30 |  | 9752 | 81 |  | 9752 | 81 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 70 | None | None | 206 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 19:30 |  | 9752 | 88 |  | 9752 | 81 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 7 | 7 | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 206 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 20:30 |  | 9752 | 73 |  | 9752 | 73 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 62 | None | None | 206 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 21:30 | 9500 |  |  | 9500 |  |  | -5364 | -5364 | -5363 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 192 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 22:30 | 9500 |  |  | 9500 |  |  | -5364 | -5364 | -5363 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 192 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-19 | November | 23:30 | 8705 |  |  | 8704 |  |  | -4570 | -4570 | -4568 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | 69 | None | None | 190 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-20 | November | 12:30 | 4077 |  |  | 4077 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 81 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-20 | November | 13:30 | 4145 |  |  | 4145 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | 81 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-20 | November | 14:30 | 4753 |  |  | 4875 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -122 | NA | NA | NA | 0 | 1 | 70 | None | None | 14 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-20 | November | 15:30 | 5043 |  |  | 5043 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | -66 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-20 | November | 16:30 | 4322 |  |  | 4322 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -69 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-20 | November | 17:30 | 3832 |  |  | 3832 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 12 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 90 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-20 | November | 18:30 |  | 4466 | 878 |  | 4729 | 877 | 3966 | -71 | 3966 | ID schedules | ID schedules | 4037 | NA | -263 | 1 | -262 | -71 | 1 | -103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 119 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-20 | November | 19:30 |  | 5793 | 875 |  | 6172 | 867 | 4084 | -71 | 4084 | ID schedules | ID schedules | 4155 | NA | -379 | 8 | -371 | -71 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 88 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-20 | November | 20:30 |  | 7058 | 869 |  | 7441 | 836 | 2759 | -71 | 2759 | ID schedules | ID schedules | 2830 | NA | -383 | 33 | -350 | -71 | 1 | 42 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 65 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-20 | November | 21:30 | 9646 |  |  | 9247 |  |  | -4802 | -4802 | -4403 | Critical Branch | ID schedules | 0 | 399 | NA | NA | NA | 0 | 1 | 70 | None | None | 194 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-20 | November | 22:30 | 9646 |  |  | 9431 |  |  | -4802 | -4802 | -4591 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 215 | NA | NA | NA | 0 | 1 | 70 | None | None | 195 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-20 | November | 23:30 | 8851 |  |  | 8625 |  |  | -4008 | -4008 | -3787 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 226 | NA | NA | NA | 0 | 1 | 69 | None | None | 194 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-21 | November | 12:30 | 8388 |  |  | 8340 |  |  | -3210 | -3210 | -3160 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 48 | NA | NA | NA | 0 | 1 | 70 | None | None | 167 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-21 | November | 13:30 | 8388 |  |  | 6840 |  |  | -3210 | -3210 | -1655 | Critical Branch | ID schedules | 0 | 1548 | NA | NA | NA | 0 | 1 | 70 | None | None | 135 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-21 | November | 14:30 | 8388 |  |  | 5960 |  |  | -3210 | -3210 | -769 | Critical Branch | ID schedules | 0 | 2428 | NA | NA | NA | 0 | 1 | 57 | None | None | 123 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-21 | November | 15:30 |  | 3265 | 483 |  | 3265 | 453 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 30 | 30 | 0 | 1 | 7 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 91 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-21 | November | 16:30 |  | 3267 | 563 |  | 3267 | 562 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | 7 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -6 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-21 | November | 17:30 |  | 3265 | 563 |  | 3265 | 562 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | 7 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -6 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-21 | November | 18:30 |  | 2033 | 825 |  | 1943 | 562 | 3057 | 0 | 3057 | Critical Branch | ID schedules | 3057 | NA | 90 | 263 | 353 | 0 | 1 | 5 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 96 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-21 | November | 19:30 |  | 2712 | 1320 |  | 2712 | 1209 | 2358 | 0 | 2358 | ID schedules | ID schedules | 2358 | NA | 0 | 111 | 111 | 0 | 1 | 67 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 194 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-21 | November | 20:30 |  | 4487 | 1375 |  | 4362 | 1196 | 698 | 0 | 698 | ID schedules | TTC Validation phase - bilateral reduction | 698 | NA | 125 | 179 | 304 | 0 | 1 | 118 | None | None | 63 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-21 | November | 21:30 | 5174 |  |  | 5171 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 3 | NA | NA | NA | 0 | 1 | 153 | None | None | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-21 | November | 22:30 | 6031 |  |  | 6031 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | None | 390 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-21 | November | 23:30 | 5813 |  |  | 5813 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 373 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 12:30 |  | 7438 | 150 |  | 7463 | 150 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | -25 | 0 | -25 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 13:30 |  | 7438 | 150 |  | 7327 | 150 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 111 | 0 | 111 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 14:30 |  | 7355 | 177 |  | 6817 | 177 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 538 | 0 | 538 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 15:30 | 5143 |  |  | 5181 |  |  | 0 | 0 | 3347 | ID schedules | ID schedules | 0 | -38 | NA | NA | NA | 3347 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 16:30 | 5030 |  |  | 5061 |  |  | 0 | 0 | 3431 | ID schedules | ID schedules | 0 | -31 | NA | NA | NA | 3431 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 17:30 | 6220 |  |  | 6246 |  |  | 0 | 0 | 3185 | ID schedules | ID schedules | 0 | -26 | NA | NA | NA | 3185 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 18:30 | 8645 |  |  | 7748 |  |  | -1656 | -1656 | -758 | Critical Branch | ID schedules | 0 | 897 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 19:30 | 8645 |  |  | 8645 |  |  | -1656 | -1656 | -1654 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 20:30 | 8645 |  |  | 8645 |  |  | -1656 | -1656 | -1654 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 21:30 | 10357 |  |  | 10145 |  |  | -4909 | -4909 | -4695 | Critical Branch | Smoothing ramp | 0 | 212 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 22:30 | 10357 |  |  | 10357 |  |  | -4909 | -4909 | -4906 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-22 | November | 23:30 | 9547 |  |  | 9547 |  |  | -4101 | -4101 | -4100 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 12:30 |  | 5031 | 154 |  | 5031 | 154 | 10375 | -92 | 10375 | Critical Branch | TTC Validation phase - bilateral reduction | 10467 | NA | 0 | 0 | 0 | -92 | 1 | 130 | None | None | 114 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 13:30 |  | 5343 | 194 |  | 5322 | 194 | 10418 | -92 | 10418 | ID schedules | TTC Validation phase - bilateral reduction | 10510 | NA | 21 | 0 | 21 | -92 | 1 | 170 | None | None | -169 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 14:30 |  | 5026 | 154 |  | 5009 | 154 | 10425 | -92 | 10425 | Critical Branch | TTC Validation phase - bilateral reduction | 10517 | NA | 17 | 0 | 17 | -92 | 1 | 130 | None | None | 397 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 15:30 |  | 9521 | 983 |  | 7499 | 968 | 7074 | -98 | 7074 | Critical Branch | TTC Validation phase - bilateral reduction | 7172 | NA | 2022 | 15 | 2037 | -98 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 16:30 |  | 9605 | 983 |  | 8263 | 968 | 7067 | -98 | 7067 | Critical Branch | TTC Validation phase - bilateral reduction | 7165 | NA | 1342 | 15 | 1357 | -98 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 259 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 17:30 |  | 9605 | 983 |  | 9125 | 968 | 7067 | -98 | 7067 | Critical Branch | TTC Validation phase - bilateral reduction | 7165 | NA | 480 | 15 | 495 | -98 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 308 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 18:30 |  | 10184 | 205 |  | 10184 | 194 | -4844 | -4844 | -4844 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 11 | 11 | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 233 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 19:30 |  | 10184 | 205 |  | 10184 | 194 | -4844 | -4844 | -4844 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 11 | 11 | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 233 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 20:30 |  | 9993 | 205 |  | 9993 | 194 | -4779 | -4779 | -4779 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 11 | 11 | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 424 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 21:30 | 10220 |  |  | 10198 |  |  | 9884 | -76 | 9888 | Critical Branch | TTC Validation phase - bilateral reduction | 9960 | 22 | NA | NA | NA | -72 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 22:30 | 10220 |  |  | 10198 |  |  | 9884 | -76 | 9888 | Critical Branch | TTC Validation phase - bilateral reduction | 9960 | 22 | NA | NA | NA | -72 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-23 | November | 23:30 | 10220 |  |  | 10198 |  |  | 9884 | -76 | 9888 | Critical Branch | TTC Validation phase - bilateral reduction | 9960 | 22 | NA | NA | NA | -72 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-24 | November | 12:30 |  | 7914 | 820 |  | 7450 | 698 | -5749 | -5749 | -5749 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 464 | 122 | 586 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-24 | November | 13:30 |  | 7914 | 820 |  | 7450 | 698 | -5749 | -5749 | -5749 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 464 | 122 | 586 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-24 | November | 14:30 |  | 7914 | 820 |  | 7450 | 698 | -5749 | -5749 | -5749 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 464 | 122 | 586 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-24 | November | 15:30 |  | 6367 | 875 |  | 6367 | 875 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 16:30 |  | 6365 | 875 |  | 6365 | 875 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 17:30 |  | 6365 | 875 |  | 6365 | 875 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 18:30 |  | 6592 | 875 |  | 6584 | 875 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 8 | 0 | 8 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 19:30 |  | 6592 | 875 |  | 6584 | 875 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 8 | 0 | 8 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 20:30 |  | 6592 | 893 |  | 6584 | 885 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 8 | 8 | 16 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 21:30 | 7936 |  |  | 7738 |  |  | -4668 | -4668 | -4454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 198 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-24 | November | 22:30 | 7936 |  |  | 7738 |  |  | -4668 | -4668 | -4454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 198 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - Unplanned outage LA PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-24 | November | 23:30 | 7126 |  |  | 7126 |  |  | -3867 | -3867 | -3865 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Valpelline [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-25 | November | 12:30 |  | 4110 | 2434 |  | 3199 | 2412 | 2328 | 0 | 2328 | ID schedules | TTC Validation phase - bilateral reduction | 2328 | NA | 911 | 22 | 933 | 0 | 1 | 126 | None | None | 219 | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 13:30 |  | 4110 | 2215 |  | 3199 | 1778 | 2351 | 0 | 2351 | Critical Branch | TTC Validation phase - bilateral reduction | 2351 | NA | 911 | 437 | 1348 | 0 | 1 | 113 | None | None | 219 | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 14:30 |  | 4110 | 2215 |  | 3199 | 941 | 2351 | 0 | 2351 | Critical Branch | TTC Validation phase - bilateral reduction | 2351 | NA | 911 | 1274 | 2185 | 0 | 1 | 113 | None | None | 219 | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 15:30 |  | 5804 | 2779 |  | 4018 | 226 | 2253 | 0 | 2253 | Critical Branch | TTC Validation phase - bilateral reduction | 2253 | NA | 1786 | 2553 | 4339 | 0 | 1 | 114 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 0 | None | Forecasted security violation
2025-11-25 | November | 16:30 |  | 5804 | 2779 |  | 4018 | 323 | 2253 | 0 | 2253 | Critical Branch | TTC Validation phase - bilateral reduction | 2253 | NA | 1786 | 2456 | 4242 | 0 | 1 | 114 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 0 | None | Forecasted security violation
2025-11-25 | November | 17:30 |  | 5804 | 2779 |  | 4018 | 323 | 2253 | 0 | 2253 | Critical Branch | TTC Validation phase - bilateral reduction | 2253 | NA | 1786 | 2456 | 4242 | 0 | 1 | 114 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | 0 | None | Forecasted security violation
2025-11-25 | November | 18:30 |  | 5261 | 2366 |  | 3199 | 383 | 5818 | 0 | 5818 | Critical Branch | TTC Validation phase - bilateral reduction | 5818 | NA | 2062 | 1983 | 4045 | 0 | 1 | 122 | None | None | 158 | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 19:30 |  | 5261 | 2366 |  | 3199 | 871 | 5818 | 0 | 5818 | Critical Branch | TTC Validation phase - bilateral reduction | 5818 | NA | 2062 | 1495 | 3557 | 0 | 1 | 122 | None | None | 158 | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 20:30 |  | 5261 | 2366 |  | 3199 | 1344 | 5818 | 0 | 5818 | Critical Branch | TTC Validation phase - bilateral reduction | 5818 | NA | 2062 | 1022 | 3084 | 0 | 1 | 122 | None | None | 158 | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 21:30 |  | 5799 | 2377 |  | 4369 | 1395 | 1935 | 0 | 1935 | Critical Branch | TTC Validation phase - bilateral reduction | 1935 | NA | 1430 | 982 | 2412 | 0 | 1 | 150 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 22:30 |  | 5799 | 2374 |  | 4369 | 474 | 1936 | 0 | 1936 | Critical Branch | TTC Validation phase - bilateral reduction | 1936 | NA | 1430 | 1900 | 3330 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-25 | November | 23:30 |  | 5525 | 2479 |  | 4245 | 596 | 2114 | 0 | 2114 | Critical Branch | TTC Validation phase - bilateral reduction | 2114 | NA | 1280 | 1883 | 3163 | 0 | 1 | 150 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 12:30 |  | 2733 | 2379 |  | 2733 | 2258 | 7179 | 0 | 7179 | ID schedules | ID schedules | 7179 | NA | 0 | 121 | 121 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 13:30 |  | 2733 | 2267 |  | 2733 | 2115 | 7186 | 0 | 7186 | ID schedules | ID schedules | 7186 | NA | 0 | 152 | 152 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 14:30 |  | 2733 | 1969 |  | 2733 | 1373 | 7177 | 0 | 7177 | ID schedules | ID schedules | 7177 | NA | 0 | 596 | 596 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 15:30 |  | 3607 | 281 |  | 3754 | 279 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -147 | 2 | -145 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 16:30 |  | 3642 | 302 |  | 3563 | 294 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 79 | 8 | 87 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 17:30 |  | 3642 | 309 |  | 3663 | 306 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -21 | 3 | -18 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 18:30 | 8048 |  |  | 7733 |  |  | -5741 | -5741 | -5399 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 315 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 19:30 | 8048 |  |  | 7737 |  |  | -5722 | -5722 | -5385 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 311 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | -10000 | None | ATC blocked
2025-11-26 | November | 20:30 | 8048 |  |  | 7739 |  |  | -5722 | -5722 | -5388 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 309 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-26 | November | 21:30 | 8277 |  |  | 7863 |  |  | -3883 | -3883 | -3441 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 414 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-26 | November | 22:30 | 8277 |  |  | 7863 |  |  | -3883 | -3883 | -3441 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 414 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-26 | November | 23:30 | 7467 |  |  | 7245 |  |  | -3088 | -3088 | -2852 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 222 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - PRAZ VILLARODIN | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 12:30 | 7511 |  |  | 7451 |  |  | 0 | 0 | -3522 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 60 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 13:30 | 7511 |  |  | 7450 |  |  | 0 | 0 | -3534 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 61 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 14:30 | 7511 |  |  | 7450 |  |  | 0 | 0 | -3539 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 61 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 15:30 |  | 7497 | 728 |  | 7172 | 728 | -4471 | -4471 | -4471 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 325 | 0 | 325 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 16:30 |  | 7497 | 728 |  | 7180 | 728 | -4471 | -4471 | -4471 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 317 | 0 | 317 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 17:30 |  | 7499 | 728 |  | 7183 | 728 | -4468 | -4468 | -4468 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 316 | 0 | 316 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 18:30 |  | 7535 | 110 |  | 7071 | 110 | -4633 | -4633 | -4633 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 464 | 0 | 464 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 19:30 |  | 7535 | 471 |  | 7071 | 518 | -4633 | -4633 | -4633 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 464 | -47 | 417 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 20:30 |  | 7535 | 818 |  | 7071 | 818 | -4633 | -4633 | -4633 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 464 | 0 | 464 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 21:30 | 7874 |  |  | 7660 |  |  | -4518 | -4518 | -4290 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 214 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 22:30 | 7874 |  |  | 7658 |  |  | -4522 | -4522 | -4292 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 216 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-27 | November | 23:30 | 7064 |  |  | 7048 |  |  | -3717 | -3717 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2985 | None | Outage - OUTAGE TD LA PRAZ | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-28 | November | 12:30 |  | 6619 | 715 |  | 6390 | 715 | 3162 | 0 | 3162 | Critical Branch | TTC Validation phase - bilateral reduction | 3162 | NA | 229 | 0 | 229 | 0 | 1 | 104 | None | None | 244 | None | None | None | None | None | None | None | None | 2985 | None | Outage - Outage TD LA PRAZ | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-28 | November | 13:30 |  | 6819 | 715 |  | 6486 | 715 | 3144 | 0 | 3144 | Critical Branch | TTC Validation phase - bilateral reduction | 3144 | NA | 333 | 0 | 333 | 0 | 1 | 104 | None | None | 244 | None | None | None | None | None | None | None | None | 2985 | None | Outage - Outage TD LA PRAZ | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-28 | November | 14:30 |  | 6817 | 715 |  | 6481 | 715 | 3143 | 0 | 3143 | Critical Branch | TTC Validation phase - bilateral reduction | 3143 | NA | 336 | 0 | 336 | 0 | 1 | 105 | None | None | 232 | None | None | None | None | None | None | None | None | 2985 | None | Outage - Outage TD LA PRAZ | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-28 | November | 15:30 |  | 7036 | 879 |  | 6447 | 877 | -4297 | -4297 | -4297 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 589 | 2 | 591 | 0 | 1 | 111 | None | Reduction because NTC over thermal limit on border | 117 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - Outage TD LA PRAZ | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-28 | November | 16:30 |  | 7168 | 879 |  | 6619 | 871 | -4396 | -4396 | -4396 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 549 | 8 | 557 | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 102 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - Outage TD LA PRAZ | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-28 | November | 17:30 |  | 7980 | 879 |  | 7320 | 878 | -5319 | -5319 | -5319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 660 | 1 | 661 | 0 | 1 | 112 | None | Reduction because NTC over thermal limit on border | 120 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 2985 | None | Outage - Outage TD LA PRAZ | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-28 | November | 18:30 | 9830 |  |  | 9534 |  |  | -1560 | -1560 | -1345 | Critical Branch | ID schedules | 0 | 296 | NA | NA | NA | 0 | 1 | 110 | None | Reduction because NTC over thermal limit on border | 260 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-28 | November | 19:30 | 9830 |  |  | 9830 |  |  | -1755 | -1755 | -1755 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 115 | None | None | 194 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-28 | November | 20:30 | 9830 |  |  | 9830 |  |  | -1747 | -1747 | -1745 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 105 | None | None | 232 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-28 | November | 21:30 | 10798 |  |  | 10786 |  |  | -3619 | -3619 | -3610 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-28 | November | 22:30 | 10798 |  |  | 10786 |  |  | -3619 | -3619 | -3610 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | 105 | None | Reduction because NTC over thermal limit on border | 300 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-28 | November | 23:30 | 9988 |  |  | 9976 |  |  | -2799 | -2799 | -2790 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-29 | November | 12:30 |  | 7477 | 696 |  | 6427 | 696 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1050 | 0 | 1050 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 13:30 |  | 7477 | 696 |  | 6411 | 696 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1066 | 0 | 1066 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 14:30 |  | 6195 | 698 |  | 6193 | 698 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 2 | 0 | 2 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 15:30 |  | 9221 | 724 |  | 7927 | 724 | -4423 | -4423 | -4423 | Critical Branch | ID schedules | 0 | NA | 1294 | 0 | 1294 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 16:30 |  | 9221 | 724 |  | 9221 | 724 | -4423 | -4423 | -4423 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 17:30 |  | 9221 | 724 |  | 9221 | 724 | -4423 | -4423 | -4423 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 18:30 | 9077 |  |  | 9077 |  |  | -1997 | -1997 | -1995 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 19:30 | 9077 |  |  | 9077 |  |  | -1997 | -1997 | -1995 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 20:30 | 9077 |  |  | 9077 |  |  | -1997 | -1997 | -1995 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 21:30 | 10140 |  |  | 10140 |  |  | -3702 | -3702 | -3700 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 22:30 | 10140 |  |  | 10140 |  |  | -3702 | -3702 | -3700 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-29 | November | 23:30 | 9330 |  |  | 9330 |  |  | -2880 | -2880 | -2878 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-11-30 | November | 12:30 | 6198 |  |  | 6198 |  |  | -2574 | -2574 | -2574 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 280 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 13:30 | 6178 |  |  | 6178 |  |  | -2574 | -2574 | -2574 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 280 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 14:30 | 6698 |  |  | 6698 |  |  | -2574 | -2574 | -2574 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 280 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 15:30 | 7444 |  |  | 7444 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 285 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 16:30 | 7154 |  |  | 7154 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | -110 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 17:30 | 7868 |  |  | 7871 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -3 | NA | NA | NA | 0 | 1 | 125 | None | None | -66 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 18:30 | 9794 |  |  | 9591 |  |  | -5043 | -5043 | -4824 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 203 | NA | NA | NA | 0 | 1 | 130 | None | None | 246 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 19:30 | 9794 |  |  | 9794 |  |  | -5043 | -5043 | -5041 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 273 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 20:30 | 9794 |  |  | 9794 |  |  | -5032 | -5032 | -5031 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 120 | None | None | 282 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 21:30 |  | 8907 | 230 |  | 8819 | 320 | -2902 | -2902 | -2902 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 88 | -90 | -2 | 0 | 1 | 120 | None | None | 192 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 22:30 |  | 8896 | 690 |  | 8795 | 714 | -2903 | -2903 | -2903 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 101 | -24 | 77 | 0 | 1 | 120 | None | None | 205 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-11-30 | November | 23:30 |  | 8715 | 132 |  | 8693 | 139 | -2886 | -2886 | -2886 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 22 | -7 | 15 | 0 | 1 | 20 | None | Reduction because NTC over thermal limit on border | 285 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-01 | October | 12:30 | 8080 |  |  | 8000 |  |  | 14 | 14 | 72 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 80 | NA | NA | NA | 72 | 1 | -390 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 390 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 3600 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-01 | October | 13:30 | 8080 |  |  | 7998 |  |  | 14 | 14 | 74 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 82 | NA | NA | NA | 74 | 1 | -390 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 390 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 3600 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-01 | October | 14:30 | 8078 |  |  | 7999 |  |  | 12 | 12 | 71 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 79 | NA | NA | NA | 71 | 1 | -400 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 400 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 3600 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-01 | October | 15:30 |  | 7024 | 688 |  | 7048 | 688 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -24 | 0 | -24 | 0 | 1 | -370 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 370 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 16:30 |  | 6929 | 682 |  | 6929 | 688 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -6 | -6 | 0 | 1 | 135 | None | None | 366 | None | None | None | None | None | None | None | None | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 17:30 |  | 6929 | 688 |  | 6606 | 688 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 323 | 0 | 323 | 0 | 1 | -133 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3600 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 18:30 |  | 6030 | 728 |  | 5055 | 727 | -3812 | -3812 | -3812 | ID schedules | ID schedules | 0 | NA | 975 | 1 | 976 | 0 | 1 | 115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 87 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4324 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3600 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 19:30 |  | 6052 | 728 |  | 5151 | 727 | -3829 | -3829 | -3829 | ID schedules | ID schedules | 0 | NA | 901 | 1 | 902 | 0 | 1 | 115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 81 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4366 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3600 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 20:30 |  | 5825 | 728 |  | 5108 | 727 | -3652 | -3652 | -3652 | ID schedules | ID schedules | 0 | NA | 717 | 1 | 718 | 0 | 1 | 46 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 83 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4860 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | 3600 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 21:30 |  | 5985 | 2382 |  | 5079 | 747 | 1795 | 0 | 1795 | Critical Branch | ID schedules | 1795 | NA | 906 | 1635 | 2541 | 0 | 1 | -65 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 390 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3600 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 22:30 |  | 5900 | 2382 |  | 5067 | 382 | 1847 | 0 | 1847 | Critical Branch | TTC Validation phase - bilateral reduction | 1847 | NA | 833 | 2000 | 2833 | 0 | 1 | 118 | None | Reduction because NTC over thermal limit on border | 390 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3600 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-01 | October | 23:30 |  | 5706 | 2482 |  | 4946 | 418 | 1799 | 0 | 1799 | Critical Branch | TTC Validation phase - bilateral reduction | 1799 | NA | 760 | 2064 | 2824 | 0 | 1 | 136 | None | Reduction because NTC over thermal limit on border | 375 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3600 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-02 | October | 12:30 |  | 4904 | 624 |  | 4904 | 660 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -36 | -36 | 0 | 1 | 115 | None | None | -45 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 13:30 |  | 4904 | 437 |  | 4904 | 487 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -50 | -50 | 0 | 1 | 124 | None | None | -104 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 14:30 |  | 4952 | 840 |  | 4952 | 860 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -20 | -20 | 0 | 1 | 135 | None | None | -129 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 15:30 |  | 5419 | 860 |  | 5419 | 860 | 839 | -17 | 839 | ID schedules | TTC Validation phase - bilateral reduction | 856 | NA | 0 | 0 | 0 | -17 | 1 | 135 | None | None | -5 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 16:30 |  | 6119 | 877 |  | 6119 | 877 | 615 | -17 | 615 | ID schedules | TTC Validation phase - bilateral reduction | 632 | NA | 0 | 0 | 0 | -17 | 1 | 155 | None | None | 129 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 17:30 |  | 5775 | 877 |  | 5709 | 877 | 569 | -17 | 569 | ID schedules | TTC Validation phase - bilateral reduction | 586 | NA | 66 | 0 | 66 | -17 | 1 | 155 | None | None | 362 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 18:30 |  | 5649 | 877 |  | 5231 | 877 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 418 | 0 | 418 | 0 | 1 | 155 | None | None | 349 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5059 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 19:30 |  | 5794 | 877 |  | 5128 | 877 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 666 | 0 | 666 | 0 | 1 | 155 | None | None | 151 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4762 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 20:30 |  | 5257 | 877 |  | 5195 | 877 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 62 | 0 | 62 | 0 | 1 | 155 | None | None | 349 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 21:30 |  | 7661 | 167 |  | 7292 | 166 | -2908 | -2908 | -2908 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 369 | 1 | 370 | 0 | 1 | 146 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 22:30 |  | 7661 | 175 |  | 7661 | 175 | -2908 | -2908 | -2908 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-02 | October | 23:30 |  | 7066 | 212 |  | 7066 | 191 | -2307 | -2307 | -2307 | Critical Branch | Critical Branch | 0 | NA | 0 | 21 | 21 | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-03 | October | 12:30 |  | 5368 | 2334 |  | 5368 | 2334 | 461 | 0 | 461 | Critical Branch | TTC Validation phase - bilateral reduction | 461 | NA | 0 | 0 | 0 | 0 | 1 | -442 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 442 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | N-2 Albertville-Grande Ile / [FR-FR] BOIS TOLLOT-GENISSIAT [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 13:30 |  | 5368 | 2334 |  | 5368 | 2334 | 461 | 0 | 461 | Critical Branch | TTC Validation phase - bilateral reduction | 461 | NA | 0 | 0 | 0 | 0 | 1 | -442 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 442 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | N-2 Albertville-Grande Ile / [FR-FR] BOIS TOLLOT-GENISSIAT [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 14:30 |  | 5364 | 2334 |  | 5364 | 2334 | 462 | 0 | 462 | Critical Branch | TTC Validation phase - bilateral reduction | 462 | NA | 0 | 0 | 0 | 0 | 1 | -442 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 442 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | N-2 Albertville-Grande Ile / [FR-FR] BOIS TOLLOT-GENISSIAT [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 15:30 |  | 7421 | 815 |  | 6398 | 175 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1023 | 640 | 1663 | 0 | 1 | 130 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 434 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 16:30 |  | 7421 | 815 |  | 6996 | 175 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 425 | 640 | 1065 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 17:30 |  | 7421 | 815 |  | 6692 | 175 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 729 | 640 | 1369 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 434 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 18:30 |  | 7200 | 647 |  | 7199 | 647 | -3493 | -3493 | -3493 | Critical Branch | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 339 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 19:30 |  | 7253 | 647 |  | 7255 | 647 | -3691 | -3691 | -3691 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -2 | 0 | -2 | 0 | 1 | -392 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 392 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 20:30 |  | 6797 | 647 |  | 6797 | 647 | -3486 | -3486 | -3486 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 122 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -63 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 21:30 |  | 7756 | 910 |  | 7651 | 904 | -2938 | -2938 | -2938 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 105 | 6 | 111 | 0 | 1 | 71 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 216 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 22:30 |  | 7974 | 895 |  | 7864 | 885 | -3084 | -3084 | -3084 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 110 | 10 | 120 | 0 | 1 | 148 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 204 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 4000 | None | Overload - Retrait Barre Genissiat 400kV | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-03 | October | 23:30 |  | 7460 | 975 |  | 7356 | 917 | -2514 | -2514 | -2514 | Critical Branch | ID schedules | 0 | NA | 104 | 58 | 162 | 0 | 1 | 8 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 234 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-04 | October | 12:30 | 8729 |  |  | 3360 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 5369 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 13:30 | 8729 |  |  | 3478 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 5251 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 14:30 | 8729 |  |  | 3226 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 5503 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 15:30 | 8729 |  |  | 4193 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 4536 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 4000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 16:30 | 8729 |  |  | 5982 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 2747 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 4000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 17:30 | 8729 |  |  | 6980 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1749 | NA | NA | NA | 0 | 1 | 152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 219 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8343 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 4000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 18:30 | 8729 |  |  | 6791 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1938 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 412 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7575 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 19:30 | 8729 |  |  | 7288 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1441 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 412 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 20:30 | 8729 |  |  | 6832 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1897 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 412 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6955 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 21:30 | 8729 |  |  | 7061 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1668 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 416 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7032 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 22:30 | 8729 |  |  | 6822 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1907 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 416 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7180 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-04 | October | 23:30 | 8119 |  |  | 6948 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1171 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 400 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6857 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-05 | October | 12:30 |  | 3459 | 655 |  | 2574 | 694 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 885 | -39 | 846 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-05 | October | 13:30 |  | 3603 | 655 |  | 3396 | 694 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 207 | -39 | 168 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-05 | October | 14:30 |  | 3610 | 655 |  | 3420 | 694 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 190 | -39 | 151 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-05 | October | 15:30 |  | 4730 | 889 |  | 4202 | 891 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 528 | -2 | 526 | 0 | 1 | 168 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -168 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-05 | October | 16:30 |  | 5146 | 888 |  | 4976 | 889 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 170 | -1 | 169 | 0 | 1 | 168 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -168 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-05 | October | 17:30 |  | 5779 | 888 |  | 5779 | 889 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -1 | -1 | 0 | 1 | 146 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -146 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-05 | October | 18:30 | 7972 |  |  | 7971 |  |  | -202 | -202 | -201 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 170 | None | None | 411 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-05 | October | 19:30 | 8107 |  |  | 8107 |  |  | -366 | -366 | -366 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 411 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-05 | October | 20:30 | 8107 |  |  | 8107 |  |  | -366 | -366 | -366 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 411 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-05 | October | 21:30 | 8281 |  |  | 8281 |  |  | -792 | -792 | -792 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 435 | None | None | None | None | None | None | None | None | 4000 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-05 | October | 22:30 | 7868 |  |  | 7868 |  |  | -251 | -251 | -252 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 433 | None | None | None | None | None | None | None | None | 4000 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-05 | October | 23:30 | 7829 |  |  | 7829 |  |  | -88 | -88 | -87 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 435 | None | None | None | None | None | None | None | None | 4000 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 12:30 | 2573 |  |  | 2573 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -69 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-06 | October | 13:30 | 2866 |  |  | 2866 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-06 | October | 14:30 | 3009 |  |  | 3009 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -69 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-06 | October | 15:30 | 3773 |  |  | 3773 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | None | -11 | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 16:30 | 4525 |  |  | 4527 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -2 | NA | NA | NA | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 150 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 17:30 | 4785 |  |  | 4785 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 150 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 18:30 |  | 5960 | 786 |  | 5957 | 786 | 7931 | -17 | 7931 | ID schedules | TTC Validation phase - bilateral reduction | 7948 | NA | 3 | 0 | 3 | -17 | 1 | 70 | None | None | 75 | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] CREYS-SAINT VULBAS 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 19:30 |  | 5875 | 786 |  | 5875 | 786 | 8304 | -17 | 8304 | ID schedules | TTC Validation phase - bilateral reduction | 8321 | NA | 0 | 0 | 0 | -17 | 1 | 70 | None | None | 88 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 20:30 |  | 5875 | 786 |  | 5875 | 786 | 8304 | -17 | 8304 | ID schedules | TTC Validation phase - bilateral reduction | 8321 | NA | 0 | 0 | 0 | -17 | 1 | 70 | None | None | 88 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 21:30 |  | 6681 | 881 |  | 6527 | 881 | -1269 | -1269 | -1269 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 154 | 0 | 154 | 0 | 1 | 50 | None | Reduction because NTC over thermal limit on border | 150 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD - GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 22:30 |  | 6686 | 881 |  | 6577 | 881 | -1268 | -1268 | -1268 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 109 | 0 | 109 | 0 | 1 | 50 | None | Reduction because NTC over thermal limit on border | 150 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD - GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-06 | October | 23:30 |  | 5889 | 901 |  | 5776 | 901 | -539 | -539 | -539 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 113 | 0 | 113 | 0 | 1 | 50 | None | Reduction because NTC over thermal limit on border | 150 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 3000 | None | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] Lavorgo-Musignano [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-07 | October | 12:30 |  | 3229 | 2763 |  | 3229 | 2746 | 1237 | 0 | 1237 | ID schedules | TTC Validation phase - bilateral reduction | 1237 | NA | 0 | 17 | 17 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 13:30 |  | 3229 | 2648 |  | 3229 | 2585 | 1227 | 0 | 1227 | ID schedules | TTC Validation phase - bilateral reduction | 1227 | NA | 0 | 63 | 63 | 0 | 1 | 69 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 12 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 14:30 |  | 3229 | 2230 |  | 3229 | 2021 | 1216 | 0 | 1216 | ID schedules | TTC Validation phase - bilateral reduction | 1216 | NA | 0 | 209 | 209 | 0 | 1 | -83 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 83 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 15:30 |  | 3229 | 2647 |  | 3229 | 1857 | 1171 | 0 | 1171 | ID schedules | TTC Validation phase - bilateral reduction | 1171 | NA | 0 | 790 | 790 | 0 | 1 | 80 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 123 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 16:30 |  | 3229 | 2656 |  | 3229 | 2072 | 1171 | 0 | 1171 | ID schedules | TTC Validation phase - bilateral reduction | 1171 | NA | 0 | 584 | 584 | 0 | 1 | 71 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 124 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 17:30 |  | 3229 | 2647 |  | 3229 | 1114 | 1171 | 0 | 1171 | ID schedules | TTC Validation phase - bilateral reduction | 1171 | NA | 0 | 1533 | 1533 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 124 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 18:30 |  | 5169 | 784 |  | 5169 | 784 | 10005 | -39 | 10005 | ID schedules | ID schedules | 10044 | NA | 0 | 0 | 0 | -39 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 38 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 19:30 |  | 4930 | 786 |  | 4829 | 786 | 9937 | -39 | 9937 | ID schedules | ID schedules | 9976 | NA | 101 | 0 | 101 | -39 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 43 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4596 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-07 | October | 20:30 |  | 4964 | 785 |  | 4919 | 763 | 10226 | -39 | 10226 | ID schedules | ID schedules | 10265 | NA | 45 | 22 | 67 | -39 | 1 | 69 | None | None | 56 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-07 | October | 21:30 |  | 4058 | 624 |  | 4043 | 301 | 947 | -32 | 947 | Critical Branch | TTC Validation phase - bilateral reduction | 979 | NA | 15 | 323 | 338 | -32 | 1 | 70 | None | Reduction because NTC over thermal limit on border | 21 | None | Reduction because NTC over thermal limit on border | None | None | Reduction due to missing redispatch potential | None | 3852 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-07 | October | 22:30 |  | 5396 | 786 |  | 5460 | 786 | 1472 | -32 | 1472 | ID schedules | TTC Validation phase - bilateral reduction | 1504 | NA | -64 | 0 | -64 | -32 | 1 | 70 | None | None | -67 | None | None | None | None | Reduction due to missing redispatch potential | None | 5268 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-07 | October | 23:30 |  | 5617 | 652 |  | 5617 | 627 | 875 | -32 | 875 | ID schedules | TTC Validation phase - bilateral reduction | 907 | NA | 0 | 25 | 25 | -32 | 1 | 64 | None | None | 208 | None | None | None | None | Reduction due to missing redispatch potential | None | 5426 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-08 | October | 12:30 | 1756 |  |  | 1773 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -17 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 13:30 | 2206 |  |  | 2206 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 14:30 | 2583 |  |  | 2598 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -15 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 15:30 |  | 2604 | 950 |  | 2604 | 345 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 605 | 605 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2400 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-08 | October | 16:30 |  | 2604 | 1546 |  | 2604 | 1233 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 313 | 313 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2400 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-08 | October | 17:30 |  | 2604 | 1360 |  | 2604 | 866 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 494 | 494 | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 2400 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-08 | October | 18:30 | 5989 |  |  | 5601 |  |  | 12083 | -14 | 12430 | Critical Branch | TTC Validation phase - bilateral reduction | 12097 | 388 | NA | NA | NA | 333 | 1 | 52 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -52 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2400 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 19:30 | 5989 |  |  | 5946 |  |  | 12019 | -14 | 12290 | Critical Branch | TTC Validation phase - bilateral reduction | 12033 | 43 | NA | NA | NA | 257 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2400 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 20:30 | 5989 |  |  | 5950 |  |  | 12021 | -14 | 12215 | Critical Branch | TTC Validation phase - bilateral reduction | 12035 | 39 | NA | NA | NA | 180 | 1 | -100 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 100 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2400 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 21:30 | 6518 |  |  | 6470 |  |  | -763 | -763 | -713 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 48 | NA | NA | NA | 0 | 1 | -210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2400 | None | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 22:30 | 6518 |  |  | 6478 |  |  | -764 | -764 | -722 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 40 | NA | NA | NA | 0 | 1 | -210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2400 | None | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-08 | October | 23:30 | 6730 |  |  | 6730 |  |  | -1065 | -1065 | -1065 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 210 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2400 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 12:30 | 4391 |  |  | 4473 |  |  | 0 | 0 | 1052 | ID schedules | ID schedules | 0 | -82 | NA | NA | NA | 1052 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1800 | None | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 13:30 | 4603 |  |  | 4603 |  |  | 0 | 0 | 1397 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 1397 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 14:30 | 4793 |  |  | 4793 |  |  | 0 | 0 | 1359 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 1359 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 15:30 |  | 5317 | 709 |  | 5177 | 709 | 1812 | -13 | 1812 | Critical Branch | ID schedules | 1825 | NA | 140 | 0 | 140 | -13 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1800 | None | Outage - RDCR FIL Link 1 & 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-09 | October | 16:30 |  | 5317 | 709 |  | 5188 | 709 | 1999 | -13 | 1999 | Critical Branch | ID schedules | 2012 | NA | 129 | 0 | 129 | -13 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1800 | None | Outage - RDCR FIL Link 1 & 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-09 | October | 17:30 |  | 5906 | 709 |  | 5906 | 709 | 2199 | -13 | 2199 | Critical Branch | ID schedules | 2212 | NA | 0 | 0 | 0 | -13 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1800 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-09 | October | 18:30 | 7514 |  |  | 7492 |  |  | -4440 | -4440 | -4418 | Critical Branch | ID schedules | 0 | 22 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - RO CHAFFARD G.ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 19:30 | 8036 |  |  | 8036 |  |  | -4801 | -4801 | -4801 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Avise [DIR][IT] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 20:30 | 7976 |  |  | 7976 |  |  | -4753 | -4753 | -4753 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-2 Albertville-Rondissone / [CH-IT] Riddes-Avise [DIR][IT] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 21:30 | 8122 |  |  | 8115 |  |  | 1689 | 9 | 1689 | Minimum Margin | ID schedules | 1680 | 7 | NA | NA | NA | 9 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - RO CHAFFARD G.ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 22:30 | 7688 |  |  | 7683 |  |  | 1703 | 9 | 1702 | Minimum Margin | ID schedules | 1694 | 5 | NA | NA | NA | 8 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - RO CHAFFARD G.ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-09 | October | 23:30 | 7530 |  |  | 7521 |  |  | 1611 | 9 | 1611 | Minimum Margin | ID schedules | 1602 | 9 | NA | NA | NA | 9 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - RO CHAFFARD G.ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 12:30 | 5489 |  |  | 5489 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 13:30 | 6248 |  |  | 6248 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 14:30 | 6319 |  |  | 6319 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 15:30 | 7183 |  |  | 7183 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 16:30 | 7383 |  |  | 7383 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 17:30 | 6507 |  |  | 6507 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 18:30 | 6362 |  |  | 6362 |  |  | 1491 | -16 | 1491 | Critical Branch | ID schedules | 1507 | 0 | NA | NA | NA | -16 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 19:30 | 7219 |  |  | 7219 |  |  | 1232 | -16 | 1232 | ID schedules | ID schedules | 1248 | 0 | NA | NA | NA | -16 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 20:30 | 7433 |  |  | 7431 |  |  | 1166 | -16 | 1167 | ID schedules | ID schedules | 1182 | 2 | NA | NA | NA | -15 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 21:30 | 8571 |  |  | 8026 |  |  | -785 | -785 | -305 | Critical Branch | ID schedules | 0 | 545 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage - Outage Chaffard - Gd ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 22:30 | 8571 |  |  | 8026 |  |  | -785 | -785 | -305 | Critical Branch | ID schedules | 0 | 545 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage - Outage Chaffard - Gd ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-10 | October | 23:30 | 7961 |  |  | 7574 |  |  | -157 | -157 | 182 | Critical Branch | ID schedules | 0 | 387 | NA | NA | NA | 182 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage - Outage Chaffard - Gd ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-11 | October | 12:30 |  | 2947 | 1455 |  | 2947 | 1822 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -367 | -367 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-11 | October | 13:30 |  | 2947 | 1755 |  | 2947 | 2056 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -301 | -301 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-11 | October | 14:30 |  | 2947 | 1562 |  | 2947 | 1908 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -346 | -346 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-11 | October | 15:30 |  | 4858 | 536 |  | 4450 | 536 | -150 | -150 | -150 | ID schedules | ID schedules | 0 | NA | 408 | 0 | 408 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-11 | October | 16:30 |  | 4619 | 536 |  | 4428 | 536 | -206 | -206 | -206 | ID schedules | ID schedules | 0 | NA | 191 | 0 | 191 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-11 | October | 17:30 |  | 5932 | 536 |  | 5938 | 536 | -269 | -269 | -269 | ID schedules | ID schedules | 0 | NA | -6 | 0 | -6 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-11 | October | 18:30 | 7167 |  |  | 7167 |  |  | -2030 | -2030 | -2029 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-11 | October | 19:30 | 7167 |  |  | 7167 |  |  | -2030 | -2030 | -2029 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-11 | October | 20:30 | 7167 |  |  | 7167 |  |  | -2030 | -2030 | -2029 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-11 | October | 21:30 | 8370 |  |  | 7914 |  |  | -3646 | -3646 | -3203 | Critical Branch | Critical Branch | 0 | 456 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage Chaffard - Gd Ile 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-11 | October | 22:30 | 8370 |  |  | 7914 |  |  | -3646 | -3646 | -3203 | Critical Branch | Critical Branch | 0 | 456 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage Chaffard - Gd Ile 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-11 | October | 23:30 | 7760 |  |  | 6893 |  |  | 0 | 0 | -2203 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 867 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2438 | None | Outage - Outage Chaffard - Gd ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-12 | October | 12:30 | 7917 |  |  | 2148 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 5769 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-12 | October | 13:30 | 7917 |  |  | 1994 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 5923 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-12 | October | 14:30 | 7917 |  |  | 1971 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 5946 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-12 | October | 15:30 | 7917 |  |  | 3526 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 4391 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-12 | October | 16:30 | 7917 |  |  | 4957 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 2960 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-12 | October | 17:30 | 7917 |  |  | 6872 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 1045 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-12 | October | 18:30 | 7917 |  |  | 7593 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 324 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-12 | October | 19:30 | 7917 |  |  | 7564 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 353 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-12 | October | 20:30 | 7917 |  |  | 7641 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 276 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-12 | October | 21:30 | 7917 |  |  | 7584 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 333 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-12 | October | 22:30 | 7917 |  |  | 7540 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 377 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-12 | October | 23:30 | 7917 |  |  | 7540 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 377 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Outage CHAFFARD - GD ILE 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 12:30 | 4491 |  |  | 4491 |  |  | 3094 | -1 | 3097 | ID schedules | ID schedules | 3095 | 0 | NA | NA | NA | 2 | 1 | 154 | None | None | 11 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 13:30 | 5368 |  |  | 5368 |  |  | 2996 | -1 | 3029 | ID schedules | ID schedules | 2997 | 0 | NA | NA | NA | 32 | 1 | 154 | None | None | 235 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 14:30 | 5562 |  |  | 5562 |  |  | 2987 | -1 | 3051 | ID schedules | ID schedules | 2988 | 0 | NA | NA | NA | 63 | 1 | 154 | None | None | 261 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 15:30 |  | 4872 | 256 |  | 4960 | 74 | 2852 | -71 | 2852 | ID schedules | ID schedules | 2923 | NA | -88 | 182 | 94 | -71 | 1 | 45 | None | None | 402 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 16:30 |  | 4655 | 533 |  | 4600 | 521 | 2854 | -71 | 2854 | ID schedules | TTC Validation phase - bilateral reduction | 2925 | NA | 55 | 12 | 67 | -71 | 1 | 103 | None | None | 399 | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4414 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 17:30 |  | 4033 | 292 |  | 3599 | 275 | 2873 | -71 | 2873 | ID schedules | ID schedules | 2944 | NA | 434 | 17 | 451 | -71 | 1 | 14 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 2932 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-13 | October | 18:30 | 6740 |  |  | 6357 |  |  | 4692 | -20 | 5029 | Critical Branch | TTC Validation phase - bilateral reduction | 4712 | 383 | NA | NA | NA | 317 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 326 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6404 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-13 | October | 19:30 | 6740 |  |  | 6739 |  |  | 4696 | -20 | 5053 | Critical Branch | TTC Validation phase - bilateral reduction | 4716 | 1 | NA | NA | NA | 337 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 324 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6404 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-13 | October | 20:30 | 6740 |  |  | 6739 |  |  | 4678 | -20 | 5026 | Critical Branch | TTC Validation phase - bilateral reduction | 4698 | 1 | NA | NA | NA | 328 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 400 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6404 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-13 | October | 21:30 |  | 7222 | 524 |  | 6952 | 238 | -2939 | -2939 | -2939 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 270 | 286 | 556 | 0 | 1 | -434 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 434 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - maintenance work on bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-13 | October | 22:30 |  | 7224 | 524 |  | 6955 | 475 | -2940 | -2940 | -2940 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 269 | 49 | 318 | 0 | 1 | 154 | None | None | 434 | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - maintenance work on bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-13 | October | 23:30 |  | 6776 | 544 |  | 6586 | 453 | -2415 | -2415 | -2415 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 190 | 91 | 281 | 0 | 1 | 169 | None | None | 419 | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - maintenance work on bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 12:30 |  | 5136 | 889 |  | 5138 | 889 | 1838 | -16 | 1838 | ID schedules | TTC Validation phase - bilateral reduction | 1854 | NA | -2 | 0 | -2 | -16 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 4947 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 13:30 |  | 5351 | 889 |  | 5351 | 876 | 1667 | -16 | 1667 | ID schedules | TTC Validation phase - bilateral reduction | 1683 | NA | 0 | 13 | 13 | -16 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 5160 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 14:30 |  | 5629 | 889 |  | 5629 | 889 | 1785 | -16 | 1785 | ID schedules | TTC Validation phase - bilateral reduction | 1801 | NA | 0 | 0 | 0 | -16 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 5438 | Reduction due to missing redispatch potential | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 15:30 |  | 6985 | 871 |  | 6263 | 870 | -783 | -783 | -783 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 722 | 1 | 723 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 16:30 |  | 7046 | 648 |  | 6635 | 605 | -787 | -787 | -787 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 411 | 43 | 454 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 17:30 |  | 6798 | 648 |  | 6396 | 339 | -727 | -727 | -727 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 402 | 309 | 711 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-14 | October | 18:30 | 6436 |  |  | 6436 |  |  | -2563 | -2563 | -2561 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N Situation / [AT-AT] PST Nauders 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-14 | October | 19:30 | 6436 |  |  | 6436 |  |  | -2563 | -2563 | -2562 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N Situation / [AT-AT] PST Nauders 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-14 | October | 20:30 | 6436 |  |  | 6436 |  |  | -2564 | -2564 | -2562 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N Situation / [AT-AT] PST Nauders 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-14 | October | 21:30 |  | 7171 | 575 |  | 6669 | 356 | -3983 | -3983 | -3983 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 502 | 219 | 721 | 0 | 1 | None | None | None | None | None | None | None | None | Missing CNEC in CC: CNE: 380/220kV Lavorgo [OPP], C: N-2 Pradella-Robbia + Filisur-Robbia | None | 6927 | Missing CNEC in CC: CNE: 380/220kV Lavorgo [OPP], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | 3000 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-14 | October | 22:30 |  | 7165 | 647 |  | 6689 | 638 | -3980 | -3980 | -3980 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 476 | 9 | 485 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-14 | October | 23:30 |  | 6728 | 916 |  | 6334 | 902 | -3443 | -3443 | -3443 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 394 | 14 | 408 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - Bus bar 2.1 GENISSIAT | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-15 | October | 12:30 |  | 6278 | 438 |  | 5968 | 483 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 310 | -45 | 265 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 13:30 |  | 6278 | 331 |  | 5968 | 389 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 310 | -58 | 252 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 14:30 |  | 6278 | 565 |  | 5971 | 518 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 307 | 47 | 354 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 15:30 |  | 7165 | 775 |  | 6699 | 769 | -3533 | -3533 | -3533 | ID schedules | ID schedules | 0 | NA | 466 | 6 | 472 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 16:30 |  | 7165 | 651 |  | 6699 | 532 | -3533 | -3533 | -3533 | Critical Branch | ID schedules | 0 | NA | 466 | 119 | 585 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 17:30 |  | 7165 | 666 |  | 6699 | 296 | -3533 | -3533 | -3533 | Critical Branch | ID schedules | 0 | NA | 466 | 370 | 836 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 18:30 | 6698 |  |  | 6369 |  |  | -2952 | -2952 | -2589 | Critical Branch | ID schedules | 0 | 329 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-15 | October | 19:30 | 6698 |  |  | 6275 |  |  | -2969 | -2969 | -2510 | Critical Branch | ID schedules | 0 | 423 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-15 | October | 20:30 | 6698 |  |  | 6698 |  |  | -2960 | -2960 | -2960 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-15 | October | 21:30 |  | 7358 | 597 |  | 6788 | 368 | -943 | -943 | -943 | Critical Branch | ID schedules | 0 | NA | 570 | 229 | 799 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 22:30 |  | 7240 | 666 |  | 6686 | 667 | -941 | -941 | -941 | ID schedules | ID schedules | 0 | NA | 554 | -1 | 553 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-15 | October | 23:30 |  | 6637 | 662 |  | 6221 | -230 | -319 | -319 | -319 | Critical Branch | ID schedules | 0 | NA | 416 | 892 | 1308 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-16 | October | 12:30 | 5291 |  |  | 5291 |  |  | 3673 | 3 | 3674 | Minimum Margin | ID schedules | 3670 | 0 | NA | NA | NA | 4 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | 6245 | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 13:30 | 5229 |  |  | 5229 |  |  | 3673 | 3 | 3673 | Minimum Margin | ID schedules | 3670 | 0 | NA | NA | NA | 3 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | 6245 | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 14:30 | 5236 |  |  | 5236 |  |  | 3673 | 3 | 3673 | Minimum Margin | ID schedules | 3670 | 0 | NA | NA | NA | 3 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | 6245 | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 15:30 |  | 5454 | 552 |  | 5408 | 552 | 1745 | 0 | 1745 | Critical Branch | ID schedules | 1745 | NA | 46 | 0 | 46 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-16 | October | 16:30 |  | 6199 | 708 |  | 6306 | 708 | 1716 | 0 | 1716 | ID schedules | ID schedules | 1716 | NA | -107 | 0 | -107 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-16 | October | 17:30 |  | 6381 | 708 |  | 6474 | 708 | 1724 | 0 | 1724 | ID schedules | ID schedules | 1724 | NA | -93 | 0 | -93 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-16 | October | 18:30 | 8380 |  |  | 7986 |  |  | 4445 | 348 | 4468 | Minimum Margin | ID schedules | 4097 | 394 | NA | NA | NA | 371 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 19:30 | 8380 |  |  | 7978 |  |  | 4439 | 348 | 4472 | Minimum Margin | ID schedules | 4091 | 402 | NA | NA | NA | 381 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 20:30 | 8380 |  |  | 7982 |  |  | 4439 | 348 | 4468 | Minimum Margin | ID schedules | 4091 | 398 | NA | NA | NA | 377 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 21:30 | 8441 |  |  | 8025 |  |  | -921 | -921 | -546 | Critical Branch | ID schedules | 0 | 416 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 22:30 | 8441 |  |  | 8022 |  |  | -920 | -920 | -542 | Critical Branch | ID schedules | 0 | 419 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-16 | October | 23:30 | 7831 |  |  | 7569 |  |  | -286 | -286 | -50 | Critical Branch | ID schedules | 0 | 262 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3000 | None | Outage - CHAFFARD GRANDE ILE 1 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-17 | October | 12:30 | 6900 |  |  | 6900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 13:30 | 6900 |  |  | 6900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 14:30 | 6900 |  |  | 6900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 15:30 | 6900 |  |  | 6900 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 16:30 | 6900 |  |  | 6900 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 17:30 | 7800 |  |  | 7800 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 18:30 | 6945 |  |  | 6945 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 19:30 | 7522 |  |  | 7522 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 20:30 | 8599 |  |  | 8602 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -3 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 21:30 | 8543 |  |  | 8543 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 22:30 | 7867 |  |  | 7867 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-17 | October | 23:30 | 7730 |  |  | 7730 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 12:30 | 5878 |  |  | 5878 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-18 | October | 13:30 | 6346 |  |  | 6345 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-18 | October | 14:30 | 6132 |  |  | 6131 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-18 | October | 15:30 |  | 7880 | 773 |  | 6030 | 773 | -4095 | -4095 | -4095 | ID schedules | ID schedules | 0 | NA | 1850 | 0 | 1850 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-18 | October | 16:30 |  | 7821 | 773 |  | 7657 | 773 | -4074 | -4074 | -4074 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 164 | 0 | 164 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 17:30 |  | 7939 | 773 |  | 7939 | 773 | -4115 | -4115 | -4115 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 18:30 |  | 8220 | 738 |  | 8220 | 738 | -4152 | -4152 | -4152 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 19:30 |  | 8182 | 738 |  | 8217 | 738 | -4152 | -4152 | -4152 | Critical Branch | ID schedules | 0 | NA | -35 | 0 | -35 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 20:30 |  | 8197 | 738 |  | 8197 | 738 | -4128 | -4128 | -4128 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 21:30 | 8882 |  |  | 8882 |  |  | -636 | -636 | -635 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 22:30 | 8882 |  |  | 8882 |  |  | -636 | -636 | -635 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-18 | October | 23:30 | 8272 |  |  | 8272 |  |  | -6 | -6 | -4 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 12:30 |  | 5234 | 718 |  | 4630 | 718 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 604 | 0 | 604 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-19 | October | 13:30 |  | 5321 | 718 |  | 4640 | 718 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 681 | 0 | 681 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-19 | October | 14:30 |  | 5363 | 718 |  | 4645 | 718 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 718 | 0 | 718 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-19 | October | 15:30 |  | 7625 | 980 |  | 5911 | 980 | -114 | -114 | -114 | Critical Branch | ID schedules | 0 | NA | 1714 | 0 | 1714 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-19 | October | 16:30 |  | 7617 | 1000 |  | 6440 | 1000 | -92 | -92 | -92 | Critical Branch | ID schedules | 0 | NA | 1177 | 0 | 1177 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-19 | October | 17:30 |  | 7717 | 980 |  | 7678 | 980 | -155 | -155 | -155 | Critical Branch | ID schedules | 0 | NA | 39 | 0 | 39 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 18:30 |  | 8133 | 796 |  | 8133 | 796 | -305 | -305 | -305 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 19:30 |  | 8246 | 796 |  | 8246 | 796 | -362 | -362 | -362 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 20:30 |  | 8246 | 796 |  | 8246 | 796 | -362 | -362 | -362 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 4100 | None | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 21:30 | 8792 |  |  | 8792 |  |  | -262 | -262 | -259 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 22:30 | 8792 |  |  | 8792 |  |  | -262 | -262 | -259 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-19 | October | 23:30 | 8792 |  |  | 8792 |  |  | -262 | -262 | -259 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 12:30 | 8850 |  |  | 8850 |  |  | -1554 | -1554 | -1553 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 13:30 | 8850 |  |  | 8850 |  |  | -1554 | -1554 | -1553 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 14:30 | 8850 |  |  | 8850 |  |  | -1554 | -1554 | -1553 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 15:30 |  | 7799 | 656 |  | 7677 | 656 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 122 | 0 | 122 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 16:30 |  | 7757 | 658 |  | 7757 | 658 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 17:30 |  | 7754 | 658 |  | 7754 | 658 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 18:30 |  | 7574 | 642 |  | 7574 | 642 | -642 | -642 | -642 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 19:30 |  | 7604 | 642 |  | 7604 | 642 | -647 | -647 | -647 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 20:30 |  | 7630 | 642 |  | 7630 | 642 | -652 | -652 | -652 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 21:30 |  | 7153 | 702 |  | 7153 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 22:30 |  | 7153 | 702 |  | 7153 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-20 | October | 23:30 |  | 6773 | 140 |  | 6787 | 140 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -14 | 0 | -14 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-21 | October | 12:30 | 9036 |  |  | 8182 |  |  | -1184 | -1184 | -442 | Critical Branch | ID schedules | 0 | 854 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-21 | October | 13:30 | 9036 |  |  | 8182 |  |  | -1184 | -1184 | -442 | Critical Branch | ID schedules | 0 | 854 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-21 | October | 14:30 | 9036 |  |  | 8182 |  |  | -1184 | -1184 | -442 | Critical Branch | ID schedules | 0 | 854 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-21 | October | 15:30 |  | 6687 | 702 |  | 6666 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 21 | 0 | 21 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-21 | October | 16:30 |  | 6687 | 702 |  | 6666 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 21 | 0 | 21 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-21 | October | 17:30 |  | 6687 | 702 |  | 6666 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 21 | 0 | 21 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-21 | October | 18:30 |  | 7000 | 697 |  | 6939 | 697 | -4351 | -4351 | -4351 | Critical Branch | ID schedules | 0 | NA | 61 | 0 | 61 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-21 | October | 19:30 |  | 7000 | 697 |  | 6939 | 697 | -4351 | -4351 | -4351 | Critical Branch | ID schedules | 0 | NA | 61 | 0 | 61 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-21 | October | 20:30 |  | 6962 | 697 |  | 6921 | 697 | -4338 | -4338 | -4338 | Critical Branch | ID schedules | 0 | NA | 41 | 0 | 41 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-21 | October | 21:30 | 7612 |  |  | 7438 |  |  | 368 | -68 | 724 | Critical Branch | ID schedules | 436 | 174 | NA | NA | NA | 288 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-21 | October | 22:30 | 7612 |  |  | 7438 |  |  | 368 | -68 | 724 | Critical Branch | ID schedules | 436 | 174 | NA | NA | NA | 288 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-21 | October | 23:30 | 7002 |  |  | 6882 |  |  | 704 | -66 | 942 | Critical Branch | ID schedules | 770 | 120 | NA | NA | NA | 172 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-22 | October | 12:30 | 6530 |  |  | 6530 |  |  | 5636 | -63 | 5636 | ID schedules | ID schedules | 5699 | 0 | NA | NA | NA | -63 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-22 | October | 13:30 | 6618 |  |  | 6618 |  |  | 5636 | -63 | 5636 | ID schedules | ID schedules | 5699 | 0 | NA | NA | NA | -63 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-22 | October | 14:30 | 7052 |  |  | 7052 |  |  | 5636 | -63 | 5636 | ID schedules | ID schedules | 5699 | 0 | NA | NA | NA | -63 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-22 | October | 15:30 |  | 6495 | 502 |  | 6502 | 502 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -7 | 0 | -7 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 16:30 |  | 6473 | 702 |  | 6487 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -14 | 0 | -14 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 17:30 |  | 6207 | 702 |  | 6233 | 702 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -26 | 0 | -26 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 18:30 |  | 5830 | 877 |  | 5919 | 877 | -2495 | -2495 | -2495 | ID schedules | ID schedules | 0 | NA | -89 | 0 | -89 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 19:30 |  | 5839 | 896 |  | 5931 | 903 | -2497 | -2497 | -2497 | ID schedules | ID schedules | 0 | NA | -92 | -7 | -99 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 20:30 |  | 5793 | 877 |  | 5865 | 877 | -2475 | -2475 | -2475 | ID schedules | ID schedules | 0 | NA | -72 | 0 | -72 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 21:30 |  | 8551 | 860 |  | 7227 | 860 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1324 | 0 | 1324 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 22:30 |  | 8551 | 860 |  | 7227 | 860 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1324 | 0 | 1324 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-22 | October | 23:30 |  | 8048 | 880 |  | 6792 | 880 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1256 | 0 | 1256 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 12:30 | 9629 |  |  | 8979 |  |  | -5803 | -5803 | -5198 | Critical Branch | ID schedules | 0 | 650 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-23 | October | 13:30 | 9629 |  |  | 8979 |  |  | -5803 | -5803 | -5198 | Critical Branch | ID schedules | 0 | 650 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-23 | October | 14:30 | 9629 |  |  | 8979 |  |  | -5803 | -5803 | -5198 | Critical Branch | ID schedules | 0 | 650 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-23 | October | 15:30 |  | 7448 | 760 |  | 7540 | 760 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | -92 | 0 | -92 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 16:30 |  | 7567 | 829 |  | 7645 | 837 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -78 | -8 | -86 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 17:30 |  | 7579 | 819 |  | 7669 | 829 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -90 | -10 | -100 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 18:30 |  | 8641 | 667 |  | 8478 | 667 | -3431 | -3431 | -3431 | Critical Branch | ID schedules | 0 | NA | 163 | 0 | 163 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 19:30 |  | 8641 | 667 |  | 8478 | 667 | -3431 | -3431 | -3431 | Critical Branch | ID schedules | 0 | NA | 163 | 0 | 163 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 20:30 |  | 8627 | 667 |  | 8471 | 667 | -3424 | -3424 | -3424 | Critical Branch | ID schedules | 0 | NA | 156 | 0 | 156 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-23 | October | 21:30 | 9648 |  |  | 9084 |  |  | -2948 | -2948 | -2399 | Critical Branch | ID schedules | 0 | 564 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-23 | October | 22:30 | 9648 |  |  | 9084 |  |  | -2948 | -2948 | -2399 | Critical Branch | ID schedules | 0 | 564 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-23 | October | 23:30 | 8838 |  |  | 8247 |  |  | -2130 | -2130 | -1554 | Critical Branch | ID schedules | 0 | 591 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-24 | October | 12:30 | 8153 |  |  | 8153 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 13:30 | 8153 |  |  | 8153 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 14:30 | 8153 |  |  | 8153 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 15:30 | 8153 |  |  | 8153 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 16:30 | 8153 |  |  | 8153 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 17:30 | 8298 |  |  | 8298 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 18:30 | 8607 |  |  | 8607 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9310 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 19:30 | 8640 |  |  | 8640 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9310 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 20:30 | 8595 |  |  | 8595 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9310 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 21:30 | 8523 |  |  | 8523 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9310 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 22:30 | 8153 |  |  | 8153 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9310 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-24 | October | 23:30 | 7543 |  |  | 7543 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 8700 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 12:30 | 5310 |  |  | 5310 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 238 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-25 | October | 13:30 | 5269 |  |  | 5269 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 238 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-25 | October | 14:30 | 5300 |  |  | 5300 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 6 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-25 | October | 15:30 |  | 7213 | 181 |  | 6877 | 180 | 41 | 41 | 41 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 336 | 1 | 337 | 41 | 1 | 155 | None | None | 357 | None | None | None | None | Reduction due to missing redispatch potential | None | 6975 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 16:30 |  | 7213 | 181 |  | 7158 | 180 | 41 | 41 | 41 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 55 | 1 | 56 | 41 | 1 | 155 | None | None | 357 | None | None | None | None | Reduction due to missing redispatch potential | None | 6975 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 17:30 |  | 7354 | 180 |  | 7354 | 180 | -6 | -6 | -6 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 155 | None | None | 175 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 18:30 |  | 7812 | 839 |  | 7811 | 839 | -526 | -526 | -526 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 0 | 1 | 0 | 1 | 149 | None | None | 398 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 19:30 |  | 7812 | 839 |  | 7811 | 839 | -526 | -526 | -526 | Critical Branch | Min import NTC Threshold | 0 | NA | 1 | 0 | 1 | 0 | 1 | 149 | None | None | 398 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 20:30 |  | 7532 | 839 |  | 7532 | 839 | -435 | -435 | -435 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 149 | None | None | 383 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 21:30 | 8990 |  |  | 8989 |  |  | -850 | -850 | -849 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | 154 | None | None | 421 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 22:30 | 8990 |  |  | 8989 |  |  | -850 | -850 | -849 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | 154 | None | None | 421 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-25 | October | 23:30 | 8380 |  |  | 8379 |  |  | -221 | -221 | -218 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | 170 | None | None | 405 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 12:30 |  | 5562 | 902 |  | 5562 | 911 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -9 | -9 | 0 | 1 | 167 | None | None | -108 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 13:30 |  | 5815 | 902 |  | 5815 | 911 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -9 | -9 | 0 | 1 | 170 | None | None | -113 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 14:30 |  | 5569 | 898 |  | 5569 | 901 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -3 | -3 | 0 | 1 | 170 | None | None | -169 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 15:30 |  | 8039 | 757 |  | 7534 | 757 | -1713 | -1713 | -1713 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 505 | 0 | 505 | 0 | 1 | 170 | None | None | 271 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 16:30 |  | 8039 | 757 |  | 8038 | 757 | -1688 | -1688 | -1688 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 168 | None | None | 367 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 17:30 |  | 8137 | 757 |  | 8131 | 757 | -1749 | -1749 | -1749 | Critical Branch | ID schedules | 0 | NA | 6 | 0 | 6 | 0 | 1 | 168 | None | None | 435 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 18:30 | 8562 |  |  | 8566 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -4 | NA | NA | NA | 0 | 1 | 170 | None | None | 435 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 19:30 | 8697 |  |  | 8697 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-26 | October | 20:30 | 8597 |  |  | 8597 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -420 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-26 | October | 21:30 | 8168 |  |  | 8168 |  |  | -3136 | -3136 | -3136 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 420 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 22:30 | 8168 |  |  | 8168 |  |  | -3136 | -3136 | -3136 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 420 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-26 | October | 23:30 | 8168 |  |  | 8168 |  |  | -3136 | -3136 | -3136 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | None | 420 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-27 | October | 12:30 |  | 7356 | 868 |  | 5918 | 870 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1438 | -2 | 1436 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 13:30 |  | 7356 | 868 |  | 6355 | 871 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1001 | -3 | 998 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 14:30 |  | 6277 | 883 |  | 6276 | 883 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 15:30 |  | 7301 | 740 |  | 7092 | 740 | -3973 | -3973 | -3973 | ID schedules | ID schedules | 0 | NA | 209 | 0 | 209 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 16:30 |  | 7818 | 740 |  | 7818 | 740 | -4254 | -4254 | -4254 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 17:30 |  | 7954 | 740 |  | 7954 | 740 | -4261 | -4261 | -4261 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 18:30 |  | 8581 | 832 |  | 8522 | 832 | -5150 | -5150 | -5150 | Critical Branch | ID schedules | 0 | NA | 59 | 0 | 59 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 19:30 |  | 8898 | 832 |  | 8898 | 832 | -5422 | -5422 | -5422 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 20:30 |  | 8419 | 832 |  | 8419 | 832 | -5664 | -5664 | -5664 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-27 | October | 21:30 | 8400 |  |  | 8353 |  |  | -4310 | -4310 | -4257 | Critical Branch | ID schedules | 0 | 47 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-27 | October | 22:30 | 8400 |  |  | 8353 |  |  | -4310 | -4310 | -4257 | Critical Branch | ID schedules | 0 | 47 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-27 | October | 23:30 | 7790 |  |  | 7742 |  |  | -3706 | -3706 | -3652 | Critical Branch | ID schedules | 0 | 48 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-28 | October | 12:30 |  | 7288 | 155 |  | 7250 | 73 | 98 | 11 | 98 | Minimum Margin | ID schedules | 87 | NA | 38 | 82 | 120 | 11 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 13:30 |  | 7424 | 181 |  | 7424 | 180 | 83 | 11 | 83 | Minimum Margin | ID schedules | 72 | NA | 0 | 1 | 1 | 11 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 14:30 |  | 7288 | 181 |  | 7250 | 180 | 148 | 11 | 148 | Minimum Margin | ID schedules | 137 | NA | 38 | 1 | 39 | 11 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 15:30 |  | 6802 | 703 |  | 6792 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 10 | 0 | 10 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 16:30 |  | 8723 | 736 |  | 8723 | 736 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 17:30 |  | 8944 | 675 |  | 8944 | 675 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 18:30 |  | 8801 | 698 |  | 8801 | 698 | -3385 | -3385 | -3385 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 19:30 |  | 8801 | 304 |  | 8801 | 316 | -3909 | -3909 | -3909 | ID schedules | ID schedules | 0 | NA | 0 | -12 | -12 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 20:30 |  | 8801 | 6 |  | 8801 | 6 | -4150 | -4150 | -4150 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-28 | October | 21:30 | 8502 |  |  | 8502 |  |  | -2878 | -2878 | -2878 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-28 | October | 22:30 | 8414 |  |  | 8414 |  |  | -2781 | -2781 | -2781 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-28 | October | 23:30 | 7604 |  |  | 7604 |  |  | -1962 | -1962 | -1962 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-29 | October | 12:30 | 7824 |  |  | 7179 |  |  | -4308 | -4308 | -3723 | Critical Branch | ID schedules | 0 | 645 | NA | NA | NA | 0 | 1 | -349 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 349 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-29 | October | 13:30 | 7824 |  |  | 7823 |  |  | -4308 | -4308 | -4305 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | 154 | None | None | 371 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-29 | October | 14:30 | 7824 |  |  | 7823 |  |  | -4308 | -4308 | -4305 | Critical Branch | Critical Branch | 0 | 1 | NA | NA | NA | 0 | 1 | 154 | None | None | 371 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-29 | October | 15:30 |  | 7713 | 935 |  | 7713 | 935 | -393 | -393 | -393 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 145 | None | None | 408 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-29 | October | 16:30 |  | 8680 | 955 |  | 8680 | 955 | -1267 | -1267 | -1267 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-29 | October | 17:30 |  | 8762 | 935 |  | 8747 | 935 | -1419 | -1419 | -1419 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 15 | 0 | 15 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-10-29 | October | 18:30 | 9560 |  |  | 9511 |  |  | -2464 | -2464 | -2432 | Critical Branch | ID schedules | 0 | 49 | NA | NA | NA | 0 | 1 | 153 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 334 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-29 | October | 19:30 | 9560 |  |  | 9560 |  |  | -2469 | -2469 | -2469 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 416 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-29 | October | 20:30 | 9560 |  |  | 9560 |  |  | -2469 | -2469 | -2469 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 416 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-29 | October | 21:30 | 9214 |  |  | 9178 |  |  | 803 | 340 | 487 | Minimum Margin | ID schedules | 463 | 36 | NA | NA | NA | 24 | 1 | 154 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 354 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-10-29 | October | 22:30 | 9214 |  |  | 9213 |  |  | 803 | 340 | 465 | Minimum Margin | Minimum Margin | 463 | 1 | NA | NA | NA | 2 | 1 | 154 | None | None | 389 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-29 | October | 23:30 | 8404 |  |  | 8403 |  |  | 1609 | 340 | 1271 | Minimum Margin | TTC Validation phase - bilateral reduction | 1269 | 1 | NA | NA | NA | 2 | 1 | 170 | None | None | 371 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 12:30 | 8662 |  |  | 8662 |  |  | 0 | 0 | -2959 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 13:30 | 8662 |  |  | 8662 |  |  | 0 | 0 | -2959 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 14:30 | 8662 |  |  | 8662 |  |  | 0 | 0 | -2959 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 15:30 |  | 7734 | 670 |  | 7734 | 670 | 2128 | 0 | 2128 | ID schedules | ID schedules | 2128 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 16:30 |  | 7771 | 670 |  | 7771 | 670 | 2243 | 0 | 2243 | ID schedules | ID schedules | 2243 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 17:30 |  | 7771 | 670 |  | 7771 | 670 | 2148 | 0 | 2148 | ID schedules | ID schedules | 2148 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 18:30 | 8427 |  |  | 8427 |  |  | -2140 | -2140 | -2138 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 19:30 | 8427 |  |  | 8427 |  |  | -2140 | -2140 | -2138 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 20:30 | 8427 |  |  | 8427 |  |  | -2140 | -2140 | -2138 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 21:30 | 8454 |  |  | 8454 |  |  | -2235 | -2235 | -2233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 22:30 | 8454 |  |  | 8454 |  |  | -2235 | -2235 | -2233 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-30 | October | 23:30 | 7844 |  |  | 7844 |  |  | -1620 | -1620 | -1618 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-10-31 | October | 12:30 | 8787 |  |  | 7312 |  |  | -1355 | -1355 | -88 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1475 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted violation | None | None | None
2025-10-31 | October | 13:30 | 8787 |  |  | 7312 |  |  | -1355 | -1355 | -88 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1475 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted violation | None | None | None
2025-10-31 | October | 14:30 | 8787 |  |  | 7312 |  |  | -1355 | -1355 | -88 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1475 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | forecasted violation | None | None | None
2025-10-31 | October | 15:30 |  | 6503 | 829 |  | 6503 | 829 | -3359 | -3359 | -3359 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted violation
2025-10-31 | October | 16:30 |  | 6865 | 849 |  | 6411 | 849 | -2471 | -2471 | -2471 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 454 | 0 | 454 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted violation
2025-10-31 | October | 17:30 |  | 6392 | 829 |  | 5914 | 829 | -1757 | -1757 | -1757 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 478 | 0 | 478 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | forecasted violation
2025-10-31 | October | 18:30 |  | 7606 | 983 |  | 5734 | 983 | -3077 | -3077 | -3077 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1872 | 0 | 1872 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted violation
2025-10-31 | October | 19:30 |  | 7605 | 983 |  | 5734 | 983 | -3077 | -3077 | -3077 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1871 | 0 | 1871 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted violation
2025-10-31 | October | 20:30 |  | 7605 | 983 |  | 5734 | 983 | -3077 | -3077 | -3077 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1871 | 0 | 1871 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted violation
2025-10-31 | October | 21:30 | 8564 |  |  | 6641 |  |  | 0 | 0 | 2233 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1923 | NA | NA | NA | 2233 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | forecasted violation | None | None | None
2025-10-31 | October | 22:30 | 8940 |  |  | 6986 |  |  | 539 | 376 | 1877 | Minimum Margin | TTC Validation phase - bilateral reduction | 163 | 1954 | NA | NA | NA | 1714 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | forecasted violation | None | None | None
2025-10-31 | October | 23:30 | 7954 |  |  | 6789 |  |  | 0 | 0 | 2145 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1165 | NA | NA | NA | 2145 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2400 | None | forecasted violation | None | None | None

## ID 70% reduction
ID 70% reduction results
|  |  | TTC Adjustment |  |  | ANTC |  | LimitedBy
BD | Month | TS | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | Adjustment | 70% reduction | % reduction | Category
2025-12-02 | December | 12:30 |  | 9087 | 939 | 3669 | 233 | Minimum Margin | 3436 | 93.65% | above 1000 MW
2025-12-02 | December | 13:30 |  | 9085 | 939 | 3670 | 233 | Minimum Margin | 3437 | 93.65% | above 1000 MW
2025-12-02 | December | 14:30 |  | 9198 | 939 | 3630 | 233 | Minimum Margin | 3397 | 93.58% | above 1000 MW
2025-12-02 | December | 15:30 |  | 9762 | 760 | 3275 | 223 | Minimum Margin | 3052 | 93.19% | above 1000 MW
2025-12-02 | December | 16:30 |  | 9395 | 760 | 3477 | 223 | Minimum Margin | 3254 | 93.59% | above 1000 MW
2025-12-02 | December | 17:30 |  | 8628 | 740 | 3770 | 223 | Minimum Margin | 3547 | 94.08% | above 1000 MW
2025-12-02 | December | 18:30 |  | 8732 | 852 | 3567 | 222 | Minimum Margin | 3345 | 93.78% | above 1000 MW
2025-12-02 | December | 19:30 |  | 9093 | 852 | 3451 | 222 | Minimum Margin | 3229 | 93.57% | above 1000 MW
2025-12-02 | December | 20:30 |  | 9117 | 919 | 3442 | 222 | Minimum Margin | 3220 | 93.55% | above 1000 MW
2025-12-03 | December | 21:30 |  | 5902 | 544 | 245 | -103 | Critical Branch | 348 | 142% | below 500 MW
2025-12-05 | December | 15:30 | 8824 |  |  | 3377 | -66 | Critical Branch | 3443 | 102% | above 1000 MW
2025-12-05 | December | 16:30 | 8824 |  |  | 3380 | -66 | Critical Branch | 3446 | 102% | above 1000 MW
2025-12-05 | December | 17:30 | 8824 |  |  | 3374 | -66 | Critical Branch | 3440 | 102% | above 1000 MW
2025-12-18 | December | 21:30 |  | 5916 | 141 | 3401 | 78 | Minimum Margin | 3323 | 97.71% | above 1000 MW
2025-12-18 | December | 22:30 |  | 6280 | 141 | 2997 | 78 | Minimum Margin | 2919 | 97.4% | above 1000 MW
2025-12-18 | December | 23:30 |  | 5253 | 186 | 3392 | 78 | Minimum Margin | 3314 | 97.7% | above 1000 MW
2025-12-19 | December | 23:30 |  | 7912 | 154 | 3461 | -89 | Critical Branch | 3550 | 102.6% | above 1000 MW
2025-12-21 | December | 17:30 |  | 9230 | 976 | -33 | -91 | Critical Branch | 58 | -175.8% | below 500 MW
2025-12-29 | December | 18:30 |  | 8266 | 924 | 719 | 229 | Minimum Margin | 490 | 68.15% | [500-1000] MW
2025-12-29 | December | 19:30 |  | 8266 | 909 | 719 | 229 | Minimum Margin | 490 | 68.15% | [500-1000] MW
2025-12-29 | December | 20:30 |  | 8266 | 924 | 719 | 229 | Minimum Margin | 490 | 68.15% | [500-1000] MW
2025-11-06 | November | 20:30 |  | 8514 | 695 | 242 | -94 | Critical Branch | 336 | 138.8% | below 500 MW
2025-11-09 | November | 15:30 |  | 8903 | 756 | 2758 | -59 | Critical Branch | 2817 | 102.1% | above 1000 MW
2025-11-10 | November | 12:30 |  | 4903 | 3905 | 7789 | 0 | Critical Branch | 7789 | 100% | above 1000 MW
2025-11-10 | November | 13:30 |  | 4903 | 3905 | 7789 | 0 | Critical Branch | 7789 | 100% | above 1000 MW
2025-11-10 | November | 14:30 |  | 4903 | 3905 | 7789 | 0 | Critical Branch | 7789 | 100% | above 1000 MW
2025-11-10 | November | 21:30 |  | 7126 | 180 | 2528 | 187 | Minimum Margin | 2341 | 92.6% | above 1000 MW
2025-11-10 | November | 22:30 |  | 6379 | 180 | 2719 | 187 | Minimum Margin | 2532 | 93.12% | above 1000 MW
2025-11-10 | November | 23:30 |  | 6067 | 193 | 2621 | 187 | Minimum Margin | 2434 | 92.87% | above 1000 MW
2025-11-12 | November | 15:30 |  | 6762 | 859 | 5149 | 14 | Minimum Margin | 5135 | 99.73% | above 1000 MW
2025-11-12 | November | 16:30 |  | 8089 | 856 | 4251 | 14 | Minimum Margin | 4237 | 99.67% | above 1000 MW
2025-11-12 | November | 17:30 |  | 8348 | 856 | 3989 | 14 | Minimum Margin | 3975 | 99.65% | above 1000 MW
2025-11-21 | November | 18:30 |  | 2033 | 825 | 3057 | 0 | Critical Branch | 3057 | 100% | above 1000 MW
2025-11-23 | November | 12:30 |  | 5031 | 154 | 10375 | -92 | Critical Branch | 10467 | 100.9% | above 1000 MW
2025-11-23 | November | 14:30 |  | 5026 | 154 | 10425 | -92 | Critical Branch | 10517 | 100.9% | above 1000 MW
2025-11-23 | November | 15:30 |  | 9521 | 983 | 7074 | -98 | Critical Branch | 7172 | 101.4% | above 1000 MW
2025-11-23 | November | 16:30 |  | 9605 | 983 | 7067 | -98 | Critical Branch | 7165 | 101.4% | above 1000 MW
2025-11-23 | November | 17:30 |  | 9605 | 983 | 7067 | -98 | Critical Branch | 7165 | 101.4% | above 1000 MW
2025-11-23 | November | 21:30 | 10220 |  |  | 9884 | -76 | Critical Branch | 9960 | 100.8% | above 1000 MW
2025-11-23 | November | 22:30 | 10220 |  |  | 9884 | -76 | Critical Branch | 9960 | 100.8% | above 1000 MW
2025-11-23 | November | 23:30 | 10220 |  |  | 9884 | -76 | Critical Branch | 9960 | 100.8% | above 1000 MW
2025-11-25 | November | 13:30 |  | 4110 | 2215 | 2351 | 0 | Critical Branch | 2351 | 100% | above 1000 MW
2025-11-25 | November | 14:30 |  | 4110 | 2215 | 2351 | 0 | Critical Branch | 2351 | 100% | above 1000 MW
2025-11-25 | November | 15:30 |  | 5804 | 2779 | 2253 | 0 | Critical Branch | 2253 | 100% | above 1000 MW
2025-11-25 | November | 16:30 |  | 5804 | 2779 | 2253 | 0 | Critical Branch | 2253 | 100% | above 1000 MW
2025-11-25 | November | 17:30 |  | 5804 | 2779 | 2253 | 0 | Critical Branch | 2253 | 100% | above 1000 MW
2025-11-25 | November | 18:30 |  | 5261 | 2366 | 5818 | 0 | Critical Branch | 5818 | 100% | above 1000 MW
2025-11-25 | November | 19:30 |  | 5261 | 2366 | 5818 | 0 | Critical Branch | 5818 | 100% | above 1000 MW
2025-11-25 | November | 20:30 |  | 5261 | 2366 | 5818 | 0 | Critical Branch | 5818 | 100% | above 1000 MW
2025-11-25 | November | 21:30 |  | 5799 | 2377 | 1935 | 0 | Critical Branch | 1935 | 100% | above 1000 MW
2025-11-25 | November | 22:30 |  | 5799 | 2374 | 1936 | 0 | Critical Branch | 1936 | 100% | above 1000 MW
2025-11-25 | November | 23:30 |  | 5525 | 2479 | 2114 | 0 | Critical Branch | 2114 | 100% | above 1000 MW
2025-11-28 | November | 12:30 |  | 6619 | 715 | 3162 | 0 | Critical Branch | 3162 | 100% | above 1000 MW
2025-11-28 | November | 13:30 |  | 6819 | 715 | 3144 | 0 | Critical Branch | 3144 | 100% | above 1000 MW
2025-11-28 | November | 14:30 |  | 6817 | 715 | 3143 | 0 | Critical Branch | 3143 | 100% | above 1000 MW
2025-10-01 | October | 2130 |  | 5985 | 2382 | 1795 | 0 | Critical Branch | 1795 | 100% | above 1000 MW
2025-10-01 | October | 2230 |  | 5900 | 2382 | 1847 | 0 | Critical Branch | 1847 | 100% | above 1000 MW
2025-10-01 | October | 2330 |  | 5706 | 2482 | 1799 | 0 | Critical Branch | 1799 | 100% | above 1000 MW
2025-10-03 | October | 1230 |  | 5368 | 2334 | 461 | 0 | Critical Branch | 461 | 100% | below 500 MW
2025-10-03 | October | 1330 |  | 5368 | 2334 | 461 | 0 | Critical Branch | 461 | 100% | below 500 MW
2025-10-03 | October | 1430 |  | 5364 | 2334 | 462 | 0 | Critical Branch | 462 | 100% | below 500 MW
2025-10-07 | October | 2130 |  | 4058 | 624 | 947 | -32 | Critical Branch | 979 | 103.4% | [500-1000] MW
2025-10-10 | October | 1830 | 5989 |  |  | 12083 | -14 | Critical Branch | 12097 | 100.1% | above 1000 MW
2025-10-10 | October | 1930 | 5989 |  |  | 12019 | -14 | Critical Branch | 12033 | 100.1% | above 1000 MW
2025-10-10 | October | 2030 | 5989 |  |  | 12021 | -14 | Critical Branch | 12035 | 100.1% | above 1000 MW
2025-10-09 | October | 1530 |  | 5317 | 709 | 1812 | -13 | Critical Branch | 1825 | 100.7% | above 1000 MW
2025-10-09 | October | 1630 |  | 5317 | 709 | 1999 | -13 | Critical Branch | 2012 | 100.7% | above 1000 MW
2025-10-09 | October | 1730 |  | 5906 | 709 | 2199 | -13 | Critical Branch | 2212 | 100.6% | above 1000 MW
2025-10-09 | October | 2130 | 8122 |  |  | 1689 | 9 | Minimum Margin | 1680 | 99.47% | above 1000 MW
2025-10-09 | October | 2230 | 7688 |  |  | 1703 | 9 | Minimum Margin | 1694 | 99.47% | above 1000 MW
2025-10-09 | October | 2330 | 7530 |  |  | 1611 | 9 | Minimum Margin | 1602 | 99.44% | above 1000 MW
2025-10-10 | October | 1830 | 6362 |  |  | 1491 | -16 | Critical Branch | 1507 | 101.1% | above 1000 MW
2025-10-13 | October | 1830 | 6740 |  |  | 4692 | -20 | Critical Branch | 4712 | 100.4% | above 1000 MW
2025-10-13 | October | 1930 | 6740 |  |  | 4696 | -20 | Critical Branch | 4716 | 100.4% | above 1000 MW
2025-10-13 | October | 2030 | 6740 |  |  | 4678 | -20 | Critical Branch | 4698 | 100.4% | above 1000 MW
2025-10-16 | October | 1230 | 5291 |  |  | 3673 | 3 | Minimum Margin | 3670 | 99.92% | above 1000 MW
2025-10-16 | October | 1330 | 5229 |  |  | 3673 | 3 | Minimum Margin | 3670 | 99.92% | above 1000 MW
2025-10-16 | October | 1430 | 5236 |  |  | 3673 | 3 | Minimum Margin | 3670 | 99.92% | above 1000 MW
2025-10-16 | October | 1530 |  | 5454 | 552 | 1745 | 0 | Critical Branch | 1745 | 100% | above 1000 MW
2025-10-16 | October | 1830 | 8380 |  |  | 4445 | 348 | Minimum Margin | 4097 | 92.17% | above 1000 MW
2025-10-16 | October | 1930 | 8380 |  |  | 4439 | 348 | Minimum Margin | 4091 | 92.16% | above 1000 MW
2025-10-16 | October | 2030 | 8380 |  |  | 4439 | 348 | Minimum Margin | 4091 | 92.16% | above 1000 MW
2025-10-21 | October | 2130 | 7612 |  |  | 368 | -68 | Critical Branch | 436 | 118.5% | below 500 MW
2025-10-21 | October | 2230 | 7612 |  |  | 368 | -68 | Critical Branch | 436 | 118.5% | below 500 MW
2025-10-21 | October | 2330 | 7002 |  |  | 704 | -66 | Critical Branch | 770 | 109.4% | [500-1000] MW
2025-10-28 | October | 1230 |  | 7288 | 155 | 98 | 11 | Minimum Margin | 87 | 88.78% | below 500 MW
2025-10-28 | October | 1330 |  | 7424 | 181 | 83 | 11 | Minimum Margin | 72 | 86.75% | below 500 MW
2025-10-28 | October | 1430 |  | 7288 | 181 | 148 | 11 | Minimum Margin | 137 | 92.57% | below 500 MW
2025-10-29 | October | 2130 | 9214 |  |  | 803 | 340 | Minimum Margin | 463 | 57.66% | [500-1000] MW
2025-10-29 | October | 2230 | 9214 |  |  | 803 | 340 | Minimum Margin | 463 | 57.66% | [500-1000] MW
2025-10-29 | October | 2330 | 8404 |  |  | 1609 | 340 | Minimum Margin | 1269 | 78.87% | above 1000 MW
2025-10-31 | October | 2230 | 8940 |  |  | 539 | 376 | Minimum Margin | 163 | 30.24% | [500-1000] MW

## ID validation reduction
ID Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | NTC-Import | NTC-Export | ANTC |  |  | LimitedBy |  | TTC Validation Reduction |  |  | Reason for TTC Reduction |  | Reason for TTC Reduction |  |  |  | Reason for TTC Reduction |  |  |  | Reason for TTC Reduction |  |  |  | Reason for TTC Reduction |  |  |  | Reason for TTC Reduction
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | AT-IT FR-IT | IT-AT IT-FR | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | Smoothing | Reason | TSO | NTCBilateral | MNII MIEC | Reason | TSO | NTCBilateral | MNII MIEC | Reason | TSO | NTCBilateral | MNII MIEC | Reason | TSO | NTCBilateral | MNII MIEC | Reason | TSO | NTCBilateral | MNII MIEC | Reason
2025-12-01 | December | 12:30 | 9648 |  |  | 9647 |  |  |  |  | -4454 | -4454 | -4452 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-01 | December | 13:30 | 9648 |  |  | 9647 |  |  |  |  | -4459 | -4459 | -4458 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-01 | December | 15:30 |  | 9426 | 953 |  | 9426 | 934 |  |  | -2841 | -2841 | -2841 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 19 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-01 | December | 16:30 |  | 9581 | 953 |  | 9581 | 934 |  |  | -2875 | -2875 | -2875 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 19 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-01 | December | 17:30 |  | 9568 | 953 |  | 9568 | 934 |  |  | -2879 | -2879 | -2879 | Critical Branch | ID schedules | NA | 19 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-01 | December | 18:30 |  | 9458 | 965 |  | 9458 | 945 |  |  | -1738 | -1738 | -1738 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 20 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-01 | December | 19:30 |  | 9499 | 965 |  | 9499 | 945 |  |  | -1746 | -1746 | -1746 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 20 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-01 | December | 20:30 |  | 9116 | 965 |  | 9116 | 945 |  |  | -1681 | -1681 | -1681 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 20 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-01 | December | 21:30 |  | 8941 | 698 |  | 8940 | 698 |  |  | -3891 | -3891 | -3891 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-12-01 | December | 22:30 |  | 8629 | 698 |  | 8619 | 698 |  |  | -3742 | -3742 | -3742 | ID schedules | TTC Validation phase - bilateral reduction | NA | 10 | 0
2025-12-01 | December | 23:30 |  | 8039 | 535 |  | 7927 | 538 |  |  | -3054 | -3054 | -3054 | ID schedules | TTC Validation phase - bilateral reduction | NA | 109 | 0
2025-12-02 | December | 12:30 |  | 9087 | 939 |  | 9023 | 922 |  |  | 3669 | 233 | 3669 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 81 | 233 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-02 | December | 13:30 |  | 9085 | 939 |  | 9022 | 922 |  |  | 3670 | 233 | 3670 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 80 | 233 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-02 | December | 14:30 |  | 9198 | 939 |  | 9088 | 922 |  |  | 3630 | 233 | 3630 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 127 | 233 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-02 | December | 15:30 |  | 9762 | 760 |  | 9563 | 760 |  |  | 3275 | 223 | 3275 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 199 | 223
2025-12-02 | December | 16:30 |  | 9395 | 760 |  | 9198 | 760 |  |  | 3477 | 223 | 3477 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 197 | 223
2025-12-02 | December | 18:30 |  | 8732 | 852 |  | 8731 | 847 |  |  | 3567 | 222 | 3567 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 6 | 222 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 4351 |  | Process fail during TSO validation phase
2025-12-02 | December | 19:30 |  | 9093 | 852 |  | 9018 | 847 |  |  | 3451 | 222 | 3451 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 80 | 222 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 4351 |  | Process fail during TSO validation phase
2025-12-02 | December | 20:30 |  | 9117 | 919 |  | 9037 | 905 |  |  | 3442 | 222 | 3442 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 94 | 222 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 4351 |  | Process fail during TSO validation phase
2025-12-03 | December | 12:30 |  | 8574 | 881 |  | 8574 | 873 |  |  | -5389 | -5389 | -5389 | ID schedules | TTC Validation phase - bilateral reduction | NA | 8 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-03 | December | 13:30 |  | 8574 | 870 |  | 8574 | 863 |  |  | -5389 | -5389 | -5389 | ID schedules | TTC Validation phase - bilateral reduction | NA | 7 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-03 | December | 14:30 |  | 8566 | 846 |  | 8567 | 592 |  |  | -5385 | -5385 | -5385 | Critical Branch | ID schedules | NA | 253 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-03 | December | 18:30 | 9826 |  |  | 9755 |  |  |  |  | -6259 | -6259 | -6187 | Critical Branch | TTC Validation phase - bilateral reduction | 71 | NA | 0 | [18 empty] | IT | 0 |  | Forecasted security violation
2025-12-03 | December | 19:30 | 9826 |  |  | 9825 |  |  |  |  | -6259 | -6259 | -6258 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 | [18 empty] | IT | 0 |  | Forecasted security violation
2025-12-03 | December | 20:30 | 9826 |  |  | 9022 |  |  |  |  | -6260 | -6260 | -5446 | Critical Branch | ID schedules | 804 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-03 | December | 21:30 |  | 5902 | 544 |  | 5898 | 396 |  |  | 245 | -103 | 245 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 152 | -103 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-04 | December | 12:30 |  | 8247 | 816 |  | 8100 | 815 |  |  | -5000 | -5000 | -5000 | ID schedules | ID schedules | NA | 148 | 0 | [8 empty] | 8759 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE"
2025-12-04 | December | 13:30 |  | 8258 | 816 |  | 7781 | 810 |  |  | -5007 | -5007 | -5007 | ID schedules | ID schedules | NA | 483 | 0 | [8 empty] | 8372 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE"
2025-12-04 | December | 14:30 |  | 8190 | 745 |  | 6157 | 583 |  |  | -4969 | -4969 | -4969 | Critical Branch | ID schedules | NA | 2195 | 0 | [8 empty] | 7070 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE"
2025-12-04 | December | 15:30 | 8589 |  |  | 8470 |  |  |  |  | -2234 | -2234 | -2150 | Critical Branch | TTC Validation phase - bilateral reduction | 119 | NA | 0
2025-12-04 | December | 17:30 | 8589 |  |  | 8588 |  |  |  |  | -2259 | -2259 | -2258 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-12-04 | December | 19:30 | 8112 |  |  | 8110 |  |  |  |  | -4678 | -4678 | -4675 | Critical Branch | TTC Validation phase - bilateral reduction | 2 | NA | 0
2025-12-04 | December | 21:30 | 9805 |  |  | 9612 |  |  |  |  | -4880 | -4880 | -4687 | Critical Branch | ID schedules | 193 | NA | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-04 | December | 22:30 | 9805 |  |  | 9804 |  |  |  |  | -4880 | -4880 | -4878 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-12-05 | December | 18:30 |  | 9316 | 46 |  | 9302 | 36 |  |  | -4077 | -4077 | -4077 | Critical Branch | ID schedules | NA | 24 | 0 | [21 empty] | forecasted security violation
2025-12-05 | December | 19:30 |  | 9323 | 49 |  | 9312 | 49 |  |  | -4082 | -4082 | -4082 | ID schedules | ID schedules | NA | 11 | 0
2025-12-05 | December | 20:30 |  | 9316 | 69 |  | 9302 | 69 |  |  | -4078 | -4078 | -4078 | ID schedules | ID schedules | NA | 14 | 0
2025-12-06 | December | 12:30 |  | 6701 | 831 |  | 5206 | 831 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1495 | 0 |  |  | AT | 101 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-06 | December | 13:30 |  | 6926 | 831 |  | 5258 | 831 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1668 | 0 |  |  | AT | 101 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-06 | December | 14:30 |  | 6971 | 831 |  | 5605 | 831 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1366 | 0 |  |  | AT | 101 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-06 | December | 15:30 |  | 9157 | 744 |  | 6097 | 744 |  |  | -4343 | -4343 | -4343 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 3060 | 0 |  |  | AT | 103 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-06 | December | 16:30 |  | 9157 | 744 |  | 7836 | 744 |  |  | -4343 | -4343 | -4343 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1321 | 0 |  |  | AT | 103 |  | Reduction because NTC over thermal limit on border
2025-12-06 | December | 17:30 |  | 9821 | 744 |  | 8811 | 744 |  |  | -5185 | -5185 | -5185 | Critical Branch | ID schedules | NA | 1010 | 0 |  |  | AT | 103 |  | Reduction because NTC over thermal limit on border
2025-12-06 | December | 18:30 | 10574 |  |  | 10180 |  |  |  |  | -5278 | -5278 | -4876 | Critical Branch | TTC Validation phase - bilateral reduction | 394 | NA | 0 |  |  | AT | 104 |  | Reduction because NTC over thermal limit on border
2025-12-06 | December | 19:30 | 10574 |  |  | 10569 |  |  |  |  | -5278 | -5278 | -5273 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-12-06 | December | 20:30 | 10574 |  |  | 10569 |  |  |  |  | -5278 | -5278 | -5273 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 |  |  | AT | 104 |  | Reduction because NTC over thermal limit on border
2025-12-06 | December | 21:30 | 10201 |  |  | 10200 |  |  |  |  | -5347 | -5347 | -5345 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-12-06 | December | 22:30 | 10201 |  |  | 10200 |  |  |  |  | -5347 | -5347 | -5345 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-12-07 | December | 12:30 |  | 6744 | 715 |  | 5434 | 715 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1310 | 0 |  |  | AT | 120 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-07 | December | 13:30 |  | 6728 | 715 |  | 5432 | 715 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1296 | 0 |  |  | AT | 120 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-07 | December | 14:30 |  | 6847 | 715 |  | 6781 | 715 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 66 | 0
2025-12-07 | December | 15:30 |  | 8901 | 715 |  | 8128 | 715 |  |  | -3792 | -3792 | -3792 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 773 | 0
2025-12-07 | December | 16:30 |  | 8902 | 715 |  | 8863 | 715 |  |  | -3793 | -3793 | -3793 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 39 | 0
2025-12-07 | December | 18:30 | 10631 |  |  | 10602 |  |  |  |  | -5331 | -5331 | -5310 | Critical Branch | TTC Validation phase - bilateral reduction | 29 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-07 | December | 19:30 | 10631 |  |  | 10599 |  |  |  |  | -5331 | -5331 | -5308 | Critical Branch | TTC Validation phase - bilateral reduction | 32 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-07 | December | 20:30 | 10631 |  |  | 10599 |  |  |  |  | -5331 | -5331 | -5308 | Critical Branch | TTC Validation phase - bilateral reduction | 32 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-07 | December | 21:30 | 10061 |  |  | 10047 |  |  |  |  | -3630 | -3630 | -3620 | Critical Branch | TTC Validation phase - bilateral reduction | 14 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-07 | December | 22:30 | 10061 |  |  | 10047 |  |  |  |  | -3630 | -3630 | -3620 | Critical Branch | TTC Validation phase - bilateral reduction | 14 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-07 | December | 23:30 | 10061 |  |  | 10047 |  |  |  |  | -3630 | -3630 | -3620 | Critical Branch | TTC Validation phase - bilateral reduction | 14 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-08 | December | 15:30 |  | 8076 | 851 |  | 4637 | 851 |  |  | 1838 | -109 | 1838 | ID schedules | TTC Validation phase - bilateral reduction | NA | 3439 | -109 |  |  | AT | 120 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-08 | December | 16:30 |  | 8117 | 851 |  | 6783 | 851 |  |  | 1847 | -109 | 1847 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1334 | -109
2025-12-08 | December | 17:30 |  | 8123 | 851 |  | 7417 | 851 |  |  | 1848 | -109 | 1848 | ID schedules | TTC Validation phase - bilateral reduction | NA | 706 | -109
2025-12-08 | December | 18:30 |  | 9295 | 809 |  | 8889 | 809 |  |  | -3180 | -3180 | -3180 | ID schedules | TTC Validation phase - bilateral reduction | NA | 406 | 0 |  |  | AT | 117 |  | Reduction because NTC over thermal limit on border
2025-12-08 | December | 19:30 |  | 9275 | 809 |  | 9266 | 809 |  |  | -3176 | -3176 | -3176 | ID schedules | TTC Validation phase - bilateral reduction | NA | 9 | 0 |  |  | AT | 117 |  | Reduction because NTC over thermal limit on border
2025-12-08 | December | 20:30 |  | 9247 | 808 |  | 9240 | 808 |  |  | -3169 | -3169 | -3169 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 7 | 0 |  |  | AT | 117 |  | Reduction because NTC over thermal limit on border
2025-12-08 | December | 21:30 | 10444 |  |  | 10418 |  |  |  |  | -4624 | -4624 | -4606 | Critical Branch | TTC Validation phase - bilateral reduction | 26 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-08 | December | 22:30 | 10444 |  |  | 10418 |  |  |  |  | -4624 | -4624 | -4606 | Critical Branch | TTC Validation phase - bilateral reduction | 26 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-08 | December | 23:30 | 10444 |  |  | 10418 |  |  |  |  | -4624 | -4624 | -4606 | Critical Branch | TTC Validation phase - bilateral reduction | 26 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-09 | December | 12:30 |  | 8683 | 846 |  | 8683 | 842 |  |  | -3235 | -3235 | -3235 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-09 | December | 13:30 |  | 8681 | 846 |  | 8681 | 842 |  |  | -3234 | -3234 | -3234 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-09 | December | 14:30 |  | 8686 | 846 |  | 8686 | 842 |  |  | -3238 | -3238 | -3238 | Critical Branch | ID schedules | NA | 4 | 0 |  |  | AT | 95 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-09 | December | 18:30 |  | 8634 | 766 |  | 8634 | 618 |  |  | -4766 | -4766 | -4766 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 148 | 0 |  |  | AT | -64 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-09 | December | 19:30 |  | 8797 | 676 |  | 8797 | 649 |  |  | -4850 | -4850 | -4850 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 27 | 0 |  |  | AT | 58 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-09 | December | 20:30 |  | 8132 | 676 |  | 8068 | 676 |  |  | -4472 | -4472 | -4472 | Critical Branch | ID schedules | NA | 64 | 0 |  |  | AT | 86 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-10 | December | 12:30 | 9814 |  |  | 9785 |  |  |  |  | -3146 | -3146 | -3117 | Critical Branch | TTC Validation phase - bilateral reduction | 29 | NA | 0 | [6 empty] | CH |  | 10160 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-10 | December | 13:30 | 9814 |  |  | 9784 |  |  |  |  | -3149 | -3149 | -3120 | Critical Branch | TTC Validation phase - bilateral reduction | 30 | NA | 0 | [6 empty] | CH |  | 10160 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-10 | December | 14:30 | 9814 |  |  | 9784 |  |  |  |  | -3149 | -3149 | -3120 | Critical Branch | TTC Validation phase - bilateral reduction | 30 | NA | 0 | [6 empty] | CH |  | 10160 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-10 | December | 15:30 |  | 8929 | 863 |  | 8930 | 120 |  |  | -2294 | -2294 | -2294 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 742 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | CH |  | 8758 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-10 | December | 16:30 |  | 9477 | 871 |  | 9474 | 120 |  |  | -2636 | -2636 | -2636 | ID schedules | TTC Validation phase - bilateral reduction | NA | 754 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-10 | December | 17:30 |  | 9560 | 871 |  | 9560 | 120 |  |  | -2831 | -2831 | -2831 | ID schedules | TTC Validation phase - bilateral reduction | NA | 751 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-11 | December | 15:30 | 9348 |  |  | 8605 |  |  |  |  | -2839 | -2839 | -2150 | Critical Branch | ID schedules | 743 | NA | 0 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-11 | December | 16:30 | 9348 |  |  | 9010 |  |  |  |  | -2839 | -2839 | -2498 | Critical Branch | TTC Validation phase - bilateral reduction | 338 | NA | 0 | [6 empty] | CH |  | 8760 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
2025-12-11 | December | 17:30 | 10248 |  |  | 9910 |  |  |  |  | -3634 | -3634 | -3295 | Critical Branch | Validation phase | 338 | NA | 0 | [6 empty] | CH |  | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
2025-12-11 | December | 20:30 | 9279 |  |  | 9278 |  |  |  |  | -2863 | -2863 | -2862 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 |  |  | AT | 85 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-11 | December | 21:30 | 9529 |  |  | 9528 |  |  |  |  | -2898 | -2898 | -2897 | Critical Branch | ID schedules | 1 | NA | 0 |  |  | AT | 105 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 9660 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-12 | December | 20:30 |  | 8265 | 698 |  | 8264 | 698 |  |  | -2511 | -2511 | -2511 | ID schedules | ID schedules | NA | 1 | 0
2025-12-13 | December | 18:30 | 9890 |  |  | 9427 |  |  |  |  | -5877 | -5877 | -5397 | Critical Branch | ID schedules | 463 | NA | 0
2025-12-14 | December | 12:30 |  | 5195 | 1262 |  | 5016 | 1299 |  |  | 2101 | 0 | 2101 | ID schedules | TTC Validation phase - bilateral reduction | NA | 142 | 0
2025-12-14 | December | 13:30 |  | 5196 | 1253 |  | 5086 | 1276 |  |  | 2100 | 0 | 2100 | ID schedules | TTC Validation phase - bilateral reduction | NA | 87 | 0
2025-12-14 | December | 14:30 |  | 4717 | 1211 |  | 4578 | 1210 |  |  | 2142 | 0 | 2142 | ID schedules | TTC Validation phase - bilateral reduction | NA | 140 | 0
2025-12-14 | December | 15:30 |  | 8827 | 133 |  | 7960 | 133 |  |  | -3320 | -3320 | -3320 | ID schedules | TTC Validation phase - bilateral reduction | NA | 867 | 0
2025-12-14 | December | 16:30 |  | 8875 | 136 |  | 8707 | 136 |  |  | -3386 | -3386 | -3386 | ID schedules | TTC Validation phase - bilateral reduction | NA | 168 | 0
2025-12-14 | December | 21:30 | 10112 |  |  | 10096 |  |  |  |  | -3250 | -3250 | -3239 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-14 | December | 22:30 | 10112 |  |  | 10096 |  |  |  |  | -3250 | -3250 | -3239 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-14 | December | 23:30 | 10112 |  |  | 10096 |  |  |  |  | -3250 | -3250 | -3239 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-15 | December | 15:30 |  | 7186 | 122 |  | 7124 | 122 |  |  | -2258 | -2258 | -2258 | ID schedules | ID schedules | NA | 62 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-15 | December | 17:30 |  | 7187 | 102 |  | 7130 | -270 |  |  | -2410 | -2410 | -2410 | Critical Branch | ID schedules | NA | 429 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-15 | December | 18:30 |  | 7940 | 796 |  | 7940 | 525 |  |  | -3332 | -3332 | -3332 | Critical Branch | ID schedules | NA | 271 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-15 | December | 20:30 |  | 7801 | 818 |  | 7663 | 818 |  |  | -3226 | -3226 | -3226 | ID schedules | ID schedules | NA | 138 | 0 | [6 empty] | CH |  | 8049 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE" | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-16 | December | 12:30 | 9493 |  |  | 9491 |  |  |  |  | -5468 | -5468 | -5469 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-16 | December | 13:30 | 9493 |  |  | 9491 |  |  |  |  | -5463 | -5463 | -5464 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-16 | December | 14:30 | 9493 |  |  | 9492 |  |  |  |  | -5488 | -5488 | -5489 | Critical Branch | ID schedules | 1 | NA | 0 |  |  | AT | 19 |  | Reduction because NTC over thermal limit on border
2025-12-16 | December | 18:30 |  | 7972 | 699 |  | 7971 | 699 |  |  | -2690 | -2690 | -2690 | ID schedules | ID schedules | NA | 1 | 0
2025-12-16 | December | 21:30 | 9297 |  |  | 9296 |  |  |  |  | -2130 | -2130 | -2130 | Critical Branch | ID schedules | 1 | NA | 0
2025-12-17 | December | 12:30 |  | 8797 | 816 |  | 8796 | 813 |  |  | -4235 | -4235 | -4235 | Critical Branch | Critical Branch | NA | 4 | 0 |  |  | AT | 20 |  | Reduction because NTC over thermal limit on border
2025-12-17 | December | 13:30 |  | 8797 | 816 |  | 8796 | 813 |  |  | -4235 | -4235 | -4235 | Critical Branch | Critical Branch | NA | 4 | 0 |  |  | AT | 20 |  | Reduction because NTC over thermal limit on border
2025-12-17 | December | 14:30 |  | 8797 | 816 |  | 8796 | 813 |  |  | -4235 | -4235 | -4235 | Critical Branch | Critical Branch | NA | 4 | 0 |  |  | AT | 20 |  | Reduction because NTC over thermal limit on border
2025-12-17 | December | 15:30 |  | 8230 | 748 |  | 8229 | 747 |  |  | -5478 | -5478 | -5478 | ID schedules | ID schedules | NA | 2 | 0
2025-12-17 | December | 16:30 |  | 8336 | 748 |  | 8336 | 747 |  |  | -5497 | -5497 | -5497 | ID schedules | ID schedules | NA | 1 | 0
2025-12-17 | December | 17:30 |  | 8484 | 762 |  | 8484 | 761 |  |  | -5587 | -5587 | -5587 | ID schedules | ID schedules | NA | 1 | 0 |  |  | AT | 35 |  | Reduction because NTC over thermal limit on border
2025-12-17 | December | 18:30 |  | 9037 | 809 |  | 9036 | 805 |  |  | -2565 | -2565 | -2565 | Critical Branch | Min import NTC Threshold | NA | 5 | 0 |  |  | AT | 35 |  | Reduction because NTC over thermal limit on border
2025-12-17 | December | 19:30 |  | 9037 | 809 |  | 9036 | 805 |  |  | -2565 | -2565 | -2565 | Critical Branch | Min import NTC Threshold | NA | 5 | 0 |  |  | AT | 35 |  | Reduction because NTC over thermal limit on border
2025-12-17 | December | 20:30 |  | 9037 | 809 |  | 8228 | 805 |  |  | -2565 | -2565 | -2565 | Critical Branch | ID schedules | NA | 813 | 0 |  |  | AT | 35 |  | Reduction because NTC over thermal limit on border
2025-12-18 | December | 18:30 |  | 8251 | 837 |  | 8250 | 837 |  |  | -1528 | -1528 | -1528 | ID schedules | ID schedules | NA | 1 | 0
2025-12-18 | December | 19:30 |  | 8249 | 837 |  | 8248 | 837 |  |  | -1523 | -1523 | -1523 | ID schedules | ID schedules | NA | 1 | 0
2025-12-18 | December | 20:30 |  | 8174 | 837 |  | 7866 | 837 |  |  | -1481 | -1481 | -1481 | ID schedules | ID schedules | NA | 308 | 0
2025-12-19 | December | 21:30 |  | 8777 | 139 |  | 7598 | 139 |  |  | 3182 | -89 | 3182 | ID schedules | ID schedules | NA | 1179 | -89
2025-12-19 | December | 22:30 |  | 8792 | 139 |  | 8410 | 139 |  |  | 3151 | -89 | 3151 | ID schedules | ID schedules | NA | 382 | -89
2025-12-19 | December | 23:30 |  | 7912 | 154 |  | 7911 | 154 |  |  | 3461 | -89 | 3461 | Critical Branch | ID schedules | NA | 1 | -89 |  |  | AT | 134 |  | Reduction because NTC over thermal limit on border
2025-12-20 | December | 15:30 |  | 6871 | 837 |  | 6277 | 837 |  |  | -1786 | -1786 | -1786 | ID schedules | ID schedules | NA | 594 | 0
2025-12-20 | December | 16:30 |  | 6897 | 837 |  | 6896 | 837 |  |  | -1794 | -1794 | -1794 | ID schedules | ID schedules | NA | 1 | 0
2025-12-20 | December | 17:30 |  | 6836 | 837 |  | 6834 | 837 |  |  | -1772 | -1772 | -1772 | ID schedules | ID schedules | NA | 2 | 0
2025-12-20 | December | 21:30 | 10287 |  |  | 9146 |  |  |  |  | -5186 | -5186 | -3954 | Critical Branch | ID schedules | 1141 | NA | 0
2025-12-20 | December | 22:30 | 10287 |  |  | 9908 |  |  |  |  | -5181 | -5181 | -4758 | Critical Branch | ID schedules | 379 | NA | 0
2025-12-21 | December | 12:30 |  | 6000 | 715 |  | 5301 | 715 |  |  | 1239 | -57 | 1239 | ID schedules | TTC Validation phase - bilateral reduction | NA | 699 | -57 |  |  | AT | 165 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-21 | December | 13:30 |  | 5932 | 715 |  | 5226 | 715 |  |  | 1241 | -57 | 1241 | ID schedules | TTC Validation phase - bilateral reduction | NA | 706 | -57 |  |  | AT | 164 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-21 | December | 14:30 |  | 6165 | 715 |  | 5484 | 715 |  |  | 1235 | -57 | 1235 | ID schedules | TTC Validation phase - bilateral reduction | NA | 681 | -57 |  |  | AT | 165 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-12-21 | December | 15:30 |  | 9298 | 1072 |  | 7661 | 1050 |  |  | -3 | -91 | -3 | ID schedules | ID schedules | NA | 1659 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-21 | December | 16:30 |  | 9251 | 951 |  | 8246 | 971 |  |  | -32 | -91 | -32 | ID schedules | ID schedules | NA | 985 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-21 | December | 17:30 |  | 9230 | 976 |  | 8821 | 964 |  |  | -33 | -91 | -33 | Critical Branch | ID schedules | NA | 421 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-22 | December | 18:30 | 9548 |  |  | 9321 |  |  |  |  | -1822 | -1822 | -1816 | Critical Branch | ID schedules | 227 | NA | 0
2025-12-22 | December | 19:30 | 9548 |  |  | 9275 |  |  |  |  | -703 | -703 | -690 | Critical Branch | ID schedules | 273 | NA | 0
2025-12-22 | December | 20:30 | 9548 |  |  | 7769 |  |  |  |  | -660 | -660 | 859 | Critical Branch | ID schedules | 1779 | NA | 859
2025-12-23 | December | 15:30 | 10529 |  |  | 6989 |  |  |  |  | 0 | 0 | 2953 | Critical Branch | ID schedules | 3540 | NA | 2953
2025-12-23 | December | 16:30 | 10529 |  |  | 7851 |  |  |  |  | 0 | 0 | 2901 | Critical Branch | ID schedules | 2678 | NA | 2901
2025-12-23 | December | 17:30 | 10529 |  |  | 9096 |  |  |  |  | 0 | 0 | 2009 | Critical Branch | Smoothing ramp | 1433 | NA | 2009 | Smoothing ramp | Smoothing ramp
2025-12-23 | December | 18:30 |  | 8791 | 996 |  | 8790 | 973 |  |  | -2231 | -2231 | -2231 | Critical Branch | Min import NTC Threshold | NA | 24 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-23 | December | 19:30 |  | 8791 | 981 |  | 8790 | 960 |  |  | -2231 | -2231 | -2231 | Critical Branch | Min import NTC Threshold | NA | 22 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-23 | December | 20:30 |  | 8791 | 996 |  | 8790 | 973 |  |  | -2231 | -2231 | -2231 | Critical Branch | Min import NTC Threshold | NA | 24 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-23 | December | 21:30 |  | 9166 | 995 |  | 9165 | 972 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | NA | 24 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-23 | December | 22:30 |  | 9166 | 995 |  | 9165 | 972 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | NA | 24 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-23 | December | 23:30 |  | 8483 | 1090 |  | 8482 | 1061 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | NA | 30 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-24 | December | 12:30 |  | 6736 | 917 |  | 6735 | 907 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 11 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-24 | December | 13:30 |  | 6736 | 917 |  | 6735 | 907 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 11 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-24 | December | 14:30 |  | 6736 | 917 |  | 6735 | 907 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 11 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-24 | December | 15:30 | 9754 |  |  | 8680 |  |  |  |  | -4043 | -4043 | -2985 | Critical Branch | Smoothing ramp | 1074 | NA | 0 | Smoothing ramp | Smoothing ramp | [6 empty] | 9255 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago"
2025-12-24 | December | 16:30 | 9754 |  |  | 9752 |  |  |  |  | -4043 | -4043 | -4041 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-24 | December | 17:30 | 9754 |  |  | 9752 |  |  |  |  | -4043 | -4043 | -4041 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-24 | December | 18:30 | 9458 |  |  | 9456 |  |  |  |  | -3091 | -3091 | -3089 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-24 | December | 19:30 | 9458 |  |  | 9456 |  |  |  |  | -3091 | -3091 | -3089 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-24 | December | 20:30 | 9458 |  |  | 9456 |  |  |  |  | -3091 | -3091 | -3089 | Critical Branch | ID schedules | 2 | NA | 0
2025-12-24 | December | 21:30 |  | 8723 | 832 |  | 8722 | 832 |  |  | -2993 | -2993 | -2993 | ID schedules | ID schedules | NA | 1 | 0
2025-12-24 | December | 22:30 |  | 8723 | 832 |  | 8722 | 832 |  |  | -2993 | -2993 | -2993 | ID schedules | ID schedules | NA | 1 | 0
2025-12-24 | December | 23:30 |  | 8080 | 897 |  | 7973 | 896 |  |  | -2254 | -2254 | -2254 | Critical Branch | Min import NTC Threshold | NA | 108 | 0
2025-12-25 | December | 12:30 |  | 5148 | 1042 |  | 5147 | 1023 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 20 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-25 | December | 13:30 |  | 5148 | 1042 |  | 5147 | 1023 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 20 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-25 | December | 14:30 |  | 5148 | 1042 |  | 5147 | 1023 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 20 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-25 | December | 18:30 | 9429 |  |  | 6876 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 2553 | NA | 0 | Smoothing ramp | Smoothing ramp
2025-12-25 | December | 19:30 | 9429 |  |  | 8375 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 1054 | NA | 0 | Smoothing ramp | Smoothing ramp
2025-12-25 | December | 20:30 | 9429 |  |  | 9427 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 2 | NA | 0
2025-12-25 | December | 21:30 |  | 8514 | 1127 |  | 8513 | 1096 |  |  | -180 | -180 | -180 | Critical Branch | ID schedules | NA | 32 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-25 | December | 22:30 |  | 8514 | 1127 |  | 8513 | 1096 |  |  | -180 | -180 | -180 | Critical Branch | ID schedules | NA | 32 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-25 | December | 23:30 |  | 8514 | 1127 |  | 8513 | 1096 |  |  | -180 | -180 | -180 | Critical Branch | ID schedules | NA | 32 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 12:30 |  | 3903 | 928 |  | 3903 | 923 |  |  | 1065 | -78 | 1065 | ID schedules | ID schedules | NA | 5 | -78 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 13:30 |  | 4008 | 928 |  | 4008 | 923 |  |  | 1007 | -78 | 1007 | ID schedules | ID schedules | NA | 5 | -78 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 14:30 |  | 3864 | 928 |  | 3864 | 923 |  |  | 1050 | -78 | 1050 | ID schedules | ID schedules | NA | 5 | -78 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 15:30 |  | 7242 | 1036 |  | 4769 | 1018 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 2491 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 16:30 |  | 7242 | 1038 |  | 5737 | 1028 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | NA | 1515 | 0 | Smoothing ramp | Smoothing ramp | AT | 175 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 17:30 |  | 7242 | 1038 |  | 7135 | 1028 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | NA | 117 | 0 | Smoothing ramp | Smoothing ramp | AT | 175 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 18:30 |  | 8861 | 1041 |  | 8562 | 1019 |  |  | -2868 | -2868 | -2868 | Critical Branch | Smoothing ramp | NA | 321 | 0 | Smoothing ramp | Smoothing ramp | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 19:30 |  | 8861 | 996 |  | 8860 | 981 |  |  | -2868 | -2868 | -2868 | Critical Branch | Critical Branch | NA | 16 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 20:30 |  | 8861 | 1041 |  | 8860 | 1019 |  |  | -2868 | -2868 | -2868 | Critical Branch | Critical Branch | NA | 23 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 21:30 |  | 7719 | 1096 |  | 7718 | 1070 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 27 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 22:30 |  | 7719 | 1096 |  | 7718 | 1070 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 27 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-26 | December | 23:30 |  | 7719 | 1096 |  | 7718 | 1070 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 27 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-27 | December | 21:30 |  | 10703 | 1140 |  | 5678 | 1110 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 5055 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-27 | December | 22:30 |  | 10703 | 1140 |  | 6512 | 1110 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 4221 | 0 | Smoothing ramp | Smoothing ramp | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-27 | December | 23:30 |  | 10020 | 1235 |  | 7914 | 1184 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 2157 | 0 | Smoothing ramp | Smoothing ramp | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 12:30 |  | 4392 | 946 |  | 4342 | 940 |  |  | 225 | -97 | 225 | ID schedules | ID schedules | NA | 56 | -97 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 13:30 |  | 3980 | 946 |  | 3980 | 940 |  |  | 225 | -97 | 225 | ID schedules | ID schedules | NA | 6 | -97 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 14:30 |  | 4049 | 946 |  | 4049 | 940 |  |  | 225 | -97 | 225 | ID schedules | ID schedules | NA | 6 | -97 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 15:30 |  | 9306 | 1209 |  | 5542 | 1162 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 3811 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 16:30 |  | 9306 | 1209 |  | 6240 | 1162 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 3113 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 17:30 |  | 9306 | 1209 |  | 7266 | 1162 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 2087 | 0 | Smoothing ramp | Smoothing ramp | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 18:30 |  | 8737 | 912 |  | 8682 | 909 |  |  | -3078 | -3078 | -3078 | Critical Branch | Smoothing ramp | NA | 58 | 0 | Smoothing ramp | Smoothing ramp | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 19:30 |  | 8737 | 896 |  | 8736 | 896 |  |  | -3078 | -3078 | -3078 | ID schedules | Min import NTC Threshold | NA | 1 | 0
2025-12-28 | December | 20:30 |  | 8737 | 912 |  | 8736 | 909 |  |  | -3078 | -3078 | -3078 | Critical Branch | Min import NTC Threshold | NA | 4 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-28 | December | 21:30 | 8739 |  |  | 8737 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 2 | NA | 0
2025-12-28 | December | 22:30 | 8739 |  |  | 8737 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 2 | NA | 0
2025-12-28 | December | 23:30 | 8739 |  |  | 8737 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 2 | NA | 0
2025-12-29 | December | 12:30 | 4923 |  |  | 4921 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 2 | NA | 0
2025-12-29 | December | 13:30 | 4923 |  |  | 4922 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 1 | NA | 0
2025-12-29 | December | 14:30 | 4923 |  |  | 4915 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 8 | NA | 0
2025-12-29 | December | 18:30 |  | 8266 | 924 |  | 7773 | 909 |  |  | 719 | 229 | 719 | Minimum Margin | Smoothing ramp | NA | 508 | 229 | Smoothing ramp | Smoothing ramp | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-29 | December | 19:30 |  | 8266 | 909 |  | 8265 | 900 |  |  | 719 | 229 | 719 | Minimum Margin | Min import NTC Threshold | NA | 10 | 229 |  |  | AT | 124 |  | Reduction because NTC over thermal limit on border
2025-12-29 | December | 20:30 |  | 8266 | 924 |  | 8265 | 909 |  |  | 719 | 229 | 719 | Minimum Margin | Min import NTC Threshold | NA | 16 | 229 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-29 | December | 21:30 |  | 8594 | 925 |  | 8593 | 912 |  |  | -4299 | -4299 | -4299 | Critical Branch | Min import NTC Threshold | NA | 14 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-29 | December | 22:30 |  | 8594 | 925 |  | 8593 | 912 |  |  | -4299 | -4299 | -4299 | Critical Branch | Min import NTC Threshold | NA | 14 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-29 | December | 23:30 |  | 7950 | 1020 |  | 7843 | 1001 |  |  | -3565 | -3565 | -3565 | Critical Branch | Min import NTC Threshold | NA | 126 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-30 | December | 18:30 | 10372 |  |  | 7875 |  |  |  |  | -2674 | -2674 | -242 | Critical Branch | Smoothing ramp | 2497 | NA | 0 | Smoothing ramp | Smoothing ramp | [6 empty] | 9714 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Divaca-Redipuglia + Divaca-Padriciano"
2025-12-30 | December | 19:30 | 10372 |  |  | 9375 |  |  |  |  | -2674 | -2674 | -1704 | Critical Branch | Smoothing ramp | 997 | NA | 0 | Smoothing ramp | Smoothing ramp |  |  |  |  | CH |  | 9812 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Divaca-Redipuglia + Divaca-Padriciano"
2025-12-30 | December | 20:30 | 10372 |  |  | 9834 |  |  |  |  | -2674 | -2674 | -2151 | Critical Branch | Smoothing ramp | 538 | NA | 0 | Smoothing ramp | Smoothing ramp | [6 empty] | 9871 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE"
2025-12-30 | December | 21:30 |  | 9665 | 1042 |  | 7828 | 1013 |  |  | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1866 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-30 | December | 22:30 |  | 9665 | 1042 |  | 7828 | 1013 |  |  | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1866 | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-12-30 | December | 23:30 |  | 8982 | 1137 |  | 7077 | 1100 |  |  | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1942 | 0 |  |  | AT | 165 |  | Reduction because NTC over thermal limit on border
2025-12-31 | December | 12:30 | 2972 |  |  | 2971 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 13:30 | 2972 |  |  | 2844 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 128 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 14:30 | 2972 |  |  | 2941 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 31 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 15:30 |  | 7475 | 1059 |  | 5307 | 1059 |  |  | -873 | -873 | -873 | ID schedules | TTC Validation phase - bilateral reduction | NA | 2168 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 16:30 |  | 7475 | 1059 |  | 6019 | 1059 |  |  | -873 | -873 | -873 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1456 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 17:30 |  | 7475 | 1059 |  | 7291 | 1059 |  |  | -873 | -873 | -873 | ID schedules | TTC Validation phase - bilateral reduction | NA | 184 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 18:30 |  | 9235 | 1047 |  | 8692 | 1040 |  |  | -3249 | -3249 | -3249 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 550 | 0 |  |  | AT | 144 |  | Reduction because NTC over thermal limit on border | CH |  | 9486 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 19:30 |  | 9235 | 1032 |  | 9173 | 1023 |  |  | -3249 | -3249 | -3249 | Critical Branch | Validation phase | NA | 71 | 0 |  |  | AT | 144 |  | Reduction because NTC over thermal limit on border | CH |  | 9486 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 20:30 |  | 9235 | 1047 |  | 8660 | 1011 |  |  | -3249 | -3249 | -3249 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 611 | 0 |  |  | AT | 144 |  | Reduction because NTC over thermal limit on border | CH |  | 9446 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 SOAZZA-BULCIAGO" | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 21:30 |  | 8911 | 973 |  | 8748 | 973 |  |  | -3784 | -3784 | -3784 | ID schedules | TTC Validation phase - bilateral reduction | NA | 163 | 0 | [6 empty] | CH |  | 9144 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 22:30 |  | 8911 | 973 |  | 8411 | 973 |  |  | -3784 | -3784 | -3784 | ID schedules | TTC Validation phase - bilateral reduction | NA | 500 | 0 | [6 empty] | CH |  | 9144 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | [8 empty] | IT | -10000 |  | ATC blocked
2025-12-31 | December | 23:30 |  | 8268 | 1069 |  | 7869 | 1068 |  |  | -3017 | -3017 | -3017 | ID schedules | TTC Validation phase - bilateral reduction | NA | 400 | 0 | [6 empty] | CH |  | 8334 | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | [8 empty] | IT | -10000 |  | ATC blocked
2025-11-02 | November | 12:30 |  | 7805 | 191 |  | 6526 | -384 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1854 | 0 |  |  | AT | -412 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-02 | November | 13:30 |  | 7805 | 191 |  | 6645 | 129 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1222 | 0 |  |  | AT | 101 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-02 | November | 14:30 |  | 7805 | 191 |  | 6727 | 10 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1259 | 0 |  |  | AT | -210 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-02 | November | 15:30 |  | 7552 | 1260 |  | 5089 | 1259 |  |  | -3490 | -3490 | -3490 | Critical Branch | ID schedules | NA | 2464 | 0 |  |  | AT | 79 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-02 | November | 16:30 |  | 7552 | 1280 |  | 6501 | 1279 |  |  | -3490 | -3490 | -3490 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1052 | 0 | [18 empty] | IT | 2500 |  | forecasted violations
2025-11-02 | November | 17:30 |  | 7552 | 1259 |  | 6687 | 1257 |  |  | -3490 | -3490 | -3490 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 867 | 0 | [18 empty] | IT | 2300 |  | forecasted violations
2025-11-02 | November | 18:30 | 9010 |  |  | 7430 |  |  |  |  | -3740 | -3740 | -2042 | Critical Branch | TTC Validation phase - bilateral reduction | 1580 | NA | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2300 |  | forecasted violations
2025-11-02 | November | 19:30 | 9010 |  |  | 7430 |  |  |  |  | -3740 | -3740 | -2042 | Critical Branch | TTC Validation phase - bilateral reduction | 1580 | NA | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2300 |  | forecasted violations
2025-11-02 | November | 20:30 | 9010 |  |  | 7430 |  |  |  |  | -3740 | -3740 | -2042 | Critical Branch | TTC Validation phase - bilateral reduction | 1580 | NA | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2300 |  | forecasted violations
2025-11-02 | November | 21:30 |  | 9207 | 962 |  | 6694 | 962 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2513 | 0 |  |  | AT | 160 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2300 |  | forecasted violations
2025-11-02 | November | 22:30 |  | 9207 | 962 |  | 6694 | 962 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2513 | 0 |  |  | AT | 160 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2300 |  | forecasted violations
2025-11-02 | November | 23:30 |  | 9407 | 962 |  | 7195 | 962 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2212 | 0 |  |  | AT | 160 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2500 |  | forecasted violations
2025-11-03 | November | 12:30 | 9141 |  |  | 7800 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1341 | NA | 0 | [18 empty] | IT | 2600 |  | forecasted security violation
2025-11-03 | November | 13:30 | 9141 |  |  | 7800 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1341 | NA | 0 | [18 empty] | IT | 2600 |  | forecasted security violation
2025-11-03 | November | 14:30 | 9141 |  |  | 7800 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1341 | NA | 0 | [18 empty] | IT | 2600 |  | forecasted security violation
2025-11-03 | November | 16:30 |  | 6437 | 486 |  | 6412 | 486 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 25 | 0 | [18 empty] | IT | 2400 |  | forecasted security violation
2025-11-03 | November | 17:30 |  | 6029 | 486 |  | 6012 | 486 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 17 | 0 | [18 empty] | IT | 2200 |  | forecasted security violation
2025-11-03 | November | 18:30 | 7888 |  |  | 6233 |  |  |  |  | 0 | 0 | 945 | Critical Branch | TTC Validation phase - bilateral reduction | 1655 | NA | 945 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-03 | November | 19:30 | 7888 |  |  | 6233 |  |  |  |  | 0 | 0 | 944 | Critical Branch | TTC Validation phase - bilateral reduction | 1655 | NA | 944 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-03 | November | 20:30 | 7888 |  |  | 6233 |  |  |  |  | 0 | 0 | 945 | Critical Branch | TTC Validation phase - bilateral reduction | 1655 | NA | 945 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-03 | November | 21:30 | 8465 |  |  | 6306 |  |  |  |  | 0 | 0 | 465 | Critical Branch | TTC Validation phase - bilateral reduction | 2159 | NA | 465 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-03 | November | 22:30 | 8465 |  |  | 6706 |  |  |  |  | 0 | 0 | 28 | Critical Branch | TTC Validation phase - bilateral reduction | 1759 | NA | 28 | [18 empty] | IT | 2200 |  | forecasted security violation
2025-11-03 | November | 23:30 | 7855 |  |  | 7183 |  |  |  |  | -1273 | -1273 | -546 | Critical Branch | TTC Validation phase - bilateral reduction | 672 | NA | 0 | [18 empty] | IT | 2300 |  | forecasted security violation
2025-11-04 | November | 15:30 |  | 9600 | 1252 |  | 6031 | 1182 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3639 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2400 |  | forecasted security violation
2025-11-04 | November | 16:30 |  | 9600 | 1252 |  | 6031 | 1182 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3639 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2400 |  | forecasted security violation
2025-11-04 | November | 17:30 |  | 9600 | 1252 |  | 5631 | 1182 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 4039 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | 2200 |  | forecasted security violation
2025-11-04 | November | 18:30 |  | 8650 | 952 |  | 5607 | 952 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3043 | 0 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-04 | November | 19:30 |  | 8650 | 952 |  | 5607 | 952 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3043 | 0 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-04 | November | 20:30 |  | 8650 | 952 |  | 5595 | 952 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3055 | 0 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-04 | November | 21:30 | 8923 |  |  | 6420 |  |  |  |  | 0 | 0 | -756 | Critical Branch | TTC Validation phase - bilateral reduction | 2503 | NA | 0 | [18 empty] | IT | 2000 |  | forecasted security violation
2025-11-04 | November | 22:30 | 8923 |  |  | 6820 |  |  |  |  | 0 | 0 | -1179 | Critical Branch | TTC Validation phase - bilateral reduction | 2103 | NA | 0 |  |  | AT | -450 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-04 | November | 23:30 | 8313 |  |  | 7292 |  |  |  |  | -2790 | -2790 | -1717 | Critical Branch | TTC Validation phase - bilateral reduction | 1021 | NA | 0 |  |  | AT | -435 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-05 | November | 12:30 |  | 7115 | 701 |  | 7072 | 701 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 43 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-05 | November | 13:30 |  | 7115 | 701 |  | 7072 | 701 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 43 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-05 | November | 14:30 |  | 7083 | 703 |  | 7051 | 703 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 32 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-05 | November | 17:30 |  | 7812 | 660 |  | 6020 | 660 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1792 | 0 | [18 empty] | IT | 2500 |  | forecasted security violation
2025-11-05 | November | 18:30 | 9031 |  |  | 6720 |  |  |  |  | 0 | 0 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 2311 | NA | 0 | [18 empty] | IT | 2700 |  | forecasted security violation
2025-11-05 | November | 19:30 | 9031 |  |  | 6720 |  |  |  |  | 0 | 0 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 2311 | NA | 0 | [18 empty] | IT | 2700 |  | forecasted security violation
2025-11-05 | November | 20:30 | 9031 |  |  | 6720 |  |  |  |  | 0 | 0 | -1058 | Critical Branch | TTC Validation phase - bilateral reduction | 2311 | NA | 0 | [18 empty] | IT | 2700 |  | forecasted security violation
2025-11-05 | November | 21:30 | 9290 |  |  | 6751 |  |  |  |  | -3126 | -3126 | -457 | Critical Branch | TTC Validation phase - bilateral reduction | 2539 | NA | 0 | [18 empty] | IT | 2700 |  | forecasted security violation
2025-11-05 | November | 22:30 | 9290 |  |  | 7351 |  |  |  |  | -3126 | -3126 | -1071 | Critical Branch | TTC Validation phase - bilateral reduction | 1939 | NA | 0 | [18 empty] | IT | 2900 |  | forecasted security violation
2025-11-05 | November | 23:30 | 8480 |  |  | 7228 |  |  |  |  | -2309 | -2309 | -968 | Critical Branch | TTC Validation phase - bilateral reduction | 1252 | NA | 0 | [18 empty] | IT | 2700 |  | forecasted security violation
2025-11-06 | November | 12:30 | 8990 |  |  | 7769 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1221 | NA | 0 | [18 empty] | IT | 3200 |  | forecasted security violation
2025-11-06 | November | 13:30 | 8990 |  |  | 7764 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1226 | NA | 0 | [18 empty] | IT | 3200 |  | forecasted security violation
2025-11-06 | November | 14:30 | 8990 |  |  | 7869 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1121 | NA | 0 | [18 empty] | IT | 3200 |  | forecasted security violation
2025-11-06 | November | 15:30 |  | 7358 | 713 |  | 7071 | 713 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 287 | 0 | [18 empty] | IT | 3200 |  | forecasted security violation
2025-11-06 | November | 16:30 |  | 7358 | 713 |  | 6671 | 713 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 687 | 0 | [18 empty] | IT | 3000 |  | forecasted security violation
2025-11-06 | November | 20:30 |  | 8514 | 695 |  | 8486 | 695 |  |  | 242 | -94 | 242 | Critical Branch | ID schedules | NA | 28 | -94
2025-11-07 | November | 15:30 |  | 8105 | 903 |  | 8002 | 909 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 97 | 0
2025-11-07 | November | 16:30 |  | 8371 | 909 |  | 7621 | 901 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 758 | 0 | [8 empty] | 8422 | "Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE"
2025-11-08 | November | 12:30 |  | 5109 | 697 |  | 4446 | 697 |  |  | -173 | -173 | -173 | ID schedules | TTC Validation phase - bilateral reduction | NA | 663 | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-08 | November | 13:30 |  | 5033 | 697 |  | 4365 | 697 |  |  | -177 | -177 | -177 | ID schedules | TTC Validation phase - bilateral reduction | NA | 668 | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-08 | November | 14:30 |  | 5397 | 697 |  | 4865 | 697 |  |  | -260 | -260 | -260 | ID schedules | TTC Validation phase - bilateral reduction | NA | 532 | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-08 | November | 15:30 |  | 6009 | 1013 |  | 5059 | 992 |  |  | 1771 | -84 | 1771 | ID schedules | TTC Validation phase - bilateral reduction | NA | 971 | -84 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-08 | November | 18:30 |  | 8869 | 177 |  | 8709 | 177 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 160 | 0
2025-11-08 | November | 20:30 |  | 8829 | 177 |  | 8818 | 177 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 11 | 0
2025-11-08 | November | 21:30 | 9726 |  |  | 9725 |  |  |  |  | -926 | -926 | -924 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-11-08 | November | 22:30 | 9726 |  |  | 9725 |  |  |  |  | -926 | -926 | -924 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-11-08 | November | 23:30 | 8916 |  |  | 8915 |  |  |  |  | -520 | -520 | -518 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-11-09 | November | 15:30 |  | 8903 | 756 |  | 7038 | 756 |  |  | 2758 | -59 | 2758 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1865 | -59
2025-11-09 | November | 16:30 |  | 9032 | 854 |  | 8048 | 854 |  |  | 1488 | -59 | 1488 | ID schedules | TTC Validation phase - bilateral reduction | NA | 984 | -59
2025-11-09 | November | 17:30 |  | 9052 | 854 |  | 8705 | 854 |  |  | 1490 | -59 | 1490 | ID schedules | TTC Validation phase - bilateral reduction | NA | 347 | -59
2025-11-09 | November | 21:30 | 10786 |  |  | 10619 |  |  |  |  | -6134 | -6134 | -5979 | Critical Branch | ID schedules | 167 | NA | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-09 | November | 22:30 | 10786 |  |  | 10738 |  |  |  |  | -6134 | -6134 | -6098 | Critical Branch | TTC Validation phase - bilateral reduction | 48 | NA | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-09 | November | 23:30 | 10786 |  |  | 10737 |  |  |  |  | -6134 | -6134 | -6099 | Critical Branch | TTC Validation phase - bilateral reduction | 49 | NA | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-10 | November | 12:30 |  | 4903 | 3905 |  | 4903 | 2559 |  |  | 7789 | 0 | 7789 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1346 | 0 |  |  | AT | 153 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-10 | November | 13:30 |  | 4903 | 3905 |  | 4903 | 2432 |  |  | 7789 | 0 | 7789 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1473 | 0 |  |  | AT | 153 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-10 | November | 14:30 |  | 4903 | 3905 |  | 4903 | 1775 |  |  | 7789 | 0 | 7789 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2130 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-10 | November | 18:30 |  | 9458 | 705 |  | 9258 | 705 |  |  | -3334 | -3334 | -3334 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 200 | 0
2025-11-10 | November | 20:30 |  | 9453 | 705 |  | 9064 | 705 |  |  | -3334 | -3334 | -3334 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 389 | 0
2025-11-10 | November | 23:30 |  | 6067 | 193 |  | 6064 | 193 |  |  | 2621 | 187 | 2621 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 3 | 187
2025-11-11 | November | 15:30 |  | 8196 | 815 |  | 8082 | 178 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 751 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-11 | November | 16:30 |  | 8196 | 815 |  | 8321 | 178 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 512 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-11 | November | 17:30 |  | 8396 | 815 |  | 8479 | 177 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 555 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-11 | November | 18:30 |  | 9416 | 869 |  | 9188 | 869 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 228 | 0
2025-11-11 | November | 19:30 |  | 9416 | 869 |  | 9188 | 870 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 227 | 0
2025-11-11 | November | 20:30 |  | 9416 | 869 |  | 9188 | 870 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 227 | 0
2025-11-12 | November | 12:30 |  | 5404 | 69 |  | 5246 | 69 |  |  | 15319 | -15 | 15319 | ID schedules | ID schedules | NA | 158 | -15
2025-11-12 | November | 13:30 |  | 5951 | 121 |  | 5819 | 121 |  |  | 15283 | -15 | 15283 | ID schedules | ID schedules | NA | 132 | -15
2025-11-12 | November | 14:30 |  | 6038 | 179 |  | 5911 | 179 |  |  | 15291 | -15 | 15291 | ID schedules | ID schedules | NA | 127 | -15
2025-11-12 | November | 16:30 |  | 8089 | 856 |  | 8081 | 860 |  |  | 4251 | 14 | 4251 | Minimum Margin | ID schedules | NA | 4 | 14 | [10 empty] | FR | 3685 |  | Outage - Outage Gd-Ile - Piossasco 2
2025-11-12 | November | 17:30 |  | 8348 | 856 |  | 8338 | 860 |  |  | 3989 | 14 | 3989 | Minimum Margin | ID schedules | NA | 6 | 14 | [10 empty] | FR | 3685 |  | Outage - Gd-Ile- PIOSSASCO 2
2025-11-12 | November | 18:30 |  | 9203 | 825 |  | 9120 | 834 |  |  | -3696 | -3696 | -3696 | ID schedules | ID schedules | NA | 74 | 0
2025-11-12 | November | 19:30 |  | 9100 | 825 |  | 9024 | 834 |  |  | -3665 | -3665 | -3665 | ID schedules | ID schedules | NA | 67 | 0
2025-11-12 | November | 20:30 |  | 9072 | 790 |  | 8979 | 797 |  |  | -3670 | -3670 | -3670 | Critical Branch | ID schedules | NA | 86 | 0
2025-11-12 | November | 21:30 |  | 9085 | 860 |  | 8985 | 863 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 97 | 0
2025-11-12 | November | 22:30 |  | 9074 | 852 |  | 8984 | 856 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 86 | 0
2025-11-12 | November | 23:30 |  | 8622 | 190 |  | 8066 | 331 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 415 | 0
2025-11-13 | November | 15:30 | 8589 |  |  | 8052 |  |  |  |  | -2807 | -2807 | -2261 | Critical Branch | ID schedules | 537 | NA | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-13 | November | 19:30 |  | 8569 | 897 |  | 8557 | 903 |  |  | -4203 | -4203 | -4203 | ID schedules | ID schedules | NA | 6 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-13 | November | 20:30 |  | 8468 | 845 |  | 8376 | 871 |  |  | -4172 | -4172 | -4172 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 66 | 0
2025-11-14 | November | 15:30 |  | 7950 | 1009 |  | 7957 | 984 |  |  | -1829 | -1829 | -1829 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 18 | 0 | [10 empty] | FR | 3685 |  | N situation / [IT-IT] Rondissone-Trino [DIR][IT] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-14 | November | 16:30 |  | 8873 | 1009 |  | 8873 | 994 |  |  | -2749 | -2749 | -2749 | Critical Branch | ID schedules | NA | 15 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-14 | November | 17:30 |  | 9007 | 1009 |  | 9007 | 983 |  |  | -2880 | -2880 | -2880 | Critical Branch | ID schedules | NA | 26 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-15 | November | 15:30 |  | 8546 | 988 |  | 8435 | 966 |  |  | -541 | -541 | -541 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 133 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-15 | November | 16:30 |  | 8736 | 988 |  | 8736 | 966 |  |  | -589 | -589 | -589 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 22 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-15 | November | 17:30 |  | 8736 | 988 |  | 8736 | 966 |  |  | -589 | -589 | -589 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 22 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border
2025-11-15 | November | 18:30 |  | 8999 | 806 |  | 8998 | 806 |  |  | -1222 | -1222 | -1222 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-11-15 | November | 19:30 |  | 8999 | 806 |  | 8998 | 806 |  |  | -1222 | -1222 | -1222 | Critical Branch | Min import NTC Threshold | NA | 1 | 0
2025-11-15 | November | 20:30 |  | 8747 | 806 |  | 8746 | 806 |  |  | -1112 | -1112 | -1112 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-11-15 | November | 21:30 |  | 8823 | 230 |  | 8675 | 235 |  |  | 186 | 0 | 186 | ID schedules | ID schedules | NA | 143 | 0 | [8 empty] | 9295 | "Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE"
2025-11-15 | November | 23:30 |  | 8181 | 267 |  | 8079 | 319 |  |  | 960 | 0 | 960 | ID schedules | ID schedules | NA | 50 | 0
2025-11-16 | November | 18:30 | 9177 |  |  | 8726 |  |  |  |  | -2573 | -2573 | -2248 | Critical Branch | TTC Validation phase - bilateral reduction | 451 | NA | 0
2025-11-16 | November | 21:30 | 9920 |  |  | 9911 |  |  |  |  | -416 | -416 | -407 | Critical Branch | TTC Validation phase - bilateral reduction | 9 | NA | 0 |  |  | AT | 70 |  | Reduction because NTC over thermal limit on border
2025-11-16 | November | 22:30 | 9920 |  |  | 9911 |  |  |  |  | -416 | -416 | -407 | Critical Branch | TTC Validation phase - bilateral reduction | 9 | NA | 0 |  |  | AT | 69 |  | Reduction because NTC over thermal limit on border
2025-11-16 | November | 23:30 | 9920 |  |  | 9911 |  |  |  |  | -416 | -416 | -407 | Critical Branch | TTC Validation phase - bilateral reduction | 9 | NA | 0 |  |  | AT | 69 |  | Reduction because NTC over thermal limit on border
2025-11-18 | November | 17:30 | 6550 |  |  | 6549 |  |  |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 1 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-18 | November | 18:30 |  | 8980 | 698 |  | 8233 | 698 |  |  | -3235 | -3235 | -3235 | ID schedules | ID schedules | NA | 747 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-18 | November | 19:30 |  | 9049 | 698 |  | 9043 | 698 |  |  | -3331 | -3331 | -3331 | ID schedules | ID schedules | NA | 6 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-18 | November | 20:30 |  | 8534 | 653 |  | 8265 | 653 |  |  | -3223 | -3223 | -3223 | Critical Branch | ID schedules | NA | 269 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-18 | November | 21:30 | 9483 |  |  | 9318 |  |  |  |  | -3928 | -3928 | -3750 | Critical Branch | ID schedules | 165 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-19 | November | 12:30 | 8999 |  |  | 8998 |  |  |  |  | -4339 | -4339 | -4336 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-11-19 | November | 13:30 | 8999 |  |  | 8998 |  |  |  |  | -4339 | -4339 | -4336 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-11-19 | November | 14:30 | 8999 |  |  | 8998 |  |  |  |  | -4339 | -4339 | -4336 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-11-19 | November | 15:30 |  | 9533 | 1034 |  | 9533 | 1010 |  |  | -4466 | -4466 | -4466 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 24 | 0 |  |  | AT | 70 |  | Reduction because NTC over thermal limit on border
2025-11-19 | November | 16:30 |  | 9533 | 1034 |  | 9533 | 1010 |  |  | -4466 | -4466 | -4466 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 24 | 0 |  |  | AT | 70 |  | Reduction because NTC over thermal limit on border
2025-11-19 | November | 17:30 |  | 9490 | 1034 |  | 9454 | 1010 |  |  | -4453 | -4453 | -4453 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 60 | 0 |  |  | AT | 70 |  | Reduction because NTC over thermal limit on border
2025-11-19 | November | 19:30 |  | 9752 | 88 |  | 9752 | 81 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 7 | 0 |  |  | AT | 70 |  | Reduction because NTC over thermal limit on border
2025-11-19 | November | 23:30 | 8705 |  |  | 8704 |  |  |  |  | -4570 | -4570 | -4568 | Critical Branch | Critical Branch | 1 | NA | 0
2025-11-20 | November | 21:30 | 9646 |  |  | 9247 |  |  |  |  | -4802 | -4802 | -4403 | Critical Branch | ID schedules | 399 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-20 | November | 22:30 | 9646 |  |  | 9431 |  |  |  |  | -4802 | -4802 | -4591 | Critical Branch | TTC Validation phase - bilateral reduction | 215 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-20 | November | 23:30 | 8851 |  |  | 8625 |  |  |  |  | -4008 | -4008 | -3787 | Critical Branch | TTC Validation phase - bilateral reduction | 226 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-21 | November | 12:30 | 8388 |  |  | 8340 |  |  |  |  | -3210 | -3210 | -3160 | Critical Branch | TTC Validation phase - bilateral reduction | 48 | NA | 0
2025-11-21 | November | 13:30 | 8388 |  |  | 6840 |  |  |  |  | -3210 | -3210 | -1655 | Critical Branch | ID schedules | 1548 | NA | 0
2025-11-21 | November | 14:30 | 8388 |  |  | 5960 |  |  |  |  | -3210 | -3210 | -769 | Critical Branch | ID schedules | 2428 | NA | 0
2025-11-21 | November | 15:30 |  | 3265 | 483 |  | 3265 | 453 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 30 | 0 |  |  | AT | 7 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-21 | November | 16:30 |  | 3267 | 563 |  | 3267 | 562 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 1 | 0 |  |  | AT | 7 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-21 | November | 17:30 |  | 3265 | 563 |  | 3265 | 562 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 1 | 0 |  |  | AT | 7 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-21 | November | 18:30 |  | 2033 | 825 |  | 1943 | 562 |  |  | 3057 | 0 | 3057 | Critical Branch | ID schedules | NA | 353 | 0 |  |  | AT | 5 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-21 | November | 19:30 |  | 2712 | 1320 |  | 2712 | 1209 |  |  | 2358 | 0 | 2358 | ID schedules | ID schedules | NA | 111 | 0 |  |  | AT | 67 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-11-21 | November | 20:30 |  | 4487 | 1375 |  | 4362 | 1196 |  |  | 698 | 0 | 698 | ID schedules | TTC Validation phase - bilateral reduction | NA | 304 | 0
2025-11-21 | November | 21:30 | 5174 |  |  | 5171 |  |  |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 3 | NA | 0
2025-11-22 | November | 13:30 |  | 7438 | 150 |  | 7327 | 150 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 111 | 0
2025-11-22 | November | 14:30 |  | 7355 | 177 |  | 6817 | 177 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 538 | 0
2025-11-22 | November | 18:30 | 8645 |  |  | 7748 |  |  |  |  | -1656 | -1656 | -758 | Critical Branch | ID schedules | 897 | NA | 0
2025-11-22 | November | 21:30 | 10357 |  |  | 10145 |  |  |  |  | -4909 | -4909 | -4695 | Critical Branch | Smoothing ramp | 212 | NA | 0
2025-11-23 | November | 13:30 |  | 5343 | 194 |  | 5322 | 194 |  |  | 10418 | -92 | 10418 | ID schedules | TTC Validation phase - bilateral reduction | NA | 21 | -92
2025-11-23 | November | 14:30 |  | 5026 | 154 |  | 5009 | 154 |  |  | 10425 | -92 | 10425 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 17 | -92
2025-11-23 | November | 15:30 |  | 9521 | 983 |  | 7499 | 968 |  |  | 7074 | -98 | 7074 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2037 | -98 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 16:30 |  | 9605 | 983 |  | 8263 | 968 |  |  | 7067 | -98 | 7067 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1357 | -98 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 17:30 |  | 9605 | 983 |  | 9125 | 968 |  |  | 7067 | -98 | 7067 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 495 | -98 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 18:30 |  | 10184 | 205 |  | 10184 | 194 |  |  | -4844 | -4844 | -4844 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 11 | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 19:30 |  | 10184 | 205 |  | 10184 | 194 |  |  | -4844 | -4844 | -4844 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 11 | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 20:30 |  | 9993 | 205 |  | 9993 | 194 |  |  | -4779 | -4779 | -4779 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 11 | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 21:30 | 10220 |  |  | 10198 |  |  |  |  | 9884 | -76 | 9888 | Critical Branch | TTC Validation phase - bilateral reduction | 22 | NA | -72 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 22:30 | 10220 |  |  | 10198 |  |  |  |  | 9884 | -76 | 9888 | Critical Branch | TTC Validation phase - bilateral reduction | 22 | NA | -72 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-23 | November | 23:30 | 10220 |  |  | 10198 |  |  |  |  | 9884 | -76 | 9888 | Critical Branch | TTC Validation phase - bilateral reduction | 22 | NA | -72 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-11-24 | November | 12:30 |  | 7914 | 820 |  | 7450 | 698 |  |  | -5749 | -5749 | -5749 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 586 | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-24 | November | 13:30 |  | 7914 | 820 |  | 7450 | 698 |  |  | -5749 | -5749 | -5749 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 586 | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-24 | November | 14:30 |  | 7914 | 820 |  | 7450 | 698 |  |  | -5749 | -5749 | -5749 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 586 | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN
2025-11-24 | November | 18:30 |  | 6592 | 875 |  | 6584 | 875 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 8 | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-24 | November | 19:30 |  | 6592 | 875 |  | 6584 | 875 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 8 | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-24 | November | 20:30 |  | 6592 | 893 |  | 6584 | 885 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 16 | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-24 | November | 21:30 | 7936 |  |  | 7738 |  |  |  |  | -4668 | -4668 | -4454 | Critical Branch | TTC Validation phase - bilateral reduction | 198 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-24 | November | 22:30 | 7936 |  |  | 7738 |  |  |  |  | -4668 | -4668 | -4454 | Critical Branch | TTC Validation phase - bilateral reduction | 198 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - Unplanned outage LA PRAZ VILLARODIN
2025-11-25 | November | 12:30 |  | 4110 | 2434 |  | 3199 | 2412 |  |  | 2328 | 0 | 2328 | ID schedules | TTC Validation phase - bilateral reduction | NA | 933 | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 13:30 |  | 4110 | 2215 |  | 3199 | 1778 |  |  | 2351 | 0 | 2351 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1348 | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 14:30 |  | 4110 | 2215 |  | 3199 | 941 |  |  | 2351 | 0 | 2351 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2185 | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 15:30 |  | 5804 | 2779 |  | 4018 | 226 |  |  | 2253 | 0 | 2253 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4339 | 0 |  |  | AT | 114 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 16:30 |  | 5804 | 2779 |  | 4018 | 323 |  |  | 2253 | 0 | 2253 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4242 | 0 |  |  | AT | 114 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 17:30 |  | 5804 | 2779 |  | 4018 | 323 |  |  | 2253 | 0 | 2253 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4242 | 0 |  |  | AT | 114 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 18:30 |  | 5261 | 2366 |  | 3199 | 383 |  |  | 5818 | 0 | 5818 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 4045 | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 19:30 |  | 5261 | 2366 |  | 3199 | 871 |  |  | 5818 | 0 | 5818 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 3557 | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 20:30 |  | 5261 | 2366 |  | 3199 | 1344 |  |  | 5818 | 0 | 5818 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 3084 | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 21:30 |  | 5799 | 2377 |  | 4369 | 1395 |  |  | 1935 | 0 | 1935 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2412 | 0 |  |  | AT | 150 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 22:30 |  | 5799 | 2374 |  | 4369 | 474 |  |  | 1936 | 0 | 1936 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 3330 | 0 |  |  | AT | 155 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-25 | November | 23:30 |  | 5525 | 2479 |  | 4245 | 596 |  |  | 2114 | 0 | 2114 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 3163 | 0 |  |  | AT | 150 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-26 | November | 12:30 |  | 2733 | 2379 |  | 2733 | 2258 |  |  | 7179 | 0 | 7179 | ID schedules | ID schedules | NA | 121 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-26 | November | 13:30 |  | 2733 | 2267 |  | 2733 | 2115 |  |  | 7186 | 0 | 7186 | ID schedules | ID schedules | NA | 152 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-26 | November | 14:30 |  | 2733 | 1969 |  | 2733 | 1373 |  |  | 7177 | 0 | 7177 | ID schedules | ID schedules | NA | 596 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-26 | November | 16:30 |  | 3642 | 302 |  | 3563 | 294 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 87 | 0 | [10 empty] | FR | 2985 | [6 empty] | IT | -10000 |  | ATC blocked
2025-11-26 | November | 18:30 | 8048 |  |  | 7733 |  |  |  |  | -5741 | -5741 | -5399 | Critical Branch | TTC Validation phase - bilateral reduction | 315 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-26 | November | 19:30 | 8048 |  |  | 7737 |  |  |  |  | -5722 | -5722 | -5385 | Critical Branch | TTC Validation phase - bilateral reduction | 311 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-26 | November | 20:30 | 8048 |  |  | 7739 |  |  |  |  | -5722 | -5722 | -5388 | Critical Branch | TTC Validation phase - bilateral reduction | 309 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN
2025-11-26 | November | 21:30 | 8277 |  |  | 7863 |  |  |  |  | -3883 | -3883 | -3441 | Critical Branch | TTC Validation phase - bilateral reduction | 414 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN
2025-11-26 | November | 22:30 | 8277 |  |  | 7863 |  |  |  |  | -3883 | -3883 | -3441 | Critical Branch | TTC Validation phase - bilateral reduction | 414 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN
2025-11-26 | November | 23:30 | 7467 |  |  | 7245 |  |  |  |  | -3088 | -3088 | -2852 | Critical Branch | TTC Validation phase - bilateral reduction | 222 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - PRAZ VILLARODIN
2025-11-27 | November | 12:30 | 7511 |  |  | 7451 |  |  |  |  | 0 | 0 | -3522 | Critical Branch | TTC Validation phase - bilateral reduction | 60 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 13:30 | 7511 |  |  | 7450 |  |  |  |  | 0 | 0 | -3534 | Critical Branch | TTC Validation phase - bilateral reduction | 61 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 14:30 | 7511 |  |  | 7450 |  |  |  |  | 0 | 0 | -3539 | Critical Branch | TTC Validation phase - bilateral reduction | 61 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 15:30 |  | 7497 | 728 |  | 7172 | 728 |  |  | -4471 | -4471 | -4471 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 325 | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 16:30 |  | 7497 | 728 |  | 7180 | 728 |  |  | -4471 | -4471 | -4471 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 317 | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 17:30 |  | 7499 | 728 |  | 7183 | 728 |  |  | -4468 | -4468 | -4468 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 316 | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 18:30 |  | 7535 | 110 |  | 7071 | 110 |  |  | -4633 | -4633 | -4633 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 464 | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 19:30 |  | 7535 | 471 |  | 7071 | 518 |  |  | -4633 | -4633 | -4633 | ID schedules | TTC Validation phase - bilateral reduction | NA | 417 | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 20:30 |  | 7535 | 818 |  | 7071 | 818 |  |  | -4633 | -4633 | -4633 | ID schedules | TTC Validation phase - bilateral reduction | NA | 464 | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 21:30 | 7874 |  |  | 7660 |  |  |  |  | -4518 | -4518 | -4290 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 22:30 | 7874 |  |  | 7658 |  |  |  |  | -4522 | -4522 | -4292 | Critical Branch | TTC Validation phase - bilateral reduction | 216 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-27 | November | 23:30 | 7064 |  |  | 7048 |  |  |  |  | -3717 | -3717 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 | [10 empty] | FR | 2985 |  | Outage - OUTAGE TD LA PRAZ
2025-11-28 | November | 12:30 |  | 6619 | 715 |  | 6390 | 715 |  |  | 3162 | 0 | 3162 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 229 | 0 | [10 empty] | FR | 2985 |  | Outage - Outage TD LA PRAZ |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-28 | November | 13:30 |  | 6819 | 715 |  | 6486 | 715 |  |  | 3144 | 0 | 3144 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 333 | 0 | [10 empty] | FR | 2985 |  | Outage - Outage TD LA PRAZ |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-28 | November | 14:30 |  | 6817 | 715 |  | 6481 | 715 |  |  | 3143 | 0 | 3143 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 336 | 0 | [10 empty] | FR | 2985 |  | Outage - Outage TD LA PRAZ |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-28 | November | 15:30 |  | 7036 | 879 |  | 6447 | 877 |  |  | -4297 | -4297 | -4297 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 591 | 0 |  |  | AT | 111 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - Outage TD LA PRAZ |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-28 | November | 16:30 |  | 7168 | 879 |  | 6619 | 871 |  |  | -4396 | -4396 | -4396 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 557 | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - Outage TD LA PRAZ |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-28 | November | 17:30 |  | 7980 | 879 |  | 7320 | 878 |  |  | -5319 | -5319 | -5319 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 661 | 0 |  |  | AT | 112 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 2985 |  | Outage - Outage TD LA PRAZ |  |  |  |  | IT | -10000 |  | ATC blocked
2025-11-28 | November | 18:30 | 9830 |  |  | 9534 |  |  |  |  | -1560 | -1560 | -1345 | Critical Branch | ID schedules | 296 | NA | 0 |  |  | AT | 110 |  | Reduction because NTC over thermal limit on border
2025-11-28 | November | 21:30 | 10798 |  |  | 10786 |  |  |  |  | -3619 | -3619 | -3610 | Critical Branch | TTC Validation phase - bilateral reduction | 12 | NA | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-11-28 | November | 22:30 | 10798 |  |  | 10786 |  |  |  |  | -3619 | -3619 | -3610 | Critical Branch | TTC Validation phase - bilateral reduction | 12 | NA | 0 |  |  | AT | 105 |  | Reduction because NTC over thermal limit on border
2025-11-28 | November | 23:30 | 9988 |  |  | 9976 |  |  |  |  | -2799 | -2799 | -2790 | Critical Branch | TTC Validation phase - bilateral reduction | 12 | NA | 0 |  |  | AT | 120 |  | Reduction because NTC over thermal limit on border
2025-11-29 | November | 12:30 |  | 7477 | 696 |  | 6427 | 696 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1050 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-29 | November | 13:30 |  | 7477 | 696 |  | 6411 | 696 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1066 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-29 | November | 14:30 |  | 6195 | 698 |  | 6193 | 698 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 2 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-29 | November | 15:30 |  | 9221 | 724 |  | 7927 | 724 |  |  | -4423 | -4423 | -4423 | Critical Branch | ID schedules | NA | 1294 | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-11-30 | November | 18:30 | 9794 |  |  | 9591 |  |  |  |  | -5043 | -5043 | -4824 | Critical Branch | TTC Validation phase - bilateral reduction | 203 | NA | 0
2025-11-30 | November | 22:30 |  | 8896 | 690 |  | 8795 | 714 |  |  | -2903 | -2903 | -2903 | ID schedules | TTC Validation phase - bilateral reduction | NA | 77 | 0
2025-11-30 | November | 23:30 |  | 8715 | 132 |  | 8693 | 139 |  |  | -2886 | -2886 | -2886 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 15 | 0 |  |  | AT | 20 |  | Reduction because NTC over thermal limit on border
2025-10-01 | October | 12:30 | 8080 |  |  | 8000 |  |  |  |  | 14 | 14 | 72 | Adjustment reached | TTC Validation phase - bilateral reduction | 80 | NA | 72 |  |  | AT | -390 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3600 |  | Outage - Bus bar 2.1 GENISSIAT |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-01 | October | 13:30 | 8080 |  |  | 7998 |  |  |  |  | 14 | 14 | 74 | Adjustment reached | TTC Validation phase - bilateral reduction | 82 | NA | 74 |  |  | AT | -390 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3600 |  | Outage - Bus bar 2.1 GENISSIAT |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-01 | October | 14:30 | 8078 |  |  | 7999 |  |  |  |  | 12 | 12 | 71 | Adjustment reached | TTC Validation phase - bilateral reduction | 79 | NA | 71 |  |  | AT | -400 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3600 |  | Outage - Bus bar 2.1 GENISSIAT |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-01 | October | 17:30 |  | 6929 | 688 |  | 6606 | 688 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 323 | 0 |  |  | AT | -133 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 3600
2025-10-01 | October | 18:30 |  | 6030 | 728 |  | 5055 | 727 |  |  | -3812 | -3812 | -3812 | ID schedules | ID schedules | NA | 976 | 0 |  |  | AT | 115 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 3600 |  | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH]
2025-10-01 | October | 19:30 |  | 6052 | 728 |  | 5151 | 727 |  |  | -3829 | -3829 | -3829 | ID schedules | ID schedules | NA | 902 | 0 |  |  | AT | 115 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 3600 |  | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH]
2025-10-01 | October | 20:30 |  | 5825 | 728 |  | 5108 | 727 |  |  | -3652 | -3652 | -3652 | ID schedules | ID schedules | NA | 718 | 0 |  |  | AT | 46 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | FR | 3600 |  | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH]
2025-10-01 | October | 21:30 |  | 5985 | 2382 |  | 5079 | 747 |  |  | 1795 | 0 | 1795 | Critical Branch | ID schedules | NA | 2541 | 0 |  |  | AT | -65 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3600 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-01 | October | 22:30 |  | 5900 | 2382 |  | 5067 | 382 |  |  | 1847 | 0 | 1847 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2833 | 0 |  |  | AT | 118 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 3600 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-01 | October | 23:30 |  | 5706 | 2482 |  | 4946 | 418 |  |  | 1799 | 0 | 1799 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2824 | 0 |  |  | AT | 136 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 3600 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-02 | October | 17:30 |  | 5775 | 877 |  | 5709 | 877 |  |  | 569 | -17 | 569 | ID schedules | TTC Validation phase - bilateral reduction | NA | 66 | -17
2025-10-02 | October | 18:30 |  | 5649 | 877 |  | 5231 | 877 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 418 | 0 | [9 empty] | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-10-02 | October | 19:30 |  | 5794 | 877 |  | 5128 | 877 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 666 | 0 | [9 empty] | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-10-02 | October | 20:30 |  | 5257 | 877 |  | 5195 | 877 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 62 | 0
2025-10-02 | October | 21:30 |  | 7661 | 167 |  | 7292 | 166 |  |  | -2908 | -2908 | -2908 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 370 | 0 |  |  | AT | 146 |  | Reduction because NTC over thermal limit on border
2025-10-02 | October | 23:30 |  | 7066 | 212 |  | 7066 | 191 |  |  | -2307 | -2307 | -2307 | Critical Branch | Critical Branch | NA | 21 | 0 |  |  | AT | 170 |  | Reduction because NTC over thermal limit on border
2025-10-03 | October | 15:30 |  | 7421 | 815 |  | 6398 | 175 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1663 | 0 |  |  | AT | 130 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 4000
2025-10-03 | October | 16:30 |  | 7421 | 815 |  | 6996 | 175 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1065 | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 4000
2025-10-03 | October | 17:30 |  | 7421 | 815 |  | 6692 | 175 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1369 | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 4000
2025-10-03 | October | 18:30 |  | 7200 | 647 |  | 7199 | 647 |  |  | -3493 | -3493 | -3493 | Critical Branch | ID schedules | NA | 1 | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-03 | October | 21:30 |  | 7756 | 910 |  | 7651 | 904 |  |  | -2938 | -2938 | -2938 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 111 | 0 |  |  | AT | 71 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 4000 |  | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH]
2025-10-03 | October | 22:30 |  | 7974 | 895 |  | 7864 | 885 |  |  | -3084 | -3084 | -3084 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 120 | 0 |  |  | AT | 148 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 4000 |  | Overload - Retrait Barre Genissiat 400kV
2025-10-03 | October | 23:30 |  | 7460 | 975 |  | 7356 | 917 |  |  | -2514 | -2514 | -2514 | Critical Branch | ID schedules | NA | 162 | 0 |  |  | AT | 8 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-04 | October | 12:30 | 8729 |  |  | 3360 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 5369 | NA | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 13:30 | 8729 |  |  | 3478 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 5251 | NA | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 14:30 | 8729 |  |  | 3226 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 5503 | NA | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 15:30 | 8729 |  |  | 4193 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 4536 | NA | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 4000 | [6 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 16:30 | 8729 |  |  | 5982 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 2747 | NA | 0 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 4000 | [6 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 17:30 | 8729 |  |  | 6980 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1749 | NA | 0 |  |  | AT | 152 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 8343 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 4000 | [6 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 18:30 | 8729 |  |  | 6791 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1938 | NA | 0 |  |  | AT | 154 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 7575 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | [8 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 19:30 | 8729 |  |  | 7288 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1441 | NA | 0 |  |  | AT | 154 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 6715 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | [8 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 20:30 | 8729 |  |  | 6832 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1897 | NA | 0 |  |  | AT | 154 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 6955 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | [8 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 21:30 | 8729 |  |  | 7061 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1668 | NA | 0 |  |  | AT | 154 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 7032 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | [8 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 22:30 | 8729 |  |  | 6822 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1907 | NA | 0 |  |  | AT | 154 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 7180 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | [8 empty] | IT | -10000 |  | ATC blocked
2025-10-04 | October | 23:30 | 8119 |  |  | 6948 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1171 | NA | 0 |  |  | AT | 170 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 6857 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | [8 empty] | IT | -10000 |  | ATC blocked
2025-10-05 | October | 12:30 |  | 3459 | 655 |  | 2574 | 694 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 846 | 0 |  |  | AT | 170 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-05 | October | 13:30 |  | 3603 | 655 |  | 3396 | 694 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 168 | 0 |  |  | AT | 170 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-05 | October | 14:30 |  | 3610 | 655 |  | 3420 | 694 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 151 | 0 |  |  | AT | 170 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-05 | October | 15:30 |  | 4730 | 889 |  | 4202 | 891 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 526 | 0 |  |  | AT | 168 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-05 | October | 16:30 |  | 5146 | 888 |  | 4976 | 889 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 169 | 0 |  |  | AT | 168 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-05 | October | 18:30 | 7972 |  |  | 7971 |  |  |  |  | -202 | -202 | -201 | ID schedules | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-10-06 | October | 18:30 |  | 5960 | 786 |  | 5957 | 786 |  |  | 7931 | -17 | 7931 | ID schedules | TTC Validation phase - bilateral reduction | NA | 3 | -17 | [10 empty] | FR | 3000 |  | N-1 Creys-Saint Vulbas 1 / [FR-FR] CREYS-SAINT VULBAS 2 [OPP] [FR]
2025-10-06 | October | 21:30 |  | 6681 | 881 |  | 6527 | 881 |  |  | -1269 | -1269 | -1269 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 154 | 0 |  |  | AT | 50 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 3000 |  | Outage - CHAFFARD - GRANDE ILE 1
2025-10-06 | October | 22:30 |  | 6686 | 881 |  | 6577 | 881 |  |  | -1268 | -1268 | -1268 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 109 | 0 |  |  | AT | 50 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 3000 |  | Outage - CHAFFARD - GRANDE ILE 1
2025-10-06 | October | 23:30 |  | 5889 | 901 |  | 5776 | 901 |  |  | -539 | -539 | -539 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 113 | 0 |  |  | AT | 50 |  | Reduction because NTC over thermal limit on border |  |  |  |  | FR | 3000 |  | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] Lavorgo-Musignano [DIR] [CH]
2025-10-07 | October | 12:30 |  | 3229 | 2763 |  | 3229 | 2746 |  |  | 1237 | 0 | 1237 | ID schedules | TTC Validation phase - bilateral reduction | NA | 17 | 0 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3000 |  | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR]
2025-10-07 | October | 13:30 |  | 3229 | 2648 |  | 3229 | 2585 |  |  | 1227 | 0 | 1227 | ID schedules | TTC Validation phase - bilateral reduction | NA | 63 | 0 |  |  | AT | 69 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3000 |  | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR]
2025-10-07 | October | 14:30 |  | 3229 | 2230 |  | 3229 | 2021 |  |  | 1216 | 0 | 1216 | ID schedules | TTC Validation phase - bilateral reduction | NA | 209 | 0 |  |  | AT | -83 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3000 |  | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR]
2025-10-07 | October | 15:30 |  | 3229 | 2647 |  | 3229 | 1857 |  |  | 1171 | 0 | 1171 | ID schedules | TTC Validation phase - bilateral reduction | NA | 790 | 0 |  |  | AT | 80 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 3000
2025-10-07 | October | 16:30 |  | 3229 | 2656 |  | 3229 | 2072 |  |  | 1171 | 0 | 1171 | ID schedules | TTC Validation phase - bilateral reduction | NA | 584 | 0 |  |  | AT | 71 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 3000
2025-10-07 | October | 17:30 |  | 3229 | 2647 |  | 3229 | 1114 |  |  | 1171 | 0 | 1171 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1533 | 0 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 3000
2025-10-07 | October | 19:30 |  | 4930 | 786 |  | 4829 | 786 |  |  | 9937 | -39 | 9937 | ID schedules | ID schedules | NA | 101 | -39 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-10-07 | October | 20:30 |  | 4964 | 785 |  | 4919 | 763 |  |  | 10226 | -39 | 10226 | ID schedules | ID schedules | NA | 67 | -39
2025-10-07 | October | 21:30 |  | 4058 | 624 |  | 4043 | 301 |  |  | 947 | -32 | 947 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 338 | -32 |  |  | AT | 70 |  | Reduction because NTC over thermal limit on border |  |  |  | Reduction due to missing redispatch potential | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR]
2025-10-07 | October | 23:30 |  | 5617 | 652 |  | 5617 | 627 |  |  | 875 | -32 | 875 | ID schedules | TTC Validation phase - bilateral reduction | NA | 25 | -32 | [9 empty] | Reduction due to missing redispatch potential | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR]
2025-10-08 | October | 15:30 |  | 2604 | 950 |  | 2604 | 345 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 605 | 0 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 2400
2025-10-08 | October | 16:30 |  | 2604 | 1546 |  | 2604 | 1233 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 313 | 0 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 2400
2025-10-08 | October | 17:30 |  | 2604 | 1360 |  | 2604 | 866 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 494 | 0 |  |  | AT | 70 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [5 empty] | 2400
2025-10-08 | October | 18:30 | 5989 |  |  | 5601 |  |  |  |  | 12083 | -14 | 12430 | Critical Branch | TTC Validation phase - bilateral reduction | 388 | NA | 333 |  |  | AT | 52 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 2400 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-08 | October | 19:30 | 5989 |  |  | 5946 |  |  |  |  | 12019 | -14 | 12290 | Critical Branch | TTC Validation phase - bilateral reduction | 43 | NA | 257 |  |  | AT | 0 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 2400 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-08 | October | 20:30 | 5989 |  |  | 5950 |  |  |  |  | 12021 | -14 | 12215 | Critical Branch | TTC Validation phase - bilateral reduction | 39 | NA | 180 |  |  | AT | -100 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 2400 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-08 | October | 21:30 | 6518 |  |  | 6470 |  |  |  |  | -763 | -763 | -713 | Critical Branch | TTC Validation phase - bilateral reduction | 48 | NA | 0 |  |  | AT | -210 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 2400 |  | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-08 | October | 22:30 | 6518 |  |  | 6478 |  |  |  |  | -764 | -764 | -722 | Critical Branch | TTC Validation phase - bilateral reduction | 40 | NA | 0 |  |  | AT | -210 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 2400 |  | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-09 | October | 15:30 |  | 5317 | 709 |  | 5177 | 709 |  |  | 1812 | -13 | 1812 | Critical Branch | ID schedules | NA | 140 | -13 | [10 empty] | FR | 1800 |  | Outage - RDCR FIL Link 1 & 2
2025-10-09 | October | 16:30 |  | 5317 | 709 |  | 5188 | 709 |  |  | 1999 | -13 | 1999 | Critical Branch | ID schedules | NA | 129 | -13 | [10 empty] | FR | 1800 |  | Outage - RDCR FIL Link 1 & 2
2025-10-09 | October | 18:30 | 7514 |  |  | 7492 |  |  |  |  | -4440 | -4440 | -4418 | Critical Branch | ID schedules | 22 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - RO CHAFFARD G.ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-09 | October | 21:30 | 8122 |  |  | 8115 |  |  |  |  | 1689 | 9 | 1689 | Minimum Margin | ID schedules | 7 | NA | 9 | [10 empty] | FR | 3000 |  | Outage - RO CHAFFARD G.ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-09 | October | 22:30 | 7688 |  |  | 7683 |  |  |  |  | 1703 | 9 | 1702 | Minimum Margin | ID schedules | 5 | NA | 8 | [10 empty] | FR | 3000 |  | Outage - RO CHAFFARD G.ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-09 | October | 23:30 | 7530 |  |  | 7521 |  |  |  |  | 1611 | 9 | 1611 | Minimum Margin | ID schedules | 9 | NA | 9 | [10 empty] | FR | 3000 |  | Outage - RO CHAFFARD G.ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-10 | October | 20:30 | 7433 |  |  | 7431 |  |  |  |  | 1166 | -16 | 1167 | ID schedules | ID schedules | 2 | NA | -15 | [10 empty] | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-10 | October | 21:30 | 8571 |  |  | 8026 |  |  |  |  | -785 | -785 | -305 | Critical Branch | ID schedules | 545 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-10 | October | 22:30 | 8571 |  |  | 8026 |  |  |  |  | -785 | -785 | -305 | Critical Branch | ID schedules | 545 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-10 | October | 23:30 | 7961 |  |  | 7574 |  |  |  |  | -157 | -157 | 182 | Critical Branch | ID schedules | 387 | NA | 182 | [10 empty] | FR | 3000 |  | Outage - Outage - Outage Chaffard - Gd ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-11 | October | 15:30 |  | 4858 | 536 |  | 4450 | 536 |  |  | -150 | -150 | -150 | ID schedules | ID schedules | NA | 408 | 0
2025-10-11 | October | 16:30 |  | 4619 | 536 |  | 4428 | 536 |  |  | -206 | -206 | -206 | ID schedules | ID schedules | NA | 191 | 0
2025-10-11 | October | 21:30 | 8370 |  |  | 7914 |  |  |  |  | -3646 | -3646 | -3203 | Critical Branch | Critical Branch | 456 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage Chaffard - Gd Ile 1
2025-10-11 | October | 22:30 | 8370 |  |  | 7914 |  |  |  |  | -3646 | -3646 | -3203 | Critical Branch | Critical Branch | 456 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage Chaffard - Gd Ile 1
2025-10-11 | October | 23:30 | 7760 |  |  | 6893 |  |  |  |  | 0 | 0 | -2203 | Critical Branch | TTC Validation phase - bilateral reduction | 867 | NA | 0 | [10 empty] | FR | 2438 |  | Outage - Outage Chaffard - Gd ILE 1
2025-10-12 | October | 12:30 | 7917 |  |  | 2148 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 5769 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-12 | October | 13:30 | 7917 |  |  | 1994 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 5923 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-12 | October | 14:30 | 7917 |  |  | 1971 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 5946 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-12 | October | 15:30 | 7917 |  |  | 3526 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 4391 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-12 | October | 16:30 | 7917 |  |  | 4957 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 2960 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-12 | October | 17:30 | 7917 |  |  | 6872 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 1045 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-12 | October | 18:30 | 7917 |  |  | 7593 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 324 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1
2025-10-12 | October | 19:30 | 7917 |  |  | 7564 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 353 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1
2025-10-12 | October | 20:30 | 7917 |  |  | 7641 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 276 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1
2025-10-12 | October | 21:30 | 7917 |  |  | 7584 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 333 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1
2025-10-12 | October | 22:30 | 7917 |  |  | 7540 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 377 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1
2025-10-12 | October | 23:30 | 7917 |  |  | 7540 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 377 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - Outage CHAFFARD - GD ILE 1
2025-10-13 | October | 15:30 |  | 4872 | 256 |  | 4960 | 74 |  |  | 2852 | -71 | 2852 | ID schedules | ID schedules | NA | 94 | -71
2025-10-13 | October | 16:30 |  | 4655 | 533 |  | 4600 | 521 |  |  | 2854 | -71 | 2854 | ID schedules | TTC Validation phase - bilateral reduction | NA | 67 | -71 | [9 empty] | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-10-13 | October | 17:30 |  | 4033 | 292 |  | 3599 | 275 |  |  | 2873 | -71 | 2873 | ID schedules | ID schedules | NA | 451 | -71 |  |  | AT | 14 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-10-13 | October | 18:30 | 6740 |  |  | 6357 |  |  |  |  | 4692 | -20 | 5029 | Critical Branch | TTC Validation phase - bilateral reduction | 383 | NA | 317 |  |  | AT | 0 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 6404 | Reduction due to missing redispatch potential | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-13 | October | 19:30 | 6740 |  |  | 6739 |  |  |  |  | 4696 | -20 | 5053 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 337 |  |  | AT | 0 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 6404 | Reduction due to missing redispatch potential | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-13 | October | 20:30 | 6740 |  |  | 6739 |  |  |  |  | 4678 | -20 | 5026 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 328 |  |  | AT | 0 |  | Because of high redispatch the leftover intraday capacity was set to 0 | CH |  | 6404 | Reduction due to missing redispatch potential | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-13 | October | 21:30 |  | 7222 | 524 |  | 6952 | 238 |  |  | -2939 | -2939 | -2939 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 556 | 0 |  |  | AT | -434 |  | Because of high redispatch the leftover intraday capacity was set to 0 |  |  |  |  | FR | 3000 |  | Outage - maintenance work on bus bar 2.1 GENISSIAT
2025-10-13 | October | 22:30 |  | 7224 | 524 |  | 6955 | 475 |  |  | -2940 | -2940 | -2940 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 318 | 0 | [10 empty] | FR | 3000 |  | Outage - maintenance work on bus bar 2.1 GENISSIAT
2025-10-13 | October | 23:30 |  | 6776 | 544 |  | 6586 | 453 |  |  | -2415 | -2415 | -2415 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 281 | 0 | [10 empty] | FR | 3000 |  | Outage - maintenance work on bus bar 2.1 GENISSIAT
2025-10-14 | October | 13:30 |  | 5351 | 889 |  | 5351 | 876 |  |  | 1667 | -16 | 1667 | ID schedules | TTC Validation phase - bilateral reduction | NA | 13 | -16 | [9 empty] | Reduction due to missing redispatch potential | FR | 3000 |  | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR]
2025-10-14 | October | 15:30 |  | 6985 | 871 |  | 6263 | 870 |  |  | -783 | -783 | -783 | ID schedules | TTC Validation phase - bilateral reduction | NA | 723 | 0 | [10 empty] | FR | 3000 |  | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH]
2025-10-14 | October | 16:30 |  | 7046 | 648 |  | 6635 | 605 |  |  | -787 | -787 | -787 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 454 | 0 | [10 empty] | FR | 3000 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-14 | October | 17:30 |  | 6798 | 648 |  | 6396 | 339 |  |  | -727 | -727 | -727 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 711 | 0 | [10 empty] | FR | 3000 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-14 | October | 21:30 |  | 7171 | 575 |  | 6669 | 356 |  |  | -3983 | -3983 | -3983 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 721 | 0 | [9 empty] | Missing CNEC in CC: CNE: 380/220kV Lavorgo [OPP], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 3000 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-14 | October | 22:30 |  | 7165 | 647 |  | 6689 | 638 |  |  | -3980 | -3980 | -3980 | ID schedules | TTC Validation phase - bilateral reduction | NA | 485 | 0 | [10 empty] | FR | 3000 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-14 | October | 23:30 |  | 6728 | 916 |  | 6334 | 902 |  |  | -3443 | -3443 | -3443 | ID schedules | TTC Validation phase - bilateral reduction | NA | 408 | 0 | [10 empty] | FR | 3000 |  | Outage - Bus bar 2.1 GENISSIAT
2025-10-15 | October | 12:30 |  | 6278 | 438 |  | 5968 | 483 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 265 | 0
2025-10-15 | October | 13:30 |  | 6278 | 331 |  | 5968 | 389 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 252 | 0
2025-10-15 | October | 14:30 |  | 6278 | 565 |  | 5971 | 518 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 354 | 0
2025-10-15 | October | 15:30 |  | 7165 | 775 |  | 6699 | 769 |  |  | -3533 | -3533 | -3533 | ID schedules | ID schedules | NA | 472 | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
2025-10-15 | October | 16:30 |  | 7165 | 651 |  | 6699 | 532 |  |  | -3533 | -3533 | -3533 | Critical Branch | ID schedules | NA | 585 | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
2025-10-15 | October | 17:30 |  | 7165 | 666 |  | 6699 | 296 |  |  | -3533 | -3533 | -3533 | Critical Branch | ID schedules | NA | 836 | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
2025-10-15 | October | 18:30 | 6698 |  |  | 6369 |  |  |  |  | -2952 | -2952 | -2589 | Critical Branch | ID schedules | 329 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-15 | October | 19:30 | 6698 |  |  | 6275 |  |  |  |  | -2969 | -2969 | -2510 | Critical Branch | ID schedules | 423 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-15 | October | 21:30 |  | 7358 | 597 |  | 6788 | 368 |  |  | -943 | -943 | -943 | Critical Branch | ID schedules | NA | 799 | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
2025-10-15 | October | 22:30 |  | 7240 | 666 |  | 6686 | 667 |  |  | -941 | -941 | -941 | ID schedules | ID schedules | NA | 553 | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
2025-10-15 | October | 23:30 |  | 6637 | 662 |  | 6221 | -230 |  |  | -319 | -319 | -319 | Critical Branch | ID schedules | NA | 1308 | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1
2025-10-16 | October | 15:30 |  | 5454 | 552 |  | 5408 | 552 |  |  | 1745 | 0 | 1745 | Critical Branch | ID schedules | NA | 46 | 0
2025-10-16 | October | 18:30 | 8380 |  |  | 7986 |  |  |  |  | 4445 | 348 | 4468 | Minimum Margin | ID schedules | 394 | NA | 371 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD GRANDE ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-16 | October | 19:30 | 8380 |  |  | 7978 |  |  |  |  | 4439 | 348 | 4472 | Minimum Margin | ID schedules | 402 | NA | 381 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD GRANDE ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-16 | October | 20:30 | 8380 |  |  | 7982 |  |  |  |  | 4439 | 348 | 4468 | Minimum Margin | ID schedules | 398 | NA | 377 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD GRANDE ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-16 | October | 21:30 | 8441 |  |  | 8025 |  |  |  |  | -921 | -921 | -546 | Critical Branch | ID schedules | 416 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD GRANDE ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-16 | October | 22:30 | 8441 |  |  | 8022 |  |  |  |  | -920 | -920 | -542 | Critical Branch | ID schedules | 419 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD GRANDE ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-16 | October | 23:30 | 7831 |  |  | 7569 |  |  |  |  | -286 | -286 | -50 | Critical Branch | ID schedules | 262 | NA | 0 | [10 empty] | FR | 3000 |  | Outage - CHAFFARD GRANDE ILE 1 |  |  |  |  | IT | -10000 |  | ATC blocked
2025-10-18 | October | 13:30 | 6346 |  |  | 6345 |  |  |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 1 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-18 | October | 14:30 | 6132 |  |  | 6131 |  |  |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 1 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-18 | October | 15:30 |  | 7880 | 773 |  | 6030 | 773 |  |  | -4095 | -4095 | -4095 | ID schedules | ID schedules | NA | 1850 | 0 | [10 empty] | FR | 4100 |  | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR]
2025-10-18 | October | 16:30 |  | 7821 | 773 |  | 7657 | 773 |  |  | -4074 | -4074 | -4074 | ID schedules | TTC Validation phase - bilateral reduction | NA | 164 | 0 | [10 empty] | FR | 4100 |  | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR]
2025-10-19 | October | 12:30 |  | 5234 | 718 |  | 4630 | 718 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 604 | 0
2025-10-19 | October | 13:30 |  | 5321 | 718 |  | 4640 | 718 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 681 | 0
2025-10-19 | October | 14:30 |  | 5363 | 718 |  | 4645 | 718 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 718 | 0
2025-10-19 | October | 15:30 |  | 7625 | 980 |  | 5911 | 980 |  |  | -114 | -114 | -114 | Critical Branch | ID schedules | NA | 1714 | 0
2025-10-19 | October | 16:30 |  | 7617 | 1000 |  | 6440 | 1000 |  |  | -92 | -92 | -92 | Critical Branch | ID schedules | NA | 1177 | 0
2025-10-19 | October | 17:30 |  | 7717 | 980 |  | 7678 | 980 |  |  | -155 | -155 | -155 | Critical Branch | ID schedules | NA | 39 | 0
2025-10-20 | October | 15:30 |  | 7799 | 656 |  | 7677 | 656 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 122 | 0
2025-10-21 | October | 12:30 | 9036 |  |  | 8182 |  |  |  |  | -1184 | -1184 | -442 | Critical Branch | ID schedules | 854 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-21 | October | 13:30 | 9036 |  |  | 8182 |  |  |  |  | -1184 | -1184 | -442 | Critical Branch | ID schedules | 854 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-21 | October | 14:30 | 9036 |  |  | 8182 |  |  |  |  | -1184 | -1184 | -442 | Critical Branch | ID schedules | 854 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-21 | October | 15:30 |  | 6687 | 702 |  | 6666 | 702 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 21 | 0
2025-10-21 | October | 16:30 |  | 6687 | 702 |  | 6666 | 702 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 21 | 0
2025-10-21 | October | 17:30 |  | 6687 | 702 |  | 6666 | 702 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 21 | 0
2025-10-21 | October | 18:30 |  | 7000 | 697 |  | 6939 | 697 |  |  | -4351 | -4351 | -4351 | Critical Branch | ID schedules | NA | 61 | 0
2025-10-21 | October | 19:30 |  | 7000 | 697 |  | 6939 | 697 |  |  | -4351 | -4351 | -4351 | Critical Branch | ID schedules | NA | 61 | 0
2025-10-21 | October | 20:30 |  | 6962 | 697 |  | 6921 | 697 |  |  | -4338 | -4338 | -4338 | Critical Branch | ID schedules | NA | 41 | 0
2025-10-21 | October | 21:30 | 7612 |  |  | 7438 |  |  |  |  | 368 | -68 | 724 | Critical Branch | ID schedules | 174 | NA | 288 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-21 | October | 22:30 | 7612 |  |  | 7438 |  |  |  |  | 368 | -68 | 724 | Critical Branch | ID schedules | 174 | NA | 288 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-21 | October | 23:30 | 7002 |  |  | 6882 |  |  |  |  | 704 | -66 | 942 | Critical Branch | ID schedules | 120 | NA | 172 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-22 | October | 21:30 |  | 8551 | 860 |  | 7227 | 860 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1324 | 0
2025-10-22 | October | 22:30 |  | 8551 | 860 |  | 7227 | 860 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1324 | 0
2025-10-22 | October | 23:30 |  | 8048 | 880 |  | 6792 | 880 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1256 | 0
2025-10-23 | October | 12:30 | 9629 |  |  | 8979 |  |  |  |  | -5803 | -5803 | -5198 | Critical Branch | ID schedules | 650 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-23 | October | 13:30 | 9629 |  |  | 8979 |  |  |  |  | -5803 | -5803 | -5198 | Critical Branch | ID schedules | 650 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-23 | October | 14:30 | 9629 |  |  | 8979 |  |  |  |  | -5803 | -5803 | -5198 | Critical Branch | ID schedules | 650 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-23 | October | 18:30 |  | 8641 | 667 |  | 8478 | 667 |  |  | -3431 | -3431 | -3431 | Critical Branch | ID schedules | NA | 163 | 0
2025-10-23 | October | 19:30 |  | 8641 | 667 |  | 8478 | 667 |  |  | -3431 | -3431 | -3431 | Critical Branch | ID schedules | NA | 163 | 0
2025-10-23 | October | 20:30 |  | 8627 | 667 |  | 8471 | 667 |  |  | -3424 | -3424 | -3424 | Critical Branch | ID schedules | NA | 156 | 0
2025-10-23 | October | 21:30 | 9648 |  |  | 9084 |  |  |  |  | -2948 | -2948 | -2399 | Critical Branch | ID schedules | 564 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-23 | October | 22:30 | 9648 |  |  | 9084 |  |  |  |  | -2948 | -2948 | -2399 | Critical Branch | ID schedules | 564 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-23 | October | 23:30 | 8838 |  |  | 8247 |  |  |  |  | -2130 | -2130 | -1554 | Critical Branch | ID schedules | 591 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-25 | October | 15:30 |  | 7213 | 181 |  | 6877 | 180 |  |  | 41 | 41 | 41 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 337 | 41 | [9 empty] | Reduction due to missing redispatch potential
2025-10-25 | October | 16:30 |  | 7213 | 181 |  | 7158 | 180 |  |  | 41 | 41 | 41 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 56 | 41 | [9 empty] | Reduction due to missing redispatch potential
2025-10-25 | October | 18:30 |  | 7812 | 839 |  | 7811 | 839 |  |  | -526 | -526 | -526 | Critical Branch | Min import NTC Threshold | NA | 1 | 0
2025-10-25 | October | 19:30 |  | 7812 | 839 |  | 7811 | 839 |  |  | -526 | -526 | -526 | Critical Branch | Min import NTC Threshold | NA | 1 | 0
2025-10-25 | October | 21:30 | 8990 |  |  | 8989 |  |  |  |  | -850 | -850 | -849 | Critical Branch | Critical Branch | 1 | NA | 0
2025-10-25 | October | 22:30 | 8990 |  |  | 8989 |  |  |  |  | -850 | -850 | -849 | Critical Branch | Critical Branch | 1 | NA | 0
2025-10-25 | October | 23:30 | 8380 |  |  | 8379 |  |  |  |  | -221 | -221 | -218 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-10-26 | October | 15:30 |  | 8039 | 757 |  | 7534 | 757 |  |  | -1713 | -1713 | -1713 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 505 | 0
2025-10-26 | October | 16:30 |  | 8039 | 757 |  | 8038 | 757 |  |  | -1688 | -1688 | -1688 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-10-26 | October | 17:30 |  | 8137 | 757 |  | 8131 | 757 |  |  | -1749 | -1749 | -1749 | Critical Branch | ID schedules | NA | 6 | 0
2025-10-27 | October | 12:30 |  | 7356 | 868 |  | 5918 | 870 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1436 | 0
2025-10-27 | October | 13:30 |  | 7356 | 868 |  | 6355 | 871 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 998 | 0
2025-10-27 | October | 14:30 |  | 6277 | 883 |  | 6276 | 883 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 1 | 0
2025-10-27 | October | 15:30 |  | 7301 | 740 |  | 7092 | 740 |  |  | -3973 | -3973 | -3973 | ID schedules | ID schedules | NA | 209 | 0
2025-10-27 | October | 18:30 |  | 8581 | 832 |  | 8522 | 832 |  |  | -5150 | -5150 | -5150 | Critical Branch | ID schedules | NA | 59 | 0
2025-10-27 | October | 21:30 | 8400 |  |  | 8353 |  |  |  |  | -4310 | -4310 | -4257 | Critical Branch | ID schedules | 47 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-27 | October | 22:30 | 8400 |  |  | 8353 |  |  |  |  | -4310 | -4310 | -4257 | Critical Branch | ID schedules | 47 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-27 | October | 23:30 | 7790 |  |  | 7742 |  |  |  |  | -3706 | -3706 | -3652 | Critical Branch | ID schedules | 48 | NA | 0 | [18 empty] | IT | -10000 |  | ATC blocked
2025-10-28 | October | 12:30 |  | 7288 | 155 |  | 7250 | 73 |  |  | 98 | 11 | 98 | Minimum Margin | ID schedules | NA | 120 | 11
2025-10-28 | October | 13:30 |  | 7424 | 181 |  | 7424 | 180 |  |  | 83 | 11 | 83 | Minimum Margin | ID schedules | NA | 1 | 11
2025-10-28 | October | 14:30 |  | 7288 | 181 |  | 7250 | 180 |  |  | 148 | 11 | 148 | Minimum Margin | ID schedules | NA | 39 | 11
2025-10-28 | October | 15:30 |  | 6802 | 703 |  | 6792 | 703 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 10 | 0
2025-10-29 | October | 12:30 | 7824 |  |  | 7179 |  |  |  |  | -4308 | -4308 | -3723 | Critical Branch | ID schedules | 645 | NA | -3723 |  |  | AT | -349 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-10-29 | October | 13:30 | 7824 |  |  | 7823 |  |  |  |  | -4308 | -4308 | -4305 | Critical Branch | Critical Branch | 1 | NA | -4305
2025-10-29 | October | 14:30 | 7824 |  |  | 7823 |  |  |  |  | -4308 | -4308 | -4305 | Critical Branch | Critical Branch | 1 | NA | -4305
2025-10-29 | October | 17:30 |  | 8762 | 935 |  | 8747 | 935 |  |  | -1419 | -1419 | -1419 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 15 | -1419 |  |  | AT | 155 |  | Because of high redispatch the leftover intraday capacity was set to 0
2025-10-29 | October | 18:30 | 9560 |  |  | 9511 |  |  |  |  | -2464 | -2464 | -2432 | Critical Branch | ID schedules | 49 | NA | -2432 |  |  | AT | 153 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-10-29 | October | 21:30 | 9214 |  |  | 9178 |  |  |  |  | 803 | 340 | 487 | Minimum Margin | ID schedules | 36 | NA | 24 |  |  | AT | 154 |  | Because of high redispatch the leftover intraday capacity was set to 0 | [12 empty] | IT | -10000 |  | ATC blocked
2025-10-29 | October | 22:30 | 9214 |  |  | 9213 |  |  |  |  | 803 | 340 | 465 | Minimum Margin | Minimum Margin | 1 | NA | 2
2025-10-29 | October | 23:30 | 8404 |  |  | 8403 |  |  |  |  | 1609 | 340 | 1271 | Minimum Margin | TTC Validation phase - bilateral reduction | 1 | NA | 2
2025-10-31 | October | 12:30 | 8787 |  |  | 7312 |  |  |  |  | -1355 | -1355 | -88 | Critical Branch | TTC Validation phase - bilateral reduction | 1475 | NA | -88 | [18 empty] | IT | 2600 |  | forecasted violation
2025-10-31 | October | 13:30 | 8787 |  |  | 7312 |  |  |  |  | -1355 | -1355 | -88 | Critical Branch | TTC Validation phase - bilateral reduction | 1475 | NA | -88 | [18 empty] | IT | 2600 |  | forecasted violation
2025-10-31 | October | 14:30 | 8787 |  |  | 7312 |  |  |  |  | -1355 | -1355 | -88 | Critical Branch | TTC Validation phase - bilateral reduction | 1475 | NA | -88 | [18 empty] | IT | 2600 |  | forecasted violation
2025-10-31 | October | 16:30 |  | 6865 | 849 |  | 6411 | 849 |  |  | -2471 | -2471 | -2471 | ID schedules | TTC Validation phase - bilateral reduction | NA | 454 | -2471
2025-10-31 | October | 17:30 |  | 6392 | 829 |  | 5914 | 829 |  |  | -1757 | -1757 | -1757 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 478 | -1757
2025-10-31 | October | 18:30 |  | 7606 | 983 |  | 5734 | 983 |  |  | -3077 | -3077 | -3077 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1872 | -3077
2025-10-31 | October | 19:30 |  | 7605 | 983 |  | 5734 | 983 |  |  | -3077 | -3077 | -3077 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1871 | -3077
2025-10-31 | October | 20:30 |  | 7605 | 983 |  | 5734 | 983 |  |  | -3077 | -3077 | -3077 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1871 | -3077
2025-10-31 | October | 21:30 | 8564 |  |  | 6641 |  |  |  |  | 0 | 0 | 2233 | Critical Branch | TTC Validation phase - bilateral reduction | 1923 | NA | 2233 | [18 empty] | IT | 2000 |  | forecasted violation
2025-10-31 | October | 22:30 | 8940 |  |  | 6986 |  |  |  |  | 539 | 376 | 1877 | Minimum Margin | TTC Validation phase - bilateral reduction | 1954 | NA | 1714 | [18 empty] | IT | 2200 |  | forecasted violation
2025-10-31 | October | 23:30 | 7954 |  |  | 6789 |  |  |  |  | 0 | 0 | 2145 | Critical Branch | TTC Validation phase - bilateral reduction | 1165 | NA | 2145 | [18 empty] | IT | 2400 |  | forecasted violation

## ID FLAGS processing
FLAGS processing
TSO | Long description | Type | # of TS
AT | Because of high redispatch the leftover intraday capacity was set to 0 | Redispatch | 90
AT | Reduction because NTC over thermal limit on border | NTC over thermal limit | 162
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | Process Fail | 9
CH | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 ALBERTVILLE-RONDISSONE" | Overload | 1
CH | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Divaca-Redipuglia + Divaca-Padriciano" | Overload | 1
CH | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-1 SOAZZA-BULCIAGO" | Overload | 2
CH | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 SOAZZA-BULCIAGO" | Overload | 1
CH | "Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA" | Overload | 3
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | Overload | 5
CH | Reduction due to missing redispatch potential | Redispatch | 3
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | Process Fail | 9
CH | Reduction due to missing redispatch potential | Redispatch | 3
FR | Process fail during TSO validation phase | Outage | 3
FR | Outage - Outage Gd-Ile - Piossasco 2 | Outage | 1
FR | Outage - Gd-Ile- PIOSSASCO 2 | Outage | 1
FR | N situation / [IT-IT] Rondissone-Trino [DIR][IT] | Outage | 1
FR | Outage - Unplanned outage LA PRAZ VILLARODIN | Outage | 8
FR | Outage - PRAZ VILLARODIN | Outage | 18
FR | Outage - OUTAGE TD LA PRAZ | Outage | 18
FR | Outage - Bus bar 2.1 GENISSIAT | Outage | 11
FR | N-2 Albertville-Rondissone / [CH-IT] RIDDES-VALPELLINE [DIR] [CH] | Outage | 4
FR | Overload - Retrait Barre Genissiat 400kV | Overload | 1
FR | N-1 Creys-Saint Vulbas 1 / [FR-FR] CREYS-SAINT VULBAS 2 [OPP] [FR] | Outage | 4
FR | Outage - CHAFFARD - GRANDE ILE 1 | Outage | 2
FR | N-2 Pradella-Robbia + Filisur-Robbia / [CH-IT] Lavorgo-Musignano [DIR] [CH] | Outage | 1
FR | N-1 Creys-Saint Vulbas 2 / [FR-FR] CREYS-SAINT VULBAS 1 [OPP] [FR] | Outage | 10
FR | Outage - Outage Chaffard - Gd Ile 1 + Gd Ile - Piossasco 1 | Outage | 2
FR | Outage - RDCR FIL Link 1 & 2 | Outage | 2
FR | Outage - RO CHAFFARD G.ILE 1 | Outage | 4
FR | Outage - Outage - Outage Chaffard - Gd ILE 1 | Outage | 3
FR | Outage - Outage Chaffard - Gd Ile 1 | Outage | 2
FR | Outage - Outage Chaffard - Gd ILE 1 | Outage | 13
FR | Outage - maintenance work on bus bar 2.1 GENISSIAT | Outage | 3
FR | N-2 Robbia-Gorlago + Robbia-S.Fiorano / [CH-IT] LAVORGO-MUSIGNANO [DIR] [CH] | Outage | 1
FR | Outage - CHAFFARD-GRANDE ILE 1 and Busbar GENISSIAT 2.1 | Outage | 7
FR | Outage - CHAFFARD GRANDE ILE 1 | Outage | 6
FR | N situation / [AT-AT] PST NAUDERS 2 NRPST22 [DIR] | Outage | 2
IT | ATC blocked | ATC Blocked | 182
IT | Forecasted security violation | Forecast Security Violation | 32
IT | forecasted violation | Forecast Security Violation | 6
IT | forecasted violations | Forecast Security Violation | 8
Smoothing ramp | Smoothing ramp | Smoothing ramp | 15